**INSPECTION & TEST CHECK LIST – 401**

# SPRINKLER HYDROSTATIC PRESSURE TEST

|  |  |  |  |
| --- | --- | --- | --- |
| **PROJECT** | **Frankston Hospital Redevelopment,** | **JOB No** | **4500** |
| **AREA / ZONE** |  | **DW’G No:** | |

|  |  |  |  |
| --- | --- | --- | --- |
| **Guidelines** | | | |
| AIR - 50Kpa for 30mins | | | |
| WATER - 1400 kPa for 2 hours” with no pressure loss. | | | |
| 1400 kPa will be the maximum tested pressure. | | | |
| **SERVICE: SPRINKLER / HYDRANT** | | | |
|  | | | |
| **Air First Sighting** | | **Air Second Sighting** | |
| Date |  | Date |  |
| Time |  | Time |  |
| Pressure |  | Pressure |  |
| Witness (Contract***fire***) |  | Witness (Contract***fire***) |  |
| **Rough In First Sighting** | | **Rough In Second Sighting** | |
| Date |  | Date |  |
| Time |  | Time |  |
| Pressure |  | Pressure |  |
| Witness (Contractfire) |  | Witness (Contractfire) |  |
| **Fit Off First Sighting** | | **Fit Off Second Sighting** | |
| Date |  | Date |  |
| Time |  | Time |  |
| Pressure |  | Pressure |  |
| Witness (Contractfire) |  | Witness (Contractfire) |  |
| Witness (Lend Lease) |  | Witness (Lend Lease) |  |

|  |
| --- |
| **Comments on Hydrostatic Test carried out** |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |