

SPARK – North East Link – Primary Package

**Inspection and Test Plan (ITP)**

ITP Title: Conduits (Trenching and Install)

ITP Number: NEL-CNT-SDC-2990-PQA-ITP-0042 Rev 0

LOT Number:

Primary Asset Location Code:

Discipline:

**Security Classification: OFFICIAL**

**Spark NELP Approval Record**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Function** | **Position** | **Name** | **Signature** | **Date** |
| Prepared By | Quality Representative | Joe Failla | Joe Failla Date: 2022.09.06 13:44:52  Digitally signed by Joe Failla  +10'00' |  |
| Reviewed By | Project Engineer | Dominic Ciccone | Digitally signe DN: C=AU,  Domenic Ciccone E=domenic.c  O=SPARK,  Date: 2022.0 | d by Domenic Ciccone  [iccone@sparknel-dc.com.au,](mailto:iccone@sparknel-dc.com.au) CN=Domenic Ciccone  9.06 13:54:25+10'00' |
| Approved By | Quality Manager | Greg Iro | Digita Date:  +10'00 | lly signed by Greg Iro 2022.09.07 09:59:06  ' |

*Note:*

Joe Failla

1. *Ensure all Records or Checklist References are attached and that each Inspection Requirement is clearly named, signed, and dated.*
2. *Ensure every Records or Checklist References attached are legible*
3. *This Inspection Test Plan may be generic – ensure the requirement is demographically clear to your scope of work*
4. *Verification Inspections where applicable for the IREA stated as “Witness” or “Hold” shall be formally notified for their engagement and with sufficient advance notice time (i.e. 3 days or as agreed with the Sub-IREA Representative and/or the Nominated Authority)*
5. *All Nominated Authority Hold Points are Witness Points for Sub-IREA*
6. *The Sub-IREA representative is not required to physically sign-off on ITPs*

ITP – Conduits (Trenching and Install)

**Document Number:** NEL-CNT-SDC-2990-PQA-ITP-0042. **Revision: 0**

Spark PMS Doc# MSF28-2-NEL Rev 0

Management System - Uncontrolled Document when Printed Webuild Source Doc# MSF28-2

**OFFICIAL**

Page 1 of 12

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project**: SPARK – North East Link Primary Package **Client:** State of Victoria and the North East Link State Tolling Corporation | | | | | | | | | | | | |
| **ITP Title: Conduits (Trenching and Install)** | | | |  |  |  |  |  |  | **References:**  PSDR, IFC Drawings | |  |
| **Description:** This ITP covers the trenching and installation of conduits – project wide. | | | | | |  |  |  |  | **Standards:** VR733, VR703, TC-1220, AS 3000, TC-1230, AS 1345, AS 2053, AS 2566, TC-2203 | | |
| **ITP No**: NEL-CNT-SDC-2990-PQA-ITP-0042 **Rev No**: 0  **Lot No**: **Location**: **Ch**: **to Offset: to Layer**: | | | | | | | | | | | | |
| **Item No.** | **Responsible Person** | **Inspection and Test Activity** | **Specification Reference** | **Acceptance Criteria** | **Test Method** | **Test Frequency** | **Inspection/Verification (Name, signature & date)** | | | | **Records/Documents** | **Field Notes / Comments** |
| **Sub- Contractor** | **Spark NEL Engineer** | **Nominated Authority** | **IREA** |  |  |
| **1.0** | **Preliminaries (Include all aspects of Materials, Approvals, IFC Drawings, etc. Ensure all required permits have been raised prior to commencing works)** | | | | | | | | | | | |
| 1.1 | PE | IFC Drawings issued | IFC Drawing Number:  PSDR Part 6 Section 2(h) | IFC Drawings, approved plans, technical specification issued for construction  Construction of any Construction Package must not commence until at least 5 Business days after the later of when:   1. the Construction Documentation has been submitted to the State, the IREA and any Returned Asset Owner (if applicable) in accordance with section 2(f) and 2. Any requirements of the IREA under section 2(g) have been complied with. | V | PW | NR | **HP** | NR | NR | IFC Drawings |  |
| 1.2 | PE | Survey Set Out | QMP  IFC Drawings | Confirmation and visually inspect survey set out as per the IFC Drawing | V | PW | **HP** | **HP** | NR | NR | * InEight Document References: * Lot Map |  |
| **2.0** | **Operations (Include Work Execution – Installation / Manufacturing Process step-by-step)** | | | | | | | | | | | |
| 2.1 | SE | Material Conformance  - Pits and Lids | VR 733.07  IFC drawings, | ▫ Pits and Lids are correct type & approved notations.  ▫ Where the conduits enter the cable pit, a neat hole shall be cut | R | PL + PW | NR | WP | NR | NR | Delivery Dockets (Pit Detail) |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project**: SPARK – North East Link Primary Package **Client:** State of Victoria and the North East Link State Tolling Corporation | | | | | | | | | | | | |
| **ITP Title: Conduits (Trenching and Install)** | | | |  |  |  |  |  |  | **References:**  PSDR, IFC Drawings | |  |
| **Description:** This ITP covers the trenching and installation of conduits – project wide. | | | | | |  |  |  |  | **Standards:** VR733, VR703, TC-1220, AS 3000, TC-1230, AS 1345, AS 2053, AS 2566, TC-2203 | | |
| **ITP No**: NEL-CNT-SDC-2990-PQA-ITP-0042 **Rev No**: 0  **Lot No**: **Location**: **Ch**: **to Offset: to Layer**: | | | | | | | | | | | | |
| **Item No.** | **Responsible Person** | **Inspection and Test**  **Activity** | **Specification Reference** | **Acceptance Criteria** | **Test Method** | **Test Frequency** | **Inspection/Verification (Name, signature & date)** | | | | **Records/Documents** | **Field Notes / Comments** |
| **Sub- Contractor** | **Spark NEL Engineer** | **Nominated Authority** | **IREA** |  |  |
|  |  |  | VicRoads TC-1220  PSDR  Section 14 | in the pit using a hole cutter or similar tools. Pits with holes knocked in with a hammer or similar tool will be rejected.  ▫ The conduit shall be sealed to the box with silicone sealant or a cementitious grout / mortar where the pit is of HDPE construction.  ▫ Light duty pits to be used for non-trafficable areas. Heavy duty (Class D) pits shall be used in trafficable areas.  ▫ All conduit entry and exit points into pit walls to be sealed to provide watertight seal. |  |  |  |  |  |  |  |  |
| 2.2 | SE | Material Conformance  - Conduit | VR 733.02  AS 1345  AS 2053.2 IFC  Drawings  PSDR  Section 10.3 | ▫ All conduits installed underground shall be rigid heavy- duty grade UPVC in accordance with AS 2053.2.  ▫ Electrical – Heavy Duty Grade, Rigid orange UPVC conduit to AS/NZS 2053.2; Profile wall- smooth bore HD UPVC conduit to AS/NZS 2053.6  ▫ Communications – Heavy Duty Grade,  Rigid White UPVC communication conduit to AS/NZS 2053.2; | R | PL + PW | NR | WP | NR | NR | Delivery Docket (Conduit Detail) |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project**: SPARK – North East Link Primary Package **Client:** State of Victoria and the North East Link State Tolling Corporation | | | | | | | | | | | | |
| **ITP Title: Conduits (Trenching and Install)** | | | |  |  |  |  |  |  | **References:**  PSDR, IFC Drawings | |  |
| **Description:** This ITP covers the trenching and installation of conduits – project wide. | | | | | |  |  |  |  | **Standards:** VR733, VR703, TC-1220, AS 3000, TC-1230, AS 1345, AS 2053, AS 2566, TC-2203 | | |
| **ITP No**: NEL-CNT-SDC-2990-PQA-ITP-0042 **Rev No**: 0  **Lot No**: **Location**: **Ch**: **to Offset: to Layer**: | | | | | | | | | | | | |
| **Item No.** | **Responsible Person** | **Inspection and Test**  **Activity** | **Specification Reference** | **Acceptance Criteria** | **Test Method** | **Test Frequency** | **Inspection/Verification (Name, signature & date)** | | | | **Records/Documents** | **Field Notes / Comments** |
| **Sub- Contractor** | **Spark NEL Engineer** | **Nominated Authority** | **IREA** |  |  |
|  |  |  |  | ▫ Profile wall-smooth bore HD UPVC conduit to AS/NZS  2053.6 Review Certificate of Compliance. |  |  |  |  |  |  |  |  |
| 2.3 | SE | Material Conformance  - Concrete Mix | VR 703 | ▫ Application of concrete to comply to VR703. | R | PL + PW | NR | WP | NR | NR | * Delivery Docket * Mix Design |  |
| 2.4 | SE | Pit Lid Inscription | VicRoads TC-1220 | Inscription A:  “A1=VICROADS” or “A2=OTHER INSCRIPTION AS SPECIFIED”  Inscription B: “B1=ELECTRICAL” or “ELEC” “B2=COMMUNICATIONS” or “COMMS”  “B3=TRAFFIC SIGNALS” or “TRAFF SIG”  “B4=OTHER INSCRIPTION AS SPECIFIED | IP | F | NR | WP | NR | NR | Signed ITP |  |
| 2.5 | Nominated Authority | Excavation & Boring | VR 733.03 &  Drawings | ▫ Detailed proposals for boring under carriageways shall be submitted to the Superintendent for review two weeks prior to the programmed commencement of work.  ▫ Excavation center-line aligns with the design center-line of the | V | PL + PW | NR | WP | **HP** | WP | Signed ITP |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project**: SPARK – North East Link Primary Package **Client:** State of Victoria and the North East Link State Tolling Corporation | | | | | | | | | | | | |
| **ITP Title: Conduits (Trenching and Install)** | | | |  |  |  |  |  |  | **References:**  PSDR, IFC Drawings | |  |
| **Description:** This ITP covers the trenching and installation of conduits – project wide. | | | | | |  |  |  |  | **Standards:** VR733, VR703, TC-1220, AS 3000, TC-1230, AS 1345, AS 2053, AS 2566, TC-2203 | | |
| **ITP No**: NEL-CNT-SDC-2990-PQA-ITP-0042 **Rev No**: 0  **Lot No**: **Location**: **Ch**: **to Offset: to Layer**: | | | | | | | | | | | | |
| **Item No.** | **Responsible Person** | **Inspection and Test**  **Activity** | **Specification Reference** | **Acceptance Criteria** | **Test Method** | **Test Frequency** | **Inspection/Verification (Name, signature & date)** | | | | **Records/Documents** | **Field Notes / Comments** |
| **Sub- Contractor** | **Spark NEL Engineer** | **Nominated Authority** | **IREA** |  |  |
|  |  |  |  | conduit run, to the dimensions specified.  **Note:** Boring by water jet not permitted.  ▫ Excavation floor provides a suitable foundation with all debris removed prior to the placement of Embedment Material  ▫ Excavation kept free of water until the conduit has been installed and embedment and fill material(s) placed and compacted to a sufficient height,  to prevent flotation of the pipeline. |  |  |  |  |  |  |  |  |
| 2.6 | SE | Cover Requirements | VR Table 733.031  IFC  Drawings: NEL-CNT- SMEC-2102- IEI-DRG-0031 | ▫ Minimum Cover for underground conduits shall be 600mm.  **Note:** where minimum depth cover is not possible, a request for an exemption to Superintendent is to be considered (VR 733.03). | V | PL | NR | WP | NR | NR | Signed ITP |  |
| 2.7 | SE | Material conformance  - Bedding and Backfill material | Table VR 733.061  IFC drawings | ▫ Material shall be free from perishable matter.  ▫ Material shall comply with requirements as set-out in table VR 733.061 | IP | PL + PW | NR | WP | NR | NR | Delivery Dockets for:  Bedding and  Backfilling Material |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project**: SPARK – North East Link Primary Package **Client:** State of Victoria and the North East Link State Tolling Corporation | | | | | | | | | | | | |
| **ITP Title: Conduits (Trenching and Install)** | | | |  |  |  |  |  |  | **References:**  PSDR, IFC Drawings | |  |
| **Description:** This ITP covers the trenching and installation of conduits – project wide. | | | | | |  |  |  |  | **Standards:** VR733, VR703, TC-1220, AS 3000, TC-1230, AS 1345, AS 2053, AS 2566, TC-2203 | | |
| **ITP No**: NEL-CNT-SDC-2990-PQA-ITP-0042 **Rev No**: 0  **Lot No**: **Location**: **Ch**: **to Offset: to Layer**: | | | | | | | | | | | | |
| **Item No.** | **Responsible Person** | **Inspection and Test**  **Activity** | **Specification Reference** | **Acceptance Criteria** | **Test Method** | **Test Frequency** | **Inspection/Verification (Name, signature & date)** | | | | **Records/Documents** | **Field Notes / Comments** |
| **Sub- Contractor** | **Spark NEL Engineer** | **Nominated Authority** | **IREA** |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.8 | SE | Bedding Placement and Compaction | VR 733.06  IFC drawings AS 2566 | ▫ Minimum 80mm bedding below conduits on earth foundation  ▫ Minimum 200mm bedding below conduits on rock foundation  ▫ Bedding placed to full width of trench, and between conduits  ▫ Minimum 150mm bedding above top conduit prior to backfill  ▫ Embedment material shall be placed to ensure uniformity of density with no distortion, dislodgment, or damage to the pipeline. Where required to be compacted, embedment material shall be placed in layers of thickness in accordance with design IFC to achieve the density specified uniformly through the depth of each layer. | IP | PL | NR | WP | NR | NR | Signed ITP |  |
| 2.9 | SE | Conduit installation | VR 733.04,  IFC Drawings VR 733.01  AS 3000 | ▫ All conduits laid with the alignments, levels, gradients and clearances as per the latest revision of IFC drawings  ▫ Number of conduits, type spacing and specified colour | IP | F/ Pit | NR | WP | **HP** | WP | * Certificates of Electrical Safety * Installation Records |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project**: SPARK – North East Link Primary Package **Client:** State of Victoria and the North East Link State Tolling Corporation | | | | | | | | | | | | |
| **ITP Title: Conduits (Trenching and Install)** | | | |  |  |  |  |  |  | **References:**  PSDR, IFC Drawings | |  |
| **Description:** This ITP covers the trenching and installation of conduits – project wide. | | | | | |  |  |  |  | **Standards:** VR733, VR703, TC-1220, AS 3000, TC-1230, AS 1345, AS 2053, AS 2566, TC-2203 | | |
| **ITP No**: NEL-CNT-SDC-2990-PQA-ITP-0042 **Rev No**: 0  **Lot No**: **Location**: **Ch**: **to Offset: to Layer**: | | | | | | | | | | | | |
| **Item No.** | **Responsible Person** | **Inspection and Test**  **Activity** | **Specification Reference** | **Acceptance Criteria** | **Test Method** | **Test Frequency** | **Inspection/Verification (Name, signature & date)** | | | | **Records/Documents** | **Field Notes / Comments** |
| **Sub- Contractor** | **Spark NEL Engineer** | **Nominated Authority** | **IREA** |  |  |
|  |  |  | VR 733.11 | conduits are installed as per the latest revision IFC drawings.  ▫ All conduit and cable pit installation works for electrical wiring shall be carried out by, or under the direct site supervision of a registered electrical contractor and hold appropriate VicRoads prequalification.  ▫ An underground conduit warning sign shall be installed in accordance with VicRoads Drawing TC-1208.  ▫ Conduit Installation to comply to VR 733.04  ▫ Each conduit for electrical wiring and communication cables shall be provided with one synthetic draw cord not less than 3mm diameter and minimum breaking strain of 1.6kN (VR 733.05).  **Note:** Draw strings shall be installed in each conduit where there is no cable installed and removed when there is an existing cable(s) in conduit. |  |  |  |  |  |  | * Signed ITP |  |
| 2.10 | Nominated Authority | Post Bedding (Backfill) | VR 733.06 | ▫ Once the bedding material has been laid and the conduits put in | IP | F | NR | WP | **HP** | WP | Signed ITP |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project**: SPARK – North East Link Primary Package **Client:** State of Victoria and the North East Link State Tolling Corporation | | | | | | | | | | | | |
| **ITP Title: Conduits (Trenching and Install)** | | | |  |  |  |  |  |  | **References:**  PSDR, IFC Drawings | |  |
| **Description:** This ITP covers the trenching and installation of conduits – project wide. | | | | | |  |  |  |  | **Standards:** VR733, VR703, TC-1220, AS 3000, TC-1230, AS 1345, AS 2053, AS 2566, TC-2203 | | |
| **ITP No**: NEL-CNT-SDC-2990-PQA-ITP-0042 **Rev No**: 0  **Lot No**: **Location**: **Ch**: **to Offset: to Layer**: | | | | | | | | | | | | |
| **Item No.** | **Responsible Person** | **Inspection and Test**  **Activity** | **Specification Reference** | **Acceptance Criteria** | **Test Method** | **Test Frequency** | **Inspection/Verification (Name, signature & date)** | | | | **Records/Documents** | **Field Notes / Comments** |
| **Sub- Contractor** | **Spark NEL Engineer** | **Nominated Authority** | **IREA** |  |  |
|  |  |  |  | place, works shall not proceed prior to inspection by Superintendent or Representative.  **Note:** Bedding material must not be the same material excavated for the trench, it shall be clearly identifiable as introduced material. |  |  |  |  |  |  |  |  |
| 2.11 | SE | Pit installation | VR 733.07  VicRoads Drawings TC-1230, TC-2203  IFC  Drawings | ▫ Pits to be installed on crushed rock base thickness as per IFC Drawings.  ▫ Access pits shall be installed in accordance  with VicRoads drawings TC-2200 to TC-2219.  **Note:** Larger communication pits may be used where deemed appropriate due to splicing or other cable requirements as agreed with the Superintendent.  ▫ Pits to be constructed such that the Finished Surface Level to the top of the pit lid matches the surrounding FSL. | V | F/ Pit | NR | WP | NR | NR | * Certificates of Electrical Safety * Installation Records |  |
| 2.12 | SE | Pit Lid Surrounds | VR 733.07 (c) | Before the pit lid surround or pre- formed collar is cemented into position, an inspection by a  Superintendent (Nominated | IP | F | NR | WP | **HP** | WP | Signed ITP |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project**: SPARK – North East Link Primary Package **Client:** State of Victoria and the North East Link State Tolling Corporation | | | | | | | | | | | | |
| **ITP Title: Conduits (Trenching and Install)** | | | |  |  |  |  |  |  | **References:**  PSDR, IFC Drawings | |  |
| **Description:** This ITP covers the trenching and installation of conduits – project wide. | | | | | |  |  |  |  | **Standards:** VR733, VR703, TC-1220, AS 3000, TC-1230, AS 1345, AS 2053, AS 2566, TC-2203 | | |
| **ITP No**: NEL-CNT-SDC-2990-PQA-ITP-0042 **Rev No**: 0  **Lot No**: **Location**: **Ch**: **to Offset: to Layer**: | | | | | | | | | | | | |
| **Item No.** | **Responsible Person** | **Inspection and Test**  **Activity** | **Specification Reference** | **Acceptance Criteria** | **Test Method** | **Test Frequency** | **Inspection/Verification (Name, signature & date)** | | | | **Records/Documents** | **Field Notes / Comments** |
| **Sub- Contractor** | **Spark NEL Engineer** | **Nominated Authority** | **IREA** |  |  |
|  |  |  |  | Authority Representative) must  be carried out. |  |  |  |  |  |  |  |  |
| 2.13 | SS | Warning Tape | VR 733.05 | ▫ Marker tape to be installed 300mm below ground level.  ▫ Marker tape to be installed 75mm from the trench wall.  ▫ Where both electrical and communication conduits are provided in a trench two marker tapes shall be provided one for electrical and the other for  communication conduits. | V | PL | NR | WP | NR | NR | Photos |  |
| 2.14 | SE | Detector Pits | VR 733.08 | Detector pits and detector pit covers shall be constructed and installed in accordance with VR Standard Drawings TC-1310 and TC-1320. | V | F | NR | WP | NR | NR | Signed ITP |  |
| 2.15 | SE | Test Records   * Compaction   (Backfill)   * Concrete | VR 733.06(d) VR 703 | Backfill Compaction  ▫ Bedding and backfill materials shall have compacted in layers to a density ratio >95%,  ▫ Moisture content within the range 85% to 115% where backfill material contains material retained on a 37.5mm AS sieve. **Note (Backfill):**  Detailed proposals for compaction of backfill materials of nominal size >40mm shall be | V | PL | NR | WP | NR | NR | NATA Test Records |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project**: SPARK – North East Link Primary Package **Client:** State of Victoria and the North East Link State Tolling Corporation | | | | | | | | | | | | |
| **ITP Title: Conduits (Trenching and Install)** | | | |  |  |  |  |  |  | **References:**  PSDR, IFC Drawings | |  |
| **Description:** This ITP covers the trenching and installation of conduits – project wide. | | | | | |  |  |  |  | **Standards:** VR733, VR703, TC-1220, AS 3000, TC-1230, AS 1345, AS 2053, AS 2566, TC-2203 | | |
| **ITP No**: NEL-CNT-SDC-2990-PQA-ITP-0042 **Rev No**: 0  **Lot No**: **Location**: **Ch**: **to Offset: to Layer**: | | | | | | | | | | | | |
| **Item No.** | **Responsible Person** | **Inspection and Test**  **Activity** | **Specification Reference** | **Acceptance Criteria** | **Test Method** | **Test Frequency** | **Inspection/Verification (Name, signature & date)** | | | | **Records/Documents** | **Field Notes / Comments** |
| **Sub- Contractor** | **Spark NEL Engineer** | **Nominated Authority** | **IREA** |  |  |
|  |  |  |  | submitted to Superintendent for review before commencing works.  **Note (Concrete):**  Minimum test requirements to comply to VR 703.11 (2021). |  |  |  |  |  |  |  |  |
| **3.0** | **Post Operations (Include Inspection and Testing)** | | | | | | | | | | | |
| 3.1 | SE | Certification of installation | VR 733.04  VR 733.07  AS 3000 | ▫ All conduit installation works for electrical wiring and communications cabling shall be carried out by, or under the direct supervision of, appropriately registered and licensed  personnel provided by the Contractor. | V | PL | NR | **HP** | NR | NR | Certificate of Electrical Safety |  |
| 3.2 | SE | Redline Drawings | VR 733.11 IFC  Drawings | 1. ‘As-Constructed drawings showing complete conduit network including conduit types, sizes and depths. 2. the above “as constructed’ drawings shall also show all pits, pit types and pit sizes. 3. certificates of electrical safety for all conduits and pits installed 4. documentation demonstrating that all pits and conduits have been installed in accordance with requirements of this specification. | V | F | NR | WP | NR | NR | Redline Mark-Up Records |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project**: SPARK – North East Link Primary Package **Client:** State of Victoria and the North East Link State Tolling Corporation | | | | | | | | | | | | | | | | | |
| **ITP Title: Conduits (Trenching and Install)** | | | | |  |  |  |  |  |  |  |  |  | **References:**  PSDR, IFC Drawings | | |  |
| **Description:** This ITP covers the trenching and installation of conduits – project wide. | | | | | | | | |  |  |  |  |  | **Standards:** VR733, VR703, TC-1220, AS 3000, TC-1230, AS 1345, AS 2053, AS 2566, TC-2203 | | | |
| **ITP No**: NEL-CNT-SDC-2990-PQA-ITP-0042 **Rev No**: 0  **Lot No**: **Location**: **Ch**: **to Offset: to Layer**: | | | | | | | | | | | | | | | | | |
| **Item No.** | **Responsible Person** | **Inspection and Test**  **Activity** | | **Specification Reference** | **Acceptance Criteria** | | | **Test Method** | **Test Frequency** | **Inspection/Verification (Name, signature & date)** | | | | | | **Records/Documents** | **Field Notes / Comments** |
| **Sub- Contractor** | | **Spark NEL Engineer** | **Nominated Authority** | **IREA** | |  |  |
| **4.0** | **Quality** | | | | | | | | | | | | | | | | |
| 4.1 | QSR | Identification and control of non- conforming products or services  (if applicable) | | CQMP | Review and confirm closure of NCR’s and associated RFI’s prior to closing of construction lot | | | R | PL |  | | WP |  |  | | NCR closed with related documentation | InEight Form Reference Numbers (NCRs, RFIs etc) |
| 4.2 | QSR | Check all quality records for lot closure | | CQMP | All applicable quality records are complete | | | R | PL |  | | WP |  |  | | Compiled documents (all data reports and records) |  |
| **Legend:** | | | | | | | | | | | | | | | | | |
| **Responsibility** | | | | | | **Method** | **Inspection / Verification** | | | | **Test Frequency** | | | | **Other** | | |
| SS: Site Supervisor SE: Site Engineer PE: Project Engineer SPE: Senior Project Engineer  GE: Geotechnical Engineer PS: Project Surveyor | | | PSM: Project Systems Manager  QSR: Quality Site Rep. STR: Structural Engineer SSR: Site Safety Rep.  EMR: Environmental Management Rep.  NA: Nominated Authority (Release of HP)  IREA: Independent Reviewer (Observer) | | | V: Verify  I: Inspection R: Review T: Test | HP: Hold Point WP: Witness Point NR: Not Required | | | | PW: Prior to Works PL: Per Lot  F: Full or 100% Inspection or Testing  X1: Inspect or Test at Specified Frequency X2: Random Inspection or Test | | | | QP: Quality Plan  RFI: Request for Information NCR: Non-Conformance VC: Verification Checklist  XXXX: Sequential Number from Doc Control | | |
| **DDD – Types:** B – Building, C – Civil, G – General, M – Mechanical & Electrical, I – Motorway Operations System (ITS), S – Structure, O – Tolling, T – Tunnel, U – Urban Design & Landscape | | | | | | | | | | | | | | | | | |
|  | | **Name** | | | **Signature and Date** | | | **Spark-NELPP REP** | | **Name** | | | | | | | **Signature and Date** |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project**: SPARK – North East Link Primary Package **Client:** State of Victoria and the North East Link State Tolling Corporation | | | | | | | | | | | | |  |
| **ITP Title: Conduits (Trenching and Install)** | | | |  |  |  |  |  |  | **References:**  PSDR, IFC Drawings | |  |
| **Description:** This ITP covers the trenching and installation of conduits – project wide. | | | | | |  |  |  |  | **Standards:** VR733, VR703, TC-1220, AS 3000, TC-1230, AS 1345, AS 2053, AS 2566, TC-2203 | | |
| **ITP No**: NEL-CNT-SDC-2990-PQA-ITP-0042 **Rev No**: 0  **Lot No**: **Location**: **Ch**: **to Offset: to Layer**: | | | | | | | | | | | | |
| **Item No.** | **Responsible Person** | **Inspection and Test**  **Activity** | **Specification Reference** | **Acceptance Criteria** | **Test Method** | **Test Frequency** | **Inspection/Verification (Name, signature & date)** | | | | **Records/Documents** | **Field Notes / Comments** |
| **Sub- Contractor** | **Spark NEL Engineer** | **Nominated Authority** | **IREA** |  |  |
| **Supplier/Subcontractor**  **:**  **(If applicable)** | |  | |  |  | |  | | | | |  |  |

**Lot closure comments**:

**Spark NELP QA Rep**:

**Name Signature: Date:**