

Inspection and test plan – Carbon Steel Installation

**Project no.**  CC0398 **Project name**  VIVA ULSG **Date**  05/03/2024 **Approved by**  Ari Birch **ITP no.**  034 **Revision no.**  B **Revision date**  26/03/2024 **Plant and equipment used**  Excavator, Bobcat, Welder, **Lot no.**  **Location (chainages, detailed description or marked up plan)**

Attach Dockets, Certificates and QA Documents to ITP

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | | | | | **Verification of acceptance by** | | | | **Remarks / record (eg. test frequency, reports, certificates,**  **checklist etc)** |
| **Symal Infrastructure** | | **MDR/VIVA** | |
| **Item no.** | **Activity** | **Ref docs** | **Acceptance criteria** | **Acceptance** | **Key** | **Sign date** | **Key** | **Sign date** |
| **1.0 Preliminaries** | | | | | | | | | |
| **1.1** | Set out |  | Is the position of the pipe in accordance with the drawings?  IFC and latest available revision used? | * Yes ☐ No ☐ N/A | H |  | W |  |  |
| **1.2** | IFC Submission & Approval | Isometric Drawings | Is IFC Construction Drawing and Most Current Revision Approved by the client? | * Yes ☐ No ☐ N/A | H |  | H |  | * Isometric Drawings |
| **1.3** | Permits | Symal Safety Procedure | Have the below permits been created.  -GPP  -Working at Heights  -Hot Works  -Confined Space | * Yes ☐ No ☐ N/A | H |  | W |  |  |
| **1.4** | Determine Lot Size |  | What is the lot size? | * Yes ☐ No ☐ N/A | S |  | W |  |  |
| **1.5** | Free Issue Materials |  | Have the free issue materials been accepted and checklist completed?  Have the materials and tag numbers/heat numbers been verified? | * Yes ☐ No ☐ N/A | W |  | W |  | * Material Inspection Checklist |
| **1.6** | Pre-Qualifications | Welder Qualifications and tickets.  This ITP | Welding procedures, equipment to be used, welding qualifications and calibration of welding machines to be submitted and approved by the client, has this been completed?  Has the training records for the STOPAQ applicators been provided? | * Yes ☐ No ☐ N/A | H |  | H |  | * Welding Qualificaitons |

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | | | | | **Verification of acceptance by** | | | | **Remarks / record (eg. test frequency, reports, certificates,**  **checklist etc)** |
| **Symal Infrastructure** | | **MDR/VIVA** | |
| **Item no.** | **Activity** | **Ref docs** | **Acceptance criteria** | **Acceptance** | **Key** | **Sign date** | **Key** | **Sign date** |
|  |  |  |  |  |  |  |  |  |  |
| **1.7** | Bedding and Backfill Materials Approval | 235929-000- CV-SP-00006  UG PIPE  FAB and INSTALL  Section 12.1.8 | Has bedding and backfill materials been approved for use? | * Yes ☐ No ☐ N/A | H |  | H |  | * Material Approval |
| **2.0 Excavation and bedding** | | | | | | | | | |
| **2.1** | Service Location | DBYD &  Services marked on current IFC drawings (if  applicable) | Current DBYD documents received and works executed by qualified service locator | * Yes ☐ No ☐ N/A | H |  | S |  |  |
| **2.2** | Excavation | 235929-000- CV-SP-00006  UG PIPE  FAB and INSTALL  Section 12.1.12 | Excavation shall be to depth adequate to provide full specified bedding depth of 100mm.  Minimum trench width as per manufacture specifications pg. 17 is 1.25 x OD + 300mm.  Earthworks for trenches shall be done in  accordance with standard drawing, has this been completed? | * Yes ☐ No ☐ N/A | W |  | S |  |  |
| **2.3** | Bedding material | 235929-000- CV-SP-00006  UG PIPE  FAB and INSTALL  Section 12.1.8 | Has the bedding material been installed as per the manufacturer’s specification?  Conforms IFC drawing (if applicable)? Bedding depth minimum 100mm Overlay depth minimum 300mm. | * Yes ☐ No ☐ N/A | S |  | S |  | * Delivery Dockets |

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | | | | | **Verification of acceptance by** | | | | **Remarks / record (eg. test frequency, reports, certificates,**  **checklist etc)** |
| **Symal Infrastructure** | | **MDR/VIVA** | |
| **Item no.** | **Activity** | **Ref docs** | **Acceptance criteria** | **Acceptance** | **Key** | **Sign date** | **Key** | **Sign date** |
| **3.0 Fabrication** | | | | | | | | | |
| **3.1** | Welding | 235929-000- CV-SP-00006  UG PIPE  FAB and INSTALL  235929-RE- ENG-INT- 0003-WIITP – P11U  235929-RE- ENG-INT- 0003-WIITP – P11P  RE-ENG-INT- 0072-PR | Have the lengths been welded as per the manufacturers spec and welding duration? | * Yes ☐ No ☐ N/A | H |  | W |  | * Carbon Steel Subcontractors ITP * Welding Log |
| **3.2** | Non-Destructive Testing | 235929-RE- ENG-INT- 0003-WI  235929-RE- ENG-INT- 0003-WIITP – P11U  235929-RE- ENG-INT- 0003-WIITP –  P11P | Have the welds been tested as per the ITP’s referenced in the isometric drawings? | * Yes ☐ No ☐ N/A | H |  | W |  | * Carbon Steel Subcontractors ITP |
| **3.3** | Coating and wrapping | 235929-RE- ENG-INT- 0003-WI | Has the application procedure been provided to MDR and approved? | * Yes ☐ No ☐ N/A | H |  | W |  | * Carbon Steel Subcontractors ITP |

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | | | | | **Verification of acceptance by** | | | | **Remarks / record (eg. test frequency, reports, certificates,**  **checklist etc)** |
| **Symal Infrastructure** | | **MDR/VIVA** | |
| **Item no.** | **Activity** | **Ref docs** | **Acceptance criteria** | **Acceptance** | **Key** | **Sign date** | **Key** | **Sign date** |
|  |  | 235929-RE- ENG-INT- 0003-WIITP – P11U  235929-RE- ENG-INT- 0003-WITP – P11P  Isometric Drawings  RE-ENG-INT- 0045-PR | Have the welds been wrapped as per the drawings and specification? |  |  |  |  |  |  |
| **4.0 Laying** | | | | | | | | | |
| **4.1** | Lifting into trench | 235929-000- CV-SP-00006  UG PIPE  FAB and INSTALL  Section 12.2.1  Item 12.2.7 | Before lowering in, caps shall be placed on open ends, flanges, etc., which shall remain in place until piping connection can be made. Particular attention shall be given to the need to protect pipes from damage due to loads from heavy plant, has this been completed?  Have pipes been laid to true line and level? | Yes ☐ No ☐ N/A | H |  | S |  |  |
| **4.2** | Haunching | 235929-000- CV-SP-00006  UG PIPE  FAB and INSTALL | Has the backfill material been haunched appropriately around the pipe? | Yes ☐ No ☐ N/A | W |  | S |  |  |
| **4.3** | Pressure Testing | 235929-000- CV-SP-00006  Section 13.4 | Is Air Testing or Hydrostating testing being completed?   * Air Testing * Hydrostatic Testing   What is the test pressure? | * Yes ☐ No ☐ N/A | H |  | W |  | * Testing checklist |

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | | | | | **Verification of acceptance by** | | | | **Remarks / record (eg. test frequency, reports, certificates,**  **checklist etc)** |
| **Symal Infrastructure** | | **MDR/VIVA** | |
| **Item no.** | **Activity** | **Ref docs** | **Acceptance criteria** | **Acceptance** | **Key** | **Sign date** | **Key** | **Sign date** |
|  |  |  | Has Testing been conducted to all joints and inspected to confirm no leaks? |  |  |  |  |  |  |
| **4.4** | Backfill Materials | 235929-000- CV-SP-00006  UG PIPE  FAB and INSTALL | Has Sand Back fill been placed to 300mm above Pipe?  No compaction equipment to be used until 300mm above pipe.  Has select backfill been placed in layers not exceeding 150mm loose thickness?  No compaction equipment has been used between 0-300mm above top of pipe, light compaction equipment has only been used from 300-600mm. above pipe. | Yes ☐ No ☐ N/A | W |  | S |  |  |
| **4.5** | Backfill and Compaction | 235929-000- CV-SP-00006  UG PIPE  FAB and INSTALL | Sand Fill - not less than 90% of maximum density or 70% of relative density, except that under paved areas the entire depth shall be compacted in 150mm layers to not less than 95% of maximum density or 80% relative density.  Select Fill - Backfill under pavements shall be compacted to a dry density ratio of no less than 98% modified comp active effort.  Backfill to be in 250mm compacted layers.  Testing Frequency: Minimum 2 field density tests for each 185 m2 of each compacted fill layer, but no less than 3 tests for total area  Has compaction testing been completed as per the project specifications? | * Yes ☐ No ☐ N/A | W |  | S |  | * Compaction Testing Results |
| **5.0 Testing and Conformance Check** | | | | | | | | | |
| **5.1** | Test Pack |  | Has a test pack been provided? | * Yes ☐ No ☐ N/A | H |  | H |  | * Testing Log |

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | | | | | **Verification of acceptance by** | | | | **Remarks / record (eg. test frequency, reports, certificates,**  **checklist etc)** |
| **Symal Infrastructure** | | **MDR/VIVA** | |
| **Item no.** | **Activity** | **Ref docs** | **Acceptance criteria** | **Acceptance** | **Key** | **Sign date** | **Key** | **Sign date** |
|  |  |  | Test pack to include.   * Test Procedure * Test Map * Equipment Calibration * Equipment Details * Exclusion zones if require   Provision of testing log template |  |  |  |  |  |  |
| **5.2** | Survey |  | Tolerances in alignments shall be limited to +/- 25 mm vertically or horizontally, unless otherwise specified on engineering drawing, has this been  completed? | * Yes ☐ No ☐ N/A | W |  | W |  | * Survey as-built |
| **5.3** | Quality Submission |  | Have all QA documents in-line with the specification been provided to MDR for review? | * Yes ☐ No ☐ N/A | H |  | H |  |  |
| **Comments**: | | | | | | | | | |

**Lot acceptance:**

Symal Infrastructure representative name MDR representative name

Symal Infrastructure representative signature MDR representative signature

**Inspection key: W –** Witness, **H –** Hold Point, **S -** Surveillance