## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | ITP-019-CIV - Conduit & Pits - Rail (Supply and Install) | itp |  |  |  | Yes | ITP-019-CIV - Conduits & Pits - Rail (Supply and Install) | 10482046-fbfb-4ebb-93c9-6e3092ba1ab9
checkpoint-group |  |  | section | 1. Referenced Documentation
checkpoint-no-status |  |  | checkpoint | 1. Referenced Documentation
label | f5f2e605-ff9c-584e-8af5-7e105d3e9ed7 |  | note | ITP-019-CIV-Brunt-Conduit & Pits-Rail (Supply & Install)
label | f0c9db2b-f6bc-5d22-9dd1-ae628970b8dd |  | note | Conduit & Pits - Rail (Supply and Install)
label | afc16df7-5ab8-5198-8002-4f59cf4c9793 |  | note | CIV
label | 3e7dbcb5-8836-5dd3-aa82-50aff6ba3407 |  | note | 0
label | f52cd485-d011-5213-b0d3-d775f181853e |  | note | 13/01/2023
label | 9fe5cd5f-a9b1-58f0-bf27-c56f3d61f756 |  | note | Shubham Bajaj (Sammy)
label | 5ca1fb1d-3644-589e-8a7a-60567332f935 |  | note | Jon De Castro
label | 66f93ac0-90cb-5f8b-818f-7cc762e4f33a |  | note | This ITP is to be used in Brunt Rd only.
checkpoint-status |  |  | checkpoint | 1.1 - Non Dependent
label | 7000b2a5-bc0b-5dae-bf94-1a50fe67650d |  | note | Reference - IFC Drawings L1-CHE-STD-043 (VRIOGS 012.2.1) L1-CHE-SPE-070 Australian Standards MRPA Standards
checkpoint-group |  |  | section | 2. Preliminaries - Materials
checkpoint-status |  |  | checkpoint | 2.1 - Conduits
label | 1a2e5641-4981-55cc-95d8-bc200ee6d9ed |  | note | Reference - HV Conduit: AS 2053 - HV Conduit (boring): AS 4130 - Comms Conduit: AS/ACIF S008:2006 - LV Conduit: AS/ NZS 3000 - 2000. - L1-CHE-STD-043 - L1-CHE-SPE-070-
label | c3d31b76-c761-5345-b989-1782e338d2c3 |  | note | Acceptance Criteria - LV & Signalling: 100Ø (114mm OD), orange electrical heavy duty 5.9mm wall thickness LV & COMMS CONDUITS TO HAVE A MIN 600mm BENDING RADIUS Inspect materials upon delivery and attached delivery dockets.
label | 54d92a46-d7e3-5eb9-9039-59f8c16a520e |  | note | Method - Visual Document Review
label | 68014b69-0e72-5ca5-b207-573c74db7ee6 |  | note | Frequency - Each Material Type, Each Delivery
label | 23932b10-fbad-5efb-a718-483460d0852a |  | note | Category - IP
label | e3997368-ffcd-521a-9481-1722e2f3a753 |  | note | Responsibility - SE/PE
label | 11fb24a2-bfef-56be-a396-0518a4e98791 |  | note | Verifying Documents - Attach Material Conformnace Certs Attach delivery dockets
checkpoint-status |  |  | checkpoint | 2.2 - Pits and Pit Lids
label | 3e25cad9-a5a5-540a-b3bc-169967ed69e8 |  | note | Reference - IFC Drawings -VRIOGS -012.2.1 Section -6.15-16 - VRIOGS 012.2.1 Section 6.9 - VRIOGS 012.2.1 Cl. - 6.7 (c) - L1-CHE-SPE-070 Cl. -10 -AS1289-
label | ae0286d0-bfa8-52c3-b81b-d34f38a74fa4 |  | note | Acceptance Criteria - Pits: -Pits located within 1.5m of nearest rail, pit to be 300LA Railway loading - Pits 900x900mm or greater, multipart pits lids to be used. -Pit Lids: Pit Covers shall comply with AS3996-2006 - Pit lids in trafficable areas to be Class D, non-trafficable areas to be Class C. - LV, Comms Cover: pit covers shall be labelled with the words “RAILWAYS SIGNALS & COMMUNICATIONS” (L1-CHE-STD-043 14.6) -Inspect materials upon delivery and attached delivery dockets.-
label | 6f680932-7548-51b9-8592-1b43c44ac4ce |  | note | Method - Visual Document Review
label | 3fd0dfdc-c724-53bb-9d01-9ef21ebadbf5 |  | note | Frequency - Each Material Type, Each Delivery
label | 10f7d7b4-8b90-56ae-85d6-c42f7334aff9 |  | note | Category - IP
label | 3db869ea-2788-541a-90c6-abbb10af596a |  | note | Responsibility - SE/PE
label | 1ce80539-56e1-5d21-8c31-2ddb03ddef03 |  | note | Verifying Documents - Attach Material Conformnace Certs Attach delivery dockets
checkpoint-status |  |  | checkpoint | 2.3 - Warning/Marker Tape
label | 19b8d005-9b23-575f-ad8a-ec7bd8cf25bb |  | note | Reference - IFC Drawings AS/NZ 2648.1 TS-SP-013 L1-CHE-STD-043 6.4
label | 5d829ec8-65ac-541c-8a45-2a85037768b6 |  | note | Acceptance Criteria - Warning/Marker Tape: Above LV: 150mm minimum wide orange coloured PVC ‘DANGER RAILWAY SIGNALLING CONDUITS’
label | 9436ed88-be1b-5186-adc4-acf6a5e58844 |  | note | Above Comms: 75mm minimum wide white coloured PVC ‘WARNING COMMUNICATIONS CABLES’ with an embedded stainless steel trace wire to be laid directly above trenched VicTrack assets
label | d5235150-3157-515e-99a4-3f24dd0aee4d |  | note | Above HV: 300mm minium width orange coloured PVC 'Danger - Electrical Cable Below'
label | 0d5cf6cb-aeb5-50db-b8cb-6b06bcb86af6 |  | note | Inspect materials upon delivery and attached delivery dockets.
label | 95970bf9-eb68-54b8-9f13-327dc13025bb |  | note | Method - Visual Document Review
label | aecdd65e-1b37-59c4-ba7f-7f10e9aeb314 |  | note | Frequency - Each Material Type, Each Delivery
label | 4702353a-b047-5b10-aad3-458147742f9d |  | note | Category - IP
label | c8f17d97-c376-5fc4-be9b-1e94ceb95668 |  | note | Responsibility - SE/PE
label | e89f21bd-5d8a-54c1-918d-7d7a8fc28fdc |  | note | Verifying Documents - Attach Material Conformnace Certs Attach delivery dockets
checkpoint-status |  |  | checkpoint | 2.4 - Protection Barriers
label | 8a37118a-3924-587e-9d51-45abc496b36b |  | note | Reference - IFC Drawings L1-CHE-STD-070 10.3.3 AS4702
label | 3120690f-430e-5e26-85a8-28c6eba85fd8 |  | note | Acceptance Criteria - Protection barriers shall be polymeric cable protection covers complying with AS4702 OR a min. 40mm thick concrete barriers (pavers) not less than 15MPa at 28 days Inspect materials upon delivery and attached delivery dockets.
label | 62f63b42-6498-5138-bdd6-2b68dc7223c2 |  | note | Method - Visual Document Review
label | 1ba15ade-ffe0-52ae-908e-e7300d019009 |  | note | Frequency - Each Material Type, Each Delivery
label | 845efd91-d37e-546a-8834-ceb2e6ac1b08 |  | note | Category - IP
label | 5b24d959-e81f-5a69-93fb-dcb02eeec2c9 |  | note | Responsibility - SE/PE
label | 0813e889-c9db-59e8-a322-ece83e6afc78 |  | note | Verifying Documents - Attach Material Conformnace Certs Attach delivery dockets
checkpoint-status |  |  | checkpoint | 2.5 - Backfill Material (stabilised sand)
label | fc849307-a4b8-5fbe-b51f-dc89f84a10fb |  | note | Reference - IFC Drawings L1-CHE-STD-043 Section 2 Table 1
label | b41d9d70-017a-585f-8ed3-289ee2a0aaee |  | note | Acceptance Criteria - Material free of rocks that will not pass a 30mm sieve. The material shall be free or organic matter or anything that could dmanage the conduits. Inspect backfill material. Attached delivery dockets (if applicable).
label | ac059ad7-e386-50fd-8eb8-a22e4860a703 |  | note | Method - Visual Document Review
label | 26ff958e-9fe5-5fb6-9e2a-59480aa1c5d7 |  | note | Frequency - Each Material Type, Each Delivery
label | 716dd006-8d38-5f23-a5ec-ded1f6edd0ed |  | note | Category - IP
label | b6d4af4d-2f94-5fd9-86b3-2745c04fe548 |  | note | Responsibility - SE/PE
label | 14094ae7-514e-5061-8ec9-0741b90906b0 |  | note | Verifying Documents - Attach Material Conformnace Certs Attach delivery dockets
checkpoint-status |  |  | checkpoint | 2.6 - Bedding Sand
label | 51d353cf-3d5b-58f7-8b2e-801c52de9767 |  | note | Reference - IFC Drawings AS2758.1
label | d1ea6e61-fa75-5bf5-b068-271597493481 |  | note | Acceptance Criteria - Bedding Sand shall be a clean sand that is an uncrushed fine aggregate to AS2758.1 and shall have a thermal resistivity ≤ 1.2 °Cm/W at 5% moisture content.
label | 4cabd3b2-444e-5c86-b36d-a2f87bae9cdb |  | note | Method - Visual Document Review
label | cc9d9b7a-f81e-516e-aa3d-3b6cbce30f9f |  | note | Frequency - Each Material Type, Each Delivery
label | 8e497d93-d921-52ad-b9de-462b06835397 |  | note | Category - IP
label | d821f960-9a70-5aea-b5b8-941981a8112b |  | note | Responsibility - SE/PE
label | 49c522d3-32af-5770-b482-8f74b7cd6b93 |  | note | Verifying Documents - Attach Material Conformnace Certs Attach delivery dockets
checkpoint-status |  |  | checkpoint | 2.7 - Draw Wires
label | a21e2381-b3d6-5832-86fb-a784bfe99c26 |  | note | Reference - TS-SP-013 AS 4142
label | 0b4ce6d4-b3fe-59fd-a676-66e6b87785ea |  | note | Acceptance Criteria - 6 mm diameter polypropylene blue/yellow
label | f21dc47a-2e1c-580e-8c32-8854cf5a1993 |  | note | Method - Document Review
label | b654a229-62e4-5c0c-9672-68155b9951cc |  | note | Frequency - Each Material Type, Each Delivery
label | 5a700b49-8951-529e-885f-07db9bc61451 |  | note | Category - IP
label | b82b10fd-92cf-5c55-91d8-49b047feee63 |  | note | Responsibility - SE/PE
label | 360f9dff-4221-53fc-b4d4-8fd22ff186fa |  | note | Verifying Documents - Attach Material Conformnace Certs Attach delivery dockets
checkpoint-status |  |  | checkpoint | 2.8 - Concrete Mix - Trench
label | 2486c569-a575-5c8c-8361-42253ea4e5d3 |  | note | Reference - L1-CHE-STD-043
label | 5ac4b019-c799-5d47-8df3-e989f6157aaa |  | note | Acceptance Criteria - Concrete strength at 28 days shall be not less than 25MPa. Chemical admixtures or fly ash shall not be used
label | ade23e7d-b422-5e50-a3be-9029fcef81f6 |  | note | Method - Document Review
label | 3ee93585-2698-571e-9ae7-a42078825a96 |  | note | Frequency - Each Material Type, Each Delivery
label | 38021260-8f68-5365-86ed-8f3e22321111 |  | note | Category - IP
label | 8e854544-7261-5fa5-ae92-e8b580c1c1b8 |  | note | Responsibility - SE/PE
label | 61f5a9f6-b3ad-57e0-b62c-e537cf55d778 |  | note | Verifying Documents - Attach Material Conformnace Certs Attach delivery dockets
checkpoint-group |  |  | section | 3. Prelimnaries - Procedures & Documentation
checkpoint-status |  |  | checkpoint | 3.1 - Services
label | 4f73390a-8ec7-53eb-8615-d8048612bf66 |  | note | Reference - Services CAD file
label | c09a53c8-0b92-526f-b220-c5fad1f72f2b |  | note | Acceptance Criteria - All services within 5m of Excavation location have been identified and appropriate control in place (refer to MRPA Excavation Permit). Survey to mark out existing services.
label | c393a1cd-e412-5246-8075-87b442734d00 |  | note | Method - Visual
label | 0826e828-aba0-52b6-af9b-90fb81c34d1c |  | note | Frequency - Prior to commencement of works
label | d8d5aa4a-63f6-52b0-9d6a-92d162a7c422 |  | note | Category - IP
label | 8c0e5a58-f118-5d28-b448-b2f09b7dae34 |  | note | Responsibility - SE/Site Supervisor
label | 0909aeb7-c15d-5225-9927-f18967cc6645 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 3.2 - CSR Works Procedure
label | 8319042b-97b4-5cdb-b6e8-cd9b41899a81 |  | note | Reference - WAP_BRU_201
label | 7daf1245-ba81-5550-86f4-61233f160119 |  | note | Acceptance Criteria - WAP to be reviewed and signed by all relevant stakeholders along with Rail Safety highlighting works proedure with in the Rail Corridor
label | a3bd840e-d56d-5867-b484-1b5696fe3676 |  | note | Method - Document Review
label | 96afa029-bc3e-577b-820a-aed15b8e1eba |  | note | Frequency - Prior to commencement of works
label | ccb15b3c-7f02-5c38-8ae6-388c4ca1f523 |  | note | Category - HP*
label | b12b12c5-e50f-537b-966b-a67c4c38058e |  | note | Responsibility - SE/Site Supervisor
label | d477e924-b384-5633-aa9f-415cfaafa7d9 |  | note | Verifying Documents - This ITP
checkpoint-group |  |  | section | 4. Pre-Construction Activities
checkpoint-status |  |  | checkpoint | 4.1 - Survey Set-out
label | f6aeb431-97df-5c58-bb61-dc9a0b8b5e77 |  | note | Reference - IFC Drawings
label | f7897f00-4768-56e1-8432-2bb08cd26ee9 |  | note | Acceptance Criteria - Survey to set out trench alignment and pits, and establish construction control (alignment and level).
label | f4edd5ff-826c-51e4-ae2c-3f4df49d42bf |  | note | Method - Measure Visual
label | 9c72ceb0-cc50-5349-9a1a-e7c19cd92c03 |  | note | Frequency - Each element
label | f31f08b2-fe81-57a8-8c23-788ba4595e82 |  | note | Category - IP
label | 1e809443-e7fd-5a69-976d-13ed6d43af32 |  | note | Responsibility - Surveyor SE/Site Supervisor
label | 8da1f169-a897-50d7-b3e0-2bffb7c13808 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 4.2 - IFC Drawings
label | c8553c6f-7ddb-59e9-88a3-b0437d52b970 |  | note | Reference - IFC Drawings
label | 7f3eba87-8ebf-5d9d-971e-f088c39da223 |  | note | Acceptance Criteria - Check the revision of the IFC drawings are current as per the drawing register (on Teambinder)
label | c6ed01ca-d710-504c-b0c9-5332568ac2f1 |  | note | Method - Document Review
label | 16802713-3117-5e2d-9748-4e371b0b2e82 |  | note | Frequency - Prior to commencement of works and at regualr intervals
label | e01a3a4f-6a54-58ac-8a42-5f8690c55db3 |  | note | Category - IP
label | 97af38ec-7cbd-596d-bfb2-9e1272409415 |  | note | Responsibility - SE/Site Supervisor
label | 6891a9b3-b37e-5cd8-a15d-ec70b3dfe123 |  | note | Verifying Documents - This ITP
checkpoint-group |  |  | section | 5. Construction Activities
checkpoint-status |  |  | checkpoint | 5.1 - Trench Excavation
label | 31e168b2-9b16-574a-9a51-148afc20d816 |  | note | Reference - IFC Drawings L1-CHE-SPE-070 7.3 Table 2 L1-CHE-STD-043 L1-CHE-STD-070 7.1c
label | 2f9938d0-2e44-5cc7-881e-de3d6d132396 |  | note | Acceptance Criteria - Trench profile and depth as per IFC drawings. Edge of trenching to be a min. 2m from strucutres/pile foundation (unless it is mounting the structure) and a min. 4m from the rail for HV and 3m from the rail for LV & Comms The bottom of the cable trench shall be level across its width and free from any protrusions and rubble that could cause damage to the conduits. The width of the trench shall be not less than 200 mm (chain or bucket excavation) or 300 mm (backhoe and other).
label | 7a311320-809c-5cda-99c1-a58ad60e15df |  | note | Method - Measure, Visual
label | cd04608c-d208-5eef-8240-b4698fd1a48a |  | note | Frequency - Each lot
label | 778f455a-959c-5590-8031-ef84bf5c9add |  | note | Category - IP
label | 6277b753-4ad2-5b12-a03f-c15a18415412 |  | note | Responsibility - SE/Site Supervisor
label | 573388ad-968d-54b3-b39f-68ac3df1a654 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.2 - Trench Stability
label | 0ee562ce-980e-5d98-a929-fb2516f7ad67 |  | note | Reference - L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings MRPA Standards
label | 9b31f2f2-f67a-5dc7-b6d8-49f17f2ed42d |  | note | Acceptance Criteria - Trench stability check: - Shoring, - benching - geotech signoff Attached Geotech Report
label | f752b05d-52c0-5310-b989-53e8db433feb |  | note | Method - Visual, Document Review
label | 818f1ecb-2a23-5c7c-9321-534fbd702df8 |  | note | Frequency - Each lot
label | 3922c741-b48d-5a37-902b-30ef7ba69a6d |  | note | Category - IP
label | 3fac6657-ca7c-5acf-b904-358b78739879 |  | note | Responsibility - SE/Site Supervisor
label | 0ec11a44-ddf6-5098-829b-d7734e37c8b9 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.3 - Placement of Bedding Sand for Conduits
label | 983ca552-ff7a-5bc6-a7b7-00717df3ec87 |  | note | Reference - IFC Drawings L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070
label | 11382dbc-f616-5d2b-8114-852ca946134d |  | note | Acceptance Criteria - 100mm of bedding sand/crusher dust to be places at the base of trench.
label | 48470d92-f1a2-5c0b-ba79-7a3e8fda940f |  | note | Method - Measure, Visual
label | f485fae3-901e-565d-8d75-66450f1cc5d4 |  | note | Frequency - Each lot
label | f01b30b1-e20d-5242-a146-d007e3b1de9e |  | note | Category - IP
label | c31b5283-1499-52dc-abf3-eb7f3f39373d |  | note | Responsibility - SE/Site Supervisor
label | 07751179-7e43-50e8-879c-f3c1223e2ef6 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.4 - Conduit Placement & Configuration
label | a6c6b201-e994-5a4b-8b9b-87613f485936 |  | note | Reference - IFC Drawings L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 L1-CHE-STD-077
label | 6de8075a-c26c-5171-9ce8-56f63142f8c8 |  | note | Acceptance Criteria - Conduits are configured in accordance with IFC drawings and meet cable separation requirements. Min Cover - HV: 1000mm - VicTrack: 650mm - Signalling: 800mm - LV: 800mm - Electrolysis: 800mm - SCADA: 800mm - MTM Comms: 600mm - 800mm below water coarses (stab sand encasement) - 1200mm Under VicRoads Roads & top of Rail - 900mm below council roads
label | 52109e8f-9d0e-589f-8091-e91f4fc75f29 |  | note | Method - Measure, Visual
label | 97cb5454-4ebc-54df-abcf-d5e494d0084f |  | note | Frequency - Each lot
label | e9b3c849-24ff-5da9-926a-8406ada3e9db |  | note | Category - IP
label | 748bfda5-fef7-5f7c-a2fe-4a11dea5395d |  | note | Responsibility - SE/Site Supervisor
label | 9c7f27fb-4453-52c9-8360-78a13731a27d |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.5 - Separation of Services
label | bf75eb71-d0c9-5f1c-8061-5fbc9cedbc2f |  | note | Reference - L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 L1-CHE-STD-077 IFC Drawings
label | 47d107ae-3f46-54c1-a688-c821d3de20e3 |  | note | Acceptance Criteria - Separation of services - HV: Min. seperation distance between HV conduits at least 50mm - VicTrack: fiber 300mm from HV - Utility: 300mm to utilities - Rail: When conduits are within 2.1m of edge of sleeper they must be encased in stab sand or cover is to be increase to 1.2m
label | 9271bbb6-803d-5e26-bdc2-3a021bb59326 |  | note | Method - Measure, Visual
label | b820c892-0aab-589d-a39f-3cb44fd00e65 |  | note | Frequency - Each lot
label | ad4a7b47-e6ab-5b59-bc84-3cdf7ec1b622 |  | note | Category - IP
label | b4749dd0-3fc0-5b99-9d94-f408dff65d72 |  | note | Responsibility - SE/Site Supervisor
label | 5eb73bd7-ca90-5d00-8875-d513ba020e2e |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.6 - Joints
label | be6757fb-0a1f-5b38-81c1-de267131a034 |  | note | Reference - L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings
label | ab06d936-00cd-5449-9514-8c47754b54dd |  | note | Acceptance Criteria - All conduit joints shall be made by utilising the spigot and socket ends. Ends to be joined shall be thoroughly cleaned using a solvent approved by the conduit manufacturer. The joint shall be impervious to water and shall be glued with an adhesive approved by the conduit manufacturer. Socket ends to be placed firmly into the spigots then hit with a mallet to ensure a sound connection
label | 9e99e3dd-4735-531d-ba78-3354093d1c2e |  | note | Method - Visual
label | 5ab51977-7faf-5117-825d-0c58294707c5 |  | note | Frequency - Each Joint in each trench
label | 1bb473e9-4570-53a2-866f-a867909b3e28 |  | note | Category - IP
label | a99fb1e4-d449-5582-918f-6ae36fcd2d7c |  | note | Responsibility - SE/Site Supervisor
label | 8b4e2294-bed6-57b4-b92a-58b401ca99a9 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.7 - Conduit Inspection
label | ced848d7-c95c-57d6-a01b-af82f8c1deed |  | note | Reference - L1-CHE-STD-070 16
label | 8cfdbd39-e3a6-5921-af8a-c517ce021eb9 |  | note | Acceptance Criteria - Provision shall be made for inspection of cable routes by NA, MTM/VicTrack representatives prior to backfilling.
label | 1ba591ac-2b8c-5e28-b8b4-522b06af1aa9 |  | note | Method - Visual
label | 68d52625-82e0-572e-968b-cbd969d7a9ce |  | note | Frequency - Each lot
label | 1daccdff-ce36-51a2-82d4-821f5796a3a1 |  | note | Category - HP*
label | 1b796cec-32f5-5db6-9ce7-a0fe75e55267 |  | note | Responsibility - SE/PE MTM / VicTrack Rep.
label | 196fd312-0ab9-5d12-a924-b8e6ab16735d |  | note | Verifying Documents - This Itp
checkpoint-status |  |  | checkpoint | 5.8 - Bedding Sand Installation
label | 6439821d-3b0a-539e-a5bd-a29205128f05 |  | note | Reference - L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 CL13.1 IFC Drawings
label | 72a7b0e5-1a18-5401-b9ab-1f968be75fcc |  | note | Acceptance Criteria - Bedding sand/crusher dust extends 50mm past edge of conduits. Bedding sand/crusher dust extends 100mm above conduits. Attach Delivery Dockets
label | 661712aa-8df0-5490-818b-e209e90f1993 |  | note | Method - Visual
label | eecd0b27-272b-5097-9354-1ed3696afb05 |  | note | Frequency - Each lot
label | a4985578-d821-5d17-b35e-f3ce1478f9e4 |  | note | Category - IP
label | daac82f3-f1fb-5e29-b525-218b85b0082f |  | note | Responsibility - SE/Site Supervisor
label | 5abb78f0-df4a-5bb6-9158-a11045bf9abb |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.9 - Marker Tape
label | 2ee9f90e-4145-5378-a563-2f07150328eb |  | note | Reference - L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-SPE-070 Cl10.3.3
label | ea796636-5a11-508f-bc19-296cc487ec72 |  | note | Acceptance Criteria - Warning Tape installed a min. 300mm above top conduit or a min. 300mm above HV protection barrers. Tape to be one continuous length. VicTrack to inspect the Marker Tape placement..
label | 75fcfd03-06b3-5a50-bbaf-7f81adb1f4e8 |  | note | Method - Visual
label | 6ca8df7e-7644-5467-bccd-bc1d15389b7c |  | note | Frequency - Each lot
label | 6ec070f3-d5b1-5108-970a-408932a29d3a |  | note | Category - HP*
label | c52de600-d7ed-5fcf-bb40-0c1b9eb6736b |  | note | Responsibility - SE/PE MTM / VicTrack Rep
label | c9e61785-68a2-541a-8140-f35aa48d2b15 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.1 - Backfill Installation for Conduits
label | 1215f506-abf1-5139-9ca9-ede5e01cf9be |  | note | Reference - IFC Drawings L1-CHE-STD-043 clauses 6.15 and 6.16
label | edc87b66-8158-5c51-bc1f-d5d8c7bd32d3 |  | note | Acceptance Criteria - Backfill per trench profile - 150mm layers of 3% stabe sand - conduits under water ways to have 800mm cover from base of water way and backfilled with 3% stab sand
label | 2f4d802d-425e-5859-a56e-297e22e71eb5 |  | note | The trench shall be finished with a slight mound, height equal to approximately 25% of trench width, to provide for further settlement
label | e9f9cb0a-8098-509d-8a1d-82263a9db34b |  | note | Trenches under road pavement - backfill to be same material as the road formation material.
label | 8451879b-4f26-5339-9b7f-c910670d5e39 |  | note | Trenches immediately adjacent to footing shall be 3% stab sand. To be thoroughly placed to fill all voids without placing undue strain on or cause displacement of conduits
label | 3f000d7c-733d-58b8-b372-7630f7aa04ac |  | note | When conduits are within 2.1m of edge of sleeper they must be encased in stab sand or cover is to be increase to 1.2m
label | 54fab800-c369-5e22-89c9-fe84dd44a732 |  | note | VicTrack to be notified and witness the first layer of backfilling.
label | 9a1821d5-508f-5050-a919-8bfaa59c1665 |  | note | Attached Delivery Dockets
label | 45f12870-344a-54de-a597-8347f0d98f16 |  | note | Method - Visual
label | 7f6780f7-4556-57aa-a027-dcfe4158bfbb |  | note | Frequency - Each lot
label | e054a422-473a-57dc-a243-abe0613a5c31 |  | note | Category - HP*
label | 4f7acf9a-7389-58b8-98cd-17c679e45b16 |  | note | Responsibility - SE/PE MTM / VicTrack Rep
label | 5160af98-1cdf-5927-8ca9-e8874b0522d9 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.11 - Signalling Pits LV Pits Electrolysis Pits SCADA Pits MTM Comms Pits
label | 6bec5f74-c885-5f3d-aef2-e757cee5278a |  | note | Reference - L1-CHE-STD-043 Cl7.14.o, Cl7.14.g
label | 1d8a676b-ac6e-5a5b-a758-fda8f59c4dd3 |  | note | Acceptance Criteria - - intervals no greater than 400m (electrolysis 190m) - 3m from rail - Access Roads, Class D lids - Footpaths and non traffiacl areas, Class C Lids
label | ca60609a-f573-574a-a8b1-e26df6cd0dd8 |  | note | Method - Visual, Measure
label | 19aea829-8f98-5e76-b018-1988f0372fa2 |  | note | Frequency - Each Pit
label | ee60dfc8-7418-50a8-9648-c5076a7b8666 |  | note | Category - IP
label | a44e682f-ab1a-5488-a3f1-6c8450159698 |  | note | Responsibility - SE/Site Supervisor
label | 215f8f04-4b82-5607-a92e-f2a0b83aa21b |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.12 - Additional Considerations
label | 21d3f3c6-1ed6-5144-b0ba-f8a1d3d68635 |  | note | Reference - IFC Drawings
label | ef0651f6-25f8-569f-b27e-c92a1eae2f6b |  | note | Acceptance Criteria - Access tracks to pits Safe access and egress (i.e. lid doesn't open up with workers back to the rail) Hand rail & retaining wall installed as required
label | 6bfe9811-c054-5aae-a9a0-6371e1d481a8 |  | note | Method - Viual
label | 3ca3f387-87ee-5d3a-8b58-96f53179df75 |  | note | Frequency - Each Pit
label | 45dea665-6bcd-56d4-bd84-7466e81e0a53 |  | note | Category - IP
label | 2064a6ac-9ee8-59bb-906f-188136bbb6d8 |  | note | Responsibility - SE/Site Supervisor
label | e285c370-3a67-5266-8817-540bf5059bf1 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.13 - Bedding for Pit Installation
label | 1d1acdf6-c1f3-5b02-abc9-9a446c743353 |  | note | Reference - L1-CHE-STD-070 Cl 7.21.u L1-CHE-STD-043
label | 82b8bb32-922b-5bbc-88d2-78360c8b0c88 |  | note | Acceptance Criteria - 150mm of crushed rock under pit extending 500mm past the pit Drainage arrangements shall be provided at the base of each pit. Attach Delivery Dockets
label | b456a94d-3797-5db3-af27-601c479058aa |  | note | Method - Viual, Measure
label | 2f97c633-239a-50c2-9837-9ca78c3d262f |  | note | Frequency - Each Pit
label | 5812cc8f-bc37-57b2-a63d-3ba306b406e2 |  | note | Category - IP
label | dfac8c14-7629-5348-af3d-be469b668120 |  | note | Responsibility - SE/Site Supervisor
label | d6594ec0-47f7-52c2-b28c-e671c275430f |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.14 - Pit Orientation
label | d21be06d-2f50-5a3c-96cd-1744f3e3b54a |  | note | Reference - IFC Drawings
label | 5dbffe02-ed8c-5dab-afa0-9e70abbb177a |  | note | Acceptance Criteria - Pit to be parallel to track and parallel to conduit route.
label | c53d0e23-54b9-5807-88f7-a62027ffd390 |  | note | Method - Viual
label | 623b01cb-b4be-50a1-8531-9a3d84396ccf |  | note | Frequency - Each Pit
label | 7612ded7-bb59-51c0-960b-c314d06053af |  | note | Category - IP
label | 2b960379-9c78-5540-8fe2-3df45f6b04fe |  | note | Responsibility - SE/Site Supervisor
label | a46448a1-6778-5d6d-9404-d45a2483a7d3 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.15 - Pit Installation
label | 31e183c5-69bf-5835-9bb1-23dc245d9fbf |  | note | Reference - IFC Drawings
label | 7cf89215-7515-5610-930e-4054b39d807c |  | note | Acceptance Criteria - Pit installed to design specifications Pit chamber floor to be 100mm lower than the underside of the lowest conduit.
label | 15dd1e46-b3fd-50cf-8881-0493526c6c5e |  | note | Method - Viual
label | d83f4381-0d7a-5b64-9c97-cc3fa783f34e |  | note | Frequency - Each Pit
label | 578f0d3b-e5ba-50f4-8103-9dc9021b71e3 |  | note | Category - IP
label | b8b56d36-719f-5a65-bcf0-b81c14c1854e |  | note | Responsibility - SE/Site Supervisor
label | 73f98bc9-2259-5b5c-b0a9-54fc79838d1b |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.16 - Conduit Entry onto Pits
label | 01c846da-35b1-5346-9efa-76909fbe342e |  | note | Reference - L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings
label | 75a71957-ec19-5c32-86dc-6b1715adbcf9 |  | note | Acceptance Criteria - Lowest conduit 100mm from the pit chamber floor.
label | f4f05fb6-29b3-5e3d-b7c3-42e4a26eb8e1 |  | note | Method - Visual, Measure
label | 2c1ab7d3-10b2-5373-b4b2-cc9f308ba35e |  | note | Frequency - Each Pit
label | e9039d61-8f84-5fb3-b948-5c6194ea4d63 |  | note | Category - IP
label | c55852c7-d1f6-5156-af38-34425ce3e753 |  | note | Responsibility - SE/Site Supervisor
label | e9e5cbe1-12f3-5a39-9176-8eb00ccca1df |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.17 - Tracer Wire
label | b6d86eda-a4aa-5ff2-80a3-c9911c34d790 |  | note | Reference - L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings
label | 148a025a-d9c4-51c1-a8c7-e4eb959ed6a9 |  | note | Acceptance Criteria - Warrning tracer wire for Vic Track routes to be drilled into pits and crimped off. If tracer wire broken needs to Crimped
label | d9c50d8a-4e2e-50fd-b41d-8102437f9dcf |  | note | Method - Visual
label | 0bb1ed8d-8bf8-5c0b-a8d5-cf8c76951063 |  | note | Frequency - Each VicTrack Pit
label | a2f69fb4-9fb3-5a72-820e-1e3bc3219a2c |  | note | Category - HP*
label | 8bed12df-4265-5e8c-958f-47230c7d80d8 |  | note | Responsibility - SE/PE, MTM / Vic Track Rep
label | 2d564c82-26ea-591b-93ce-a5a56d34cbc6 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.18 - Spigots and Bell Mouths
label | 3a5ed17b-1292-5ac2-8c83-1874ac823b70 |  | note | Reference - L1-CHE-SPE-070_9.3.4
label | 67b40699-8e04-5c49-af5c-b199ecd02ee4 |  | note | Acceptance Criteria - All conduit ends in pits are to be correctly fitted with spigots to ensure that there are no sharp edges on the conduit; they are to be mounted flush with the pit wall and not touching any other spigots. HV Conduit entering the pit shall extend a minimum of 150mm beyond the edge of the excavation and be fitted with Bell Mouths.
label | 5075ed70-a410-58a4-bd81-dd465bc9ed00 |  | note | Method - Visual, Measure
label | f95af92d-d40a-5e40-9ac9-f4e8e6093ffb |  | note | Frequency - Each Pit
label | cf326f79-269a-57ea-af0d-ffcf1b042d13 |  | note | Category - IP
label | 019d64f4-e77f-5b39-a911-33f5d28a6330 |  | note | Responsibility - SE/Site Supervisor
label | 7a71d65f-2062-5643-ac67-256b9393309b |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.19 - Draw Ropes
label | 4fddd25a-2e50-5faa-8dac-60f5122ab73f |  | note | Reference - VRIOGS 012.2.1
label | ae2a31d0-adb9-5f0f-b602-bd1484ba3aef |  | note | Acceptance Criteria - The draw wire shall be continuous for the complete length of the conduit run. The draw wire shall have a minimum of 2 metres of slack within every pit.
label | f0295b7f-2df6-5b71-b42e-a608abd1f9c5 |  | note | Method - Visual
label | bb04d2e8-e4f3-50f1-89a5-e65002b50f04 |  | note | Frequency - Each Pit
label | b6ddd768-834b-55d9-92af-1c61bff578fd |  | note | Category - IP
label | fbeb27cc-01b2-58a7-97ed-2e158416fb60 |  | note | Responsibility - SE/Site Supervisor
label | 385a5488-fb42-52ac-9085-d01bcd3ee125 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.2 - Backfill and Compaction Testing (if applicable) arouns Pits
label | f34712a4-4629-51ca-951a-4ef63e31ab8d |  | note | Reference - L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings
label | b43e99b3-7e22-5bec-9f96-045452c9fe68 |  | note | Acceptance Criteria - Backfill used around pit & pit lid to achieve 95% standard compaction in layers no more than 150mm layers
label | 86d7362b-9e72-5c52-8af6-60da91022eb0 |  | note | Sand within sand pits to be compacted in layers no more than 250mm layers
label | 25af188a-d434-5389-a3cf-8b1598a754af |  | note | Backfill shall be compacted and level with the collar and surrounds for Trafficable Pits.
label | 4dd85bb9-4962-5a69-b7e0-5e19baedd459 |  | note | Attach Test Report
label | 84aadcfa-8cab-5d77-ab61-9ff66d6cd181 |  | note | Method - Document Review, Visual
label | c17f066a-ccce-592b-8623-bee914e7a491 |  | note | Frequency - Each Pit
label | 157733a2-96ba-5c65-835d-a04bd0d385fd |  | note | Category - IP
label | c689da68-6299-5651-a09e-df7799513497 |  | note | Responsibility - SE/Site Supervisor
label | adfc0dee-98df-51e0-ae47-9033a21f1a3c |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.21 - Spare Conduits
label | 6aa8e623-4824-5e92-b800-03b855ff89db |  | note | Reference - L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings
label | d1b025a1-af11-529b-aac2-f516bab063ab |  | note | Acceptance Criteria - Spare conduits to be sealed and to be included on survey report.
label | f760e199-67d3-509c-bff5-2dc9c4feab0d |  | note | Method - Visual
label | 8e47d88a-0574-5c79-a413-4ebd4fed19da |  | note | Frequency - Each Pit
label | 572a128a-e120-52e5-aba6-88b37b930a43 |  | note | Category - IP
label | e9aad2e9-9405-5ba8-8e26-5704716c8a71 |  | note | Responsibility - SE/Site Supervisor
label | 3332dde4-4bb0-58df-a2be-a883cc5ca7cb |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.22 - Pit Lables
label | fcaeb923-984d-59cc-a6f5-2bf1352b80de |  | note | Reference - L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings
label | 1886d953-0a8c-573b-ad19-bdff48bad2f1 |  | note | Acceptance Criteria - Pit labels Brass Label (30mm x 150mm) - HV: DANGER - Railway High Voltage - VicTrack: Victrack Comms - Signalling: Rail Sign Comms - LV Pits: Electrical - Electrolysis: Electrolysis - SCADA: Rail Sign Comms - MTM Comms: Rail Sign Comms
label | be068c4a-fdbc-5cb7-b4b5-83353c698c47 |  | note | Method - Visual
label | c6b04755-352c-5fd0-8725-f6ac82c7dad4 |  | note | Frequency - Each Pit Lid
label | cb3e1c0d-4ea6-5bf5-bdbe-beb4d532712f |  | note | Category - IP
label | 62faa399-ecc6-5637-80af-9a98d828830c |  | note | Responsibility - SE/Site Supervisor
label | 78a35a19-dfe2-5eb3-b383-49434e56f93e |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.23 - Pit Numbers
label | 00f40897-f49f-506b-ac7c-dceaf55700e1 |  | note | Reference - L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings
label | 1850fa58-26b6-5e26-931f-b212a4505035 |  | note | Acceptance Criteria - Pit Number Brass Label (30mm x 150mm) - HV (22kVV Feeders): ###HV - DC (HV Feeders for OHLE): ###DC - VicTrack: ###C - Signalling LV: ###SL - Signalling HV (2.2 or 3.3kv): ###SH - LV Pits: ###L - Electrolysis: ###E - SCADA: ###MS - MTM Comms: ###M
label | 4136458b-7750-5dda-859e-4a4feafd0a35 |  | note | Method - Visual
label | f5e0ea52-3a68-5ff6-86f6-bff2fa17e015 |  | note | Frequency - Each Pit Lid
label | 3c18a722-73be-53f3-baff-d282f401efad |  | note | Category - IP
label | 2e4d0544-f8ae-5adc-a066-ce6e313da7fe |  | note | Responsibility - SE/Site Supervisor
label | 922a44a0-bac8-5c84-9bd9-befc1fc18d32 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.24 - Cable Route Markers
label | 76144e2c-9d32-56bb-b798-72a0c14e63e9 |  | note | Reference - L1-CHE-SPE-070_13.2 STD_E0169 and STD_E0170 AS 4799 STD G0003 and STD G0004
label | 851593a3-d4bf-529e-9865-4432b44abf58 |  | note | Acceptance Criteria - Cable Route Markers - points entering & leaving the rail corridor - no greater than 100m spacing - Change of direction (more than 5 degrees) - White posts with marker plates for conduit runs
label | a2c4cced-3ec8-5cdb-a5df-2593006d3056 |  | note | Method - Visual
label | dde5e227-af25-5233-8a21-81ea915d0507 |  | note | Frequency - Per Cable Route
label | 77140785-815c-5d0a-a7c5-1abfc2b839ae |  | note | Category - IP
label | 2ec1825a-3131-5a94-92a6-13b1318521ea |  | note | Responsibility - SE/Site Supervisor
label | 92464743-752e-5dd0-9a9f-2083d2d62077 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.25 - Cable Pulling
label | 1494b263-e790-5ad5-a651-456fc0af211e |  | note | Reference - L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings
label | c9535c07-e04b-581e-8634-9d1d88708e1c |  | note | Acceptance Criteria - Cable pulling to be witnessed by MTM/Vic Track and to be signed off.
label | bbdeacc4-7dd7-56e5-9eb7-000f6bd60a5b |  | note | Method - Visual
label | ce0a57de-9675-5e21-9b32-15812b6505eb |  | note | Frequency - Per Cable
label | dba4d3f2-a7ce-5cd6-9626-8be6b9aa0999 |  | note | Category - HP*
label | 474ee7e6-7362-5d2c-b506-07fe3c4b24c1 |  | note | Responsibility - PE, MTM/VicTrack Rep
label | bd760feb-58ca-5224-99e0-eb3055eeca9f |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.26 - Cable Labels
label | 9ef4c9a8-fa9f-5704-9850-6bf884198749 |  | note | Reference - L1-CHE-SPE-070 Section 13.3
label | efad579a-3661-5e1f-b9d1-144f6e4286bb |  | note | Acceptance Criteria - All installed High Voltage Cables shall be legibly and indelibly marked with an appropriate identifying label at each end of the cable, and at any cable joints. The label shall state the destination points of the cable and the name of the cable relevant to appropriate drawings
label | db7184c0-91c8-523c-8a5e-1b918cde877d |  | note | Method - Visual
label | bf02e5a2-0b10-58bf-9b89-39a34dcdfc08 |  | note | Frequency - Per Cable
label | accb6718-bf60-554a-be21-ca1362f3fe60 |  | note | Category - HP*
label | 74044936-4613-5e6d-902a-ac8db4105c17 |  | note | Responsibility - PE, MTM/VicTrack Rep
label | 9b40c73c-5ec2-5c4c-a5c6-86fe8b7bf6a4 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.27 - Cable Joints
label | 47dcd337-e290-5aba-a232-d5866aaa4a1b |  | note | Reference - L1-CHE-SPE-070 L1-CHE-STD-043 L1-CHE-STD-070 IFC Drawings
label | f4979caf-7a3d-578f-9e9b-c4f8f47ec52a |  | note | Acceptance Criteria - Cable joints are installed correctly, with sufficient fault loops lengths & supported correctly in pits.
label | 28ce7dd7-acdc-5a80-bebb-da227bb23e0a |  | note | Method - Visual
label | 6b0e7a25-6a73-5a31-8e4c-b58b98dc4f48 |  | note | Frequency - Per Joint / Termination
label | fdc4d8a5-c058-5414-bb21-5d1981be273c |  | note | Category - HP*
label | 82a72261-7740-52f9-91fc-33b9d728b414 |  | note | Responsibility - PE, MTM/VicTrack Rep
label | d8d9b669-8174-5dc3-9e64-fcfd35b05734 |  | note | Verifying Documents - This ITP
checkpoint-group |  |  | section | 6. Post-construction / Post-installation Activities
checkpoint-status |  |  | checkpoint | 6.1 - As-built Survey
label | 02106fe5-d566-5b85-98cd-a1dcc18d12dc |  | note | Reference - IFC Drwings L1-CHE-SPE-070 Section 13.1
label | d7ae121c-bd83-5853-a896-8374bb78c956 |  | note | Acceptance Criteria - Survey report to include but not limited to: - Cable joint locations. - Cable pit locations (Corners) - Pit dimensions & pit lid type - Under line crossings - Under road crossings - Changes of direction - Spare Conduits - Conduits labelled as per trench profile - every 10m - Other significant points of the cable route Attached Survey Report
label | 94afee7e-64b6-5e7a-ba07-69b0937eda7f |  | note | Method - Document Review
label | b59d4a09-0d06-5844-9d5f-19485cfeb6e3 |  | note | Frequency - Each Lot
label | 9dd4d079-ae23-5898-9c6e-353133039da1 |  | note | Category - IP
label | f80025b6-b905-5028-8249-9419356af0af |  | note | Responsibility - SE/PE
label | 4a7d1749-f277-5aee-9c95-df47d4bf8421 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 6.2 - Handover Check
label | 36959fc4-1351-5557-b4ac-8b7bd36e550b |  | note | Reference - IFC Drawings
label | a256166c-16b0-57a8-9d36-2959eeeb1411 |  | note | Acceptance Criteria - Handover check completed for Testing and Commisioning. Attach MTM/Vic Track Check Sheet (Signed-off)
label | 4ea092cb-cee5-5635-b6f3-8a4413911cf4 |  | note | Method - Document Review
label | 91226f36-24e5-5000-bddc-573f2454c21c |  | note | Frequency - Each Lot
label | 9f42d629-13b9-58ae-a16f-cc418daa4139 |  | note | Category - HP*
label | 243e7650-8bb6-54a2-b774-b0d45203c161 |  | note | Responsibility - PE, MTM/VicTrack Rep
label | 341268b9-7221-56d7-afdb-66a4f3420b38 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 6.3 - Testing and Commissioning
label | 4761b513-130e-54c7-be0c-2eac06929c23 |  | note | Reference - IFC Drawings
label | 2bc7534d-a4bd-50e4-8d0e-e0e47e35e524 |  | note | Acceptance Criteria - Testing and Comminsiong to be completed Attach Testing and Comminsiong Report
label | 9e155767-af8b-5295-b8d7-eceb90ee37af |  | note | Method - Document Review
label | b0867c87-652a-5a61-80c5-246fd20e093d |  | note | Frequency - Each Lot
label | 8c71499c-15cb-59a8-9382-08808b0e21a1 |  | note | Category - HP*
label | bde653dd-1100-54ed-a88d-9175c9f8c3e9 |  | note | Responsibility - PE, MTM/VicTrack Rep
label | 05f4da77-ea4c-5ef3-9f5d-635e089da9c7 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 6.4 - Non-conformance Report (NCR) Closure
label | 1eb887ad-d2c9-5b90-8429-d24b8886d8e2 |  | note | Reference - MRPA Quality Management Plan
label | a0d218be-7278-5693-ae27-4f9a72d8e886 |  | note | Acceptance Criteria - Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed.
label | 5f2b5974-f034-5c87-a837-8b055c750b1e |  | note | Method - Document Review
label | 43d06d31-b21e-5d03-bf0b-3e9f529fc409 |  | note | Frequency - Once, prior to closure of this lot / element / Work area
label | 02360c91-5c9a-518f-8db9-1f6e878a5bf0 |  | note | Category - HP*
label | 79a480a4-be4e-5faa-bee5-924856dbef33 |  | note | Responsibility - SE/PE/SPE
label | 3e71145f-3e36-5b89-aa40-a0a52e143f42 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | Final Inspection
label | 3d519fc7-4d88-525b-b612-f6f6a689afdd |  | note | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed above have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
text | f7ac4b8f-c17d-5d54-90cb-f484b7552b0f |  | textbox | Name:
text | 39d9ba1c-8668-5096-b3be-284178b5df4e |  | textbox | Position:
text | e1aaeb98-a9ec-5db1-a282-6eec7ced6bbd |  | textbox | Date Completed:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | ITP-016-STR - OHW Structures Pilling |  |  |  |  | Yes | SYS - ITP-016-STR - OHW Structures Piling (old version) | 80cda403-11d9-4211-bbe3-2451232b8661
checkpoint-group |  |  | section | 1. Referenced Documentation
checkpoint-no-status |  |  | checkpoint | 1. Referenced Documentation
label | 8ca25506-74de-5d0f-a988-c5b7d7515c2f |  | note | Document Title: ITP-016-STR-Brunt - Overhead Wiring Structures Piles
label | d1caa2c2-700b-5922-85bf-5370da208c90 |  | note | ITP Description: OHW Structures Piling
label | 55c1cd08-80b6-5e49-a8d9-2bc48cfcb093 |  | note | Document Number (in Teambinder): MRP-0000-MRPA-ALT-ITP-00XX
label | 890c5eed-5958-5977-a1d2-3c6718db3c70 |  | note | Discipline (e.g. CIV/STR/RAIL): STR
label | 85f0eed3-a2e1-5e1d-abab-53bf24c4faa9 |  | note | Revision Number: 0
label | 56e5cddd-a53f-51cc-9eb4-5e3bef8e123e |  | note | Revision Date: 21/12/2022
label | 09cbd6d8-4404-53a2-820c-1f0391985bef |  | note | ITP created by: Casey Knowles
label | 7337facf-a0bf-559f-a346-4827ad6b581f |  | note | ITP approved for use by: Jon De Castro
checkpoint-status |  |  | checkpoint | 1.1 - Non Dependent
label | 243e6801-fe6a-5e0e-a418-ea075b743d35 |  | note | Reference - VicRoads Section 606 July 2017
checkpoint-status |  |  | checkpoint | 1.2 - Non Dependent
label | 3a58ce18-cd0f-5d30-be34-519880a78dbe |  | note | Reference - VicRoads Section 610 Feb 2020
checkpoint-status |  |  | checkpoint | 1.3 - Non Dependent
label | 1d4aa949-d0b4-5562-aaa2-c5b22f59f707 |  | note | Reference - VicRoads Section 611 November 2018
checkpoint-status |  |  | checkpoint | 1.4 - Non Dependent
label | f8e528a6-1831-5ed1-b146-e22a75c56492 |  | note | Reference - AS2159-2009
checkpoint-status |  |  | checkpoint | 1.5 - Non Dependent
label | f1a771ce-8845-5a19-a245-1645d6bfaaee |  | note | Reference - AS3810.1 2018
checkpoint-status |  |  | checkpoint | 1.6 - Non Dependent
label | 5abb89d1-d067-5b4a-a673-be7763bf546d |  | note | Reference - AS5100.3-2017
checkpoint-group |  |  | section | 2. Preliminaries - Materials
checkpoint-status |  |  | checkpoint | 2.1 - Concrete Mix
label | cd34f5c2-4ef4-5b9b-b19e-d1f751e47caa |  | note | Reference - 610.07 Table 610.071
label | ea74c36a-b09d-50de-96f6-ce90d3dd89b2 |  | note | Acceptance Criteria - Concrete Mix is Registered with VicRoads. Concrete mix meets strength, grade, and maximum aggregate size as detailed on drawings.
text | 25522720-2c0c-536b-b0c6-1b9e1455e7d9 |  | textbox | Enter: Teambinder Material Approval number
label | a97b532c-7108-545c-a44b-28dcbcfb41d3 |  | note | Method - Document Review
label | a56d5ecf-ca6f-571a-8f03-248c9331cfc2 |  | note | Frequency - Once, for each mix design, 4 weeks prior to placement of concrete
label | a4a4907b-6e00-50d8-86f9-b3718bb42051 |  | note | Category - HP
label | d19868d4-b0e4-5022-b782-a1fe51603a1a |  | note | Responsibility - Nominated Authority
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.2 - ACRS Certification (for Reinforcement)
label | c0f80059-8d59-59ea-9780-43be4e7406f4 |  | note | Reference - 611.05 (a)
label | 0aacb09a-a55c-59a8-bd6e-3806c18b4ecb |  | note | Acceptance Criteria - Current ACRS certification for materials and for bar processing. Note: ACRS certificate may cover both aspects or be for each separate portion (e.g 1 for the material supplier and another for the bar processor (bending, cropping and delivery)
text | 2a08095f-7679-5c2b-83f1-4818f4581d43 |  | textbox | Enter: Teambinder Material Approval number
label | 08cf1bbc-c7a5-5b9d-9716-b8167e4e3f70 |  | note | Method - Document Review
label | faf921cd-bc88-5ee5-8250-fa00708b15cb |  | note | Frequency - Once for each supplier, 14 days of award of contract
label | aa4d6dff-f4b1-53a1-bbe1-d1e1a34c1fff |  | note | Category - HP
label | 7165466d-16fe-569f-ba78-099f77623db1 |  | note | Responsibility - Nominated Authority
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Bar Chairs/Aspros/wheels Certification
label | b1ad85db-330d-57c7-a6ac-c14df8442fd4 |  | note | Reference - 610.26 (a)
label | c238e445-935b-5440-a87b-b67fe0ccf839 |  | note | Acceptance Criteria - Plastic bar chairs, wheels, and spacers require bi-annual testing to demostrate suitablity to prevent excessive deformation under loads.
label | 64120bcf-91a0-5972-b0fb-3a6600ca5e4d |  | note | • Concrete aspros require annual compressive strength and soluble salt testing is required.
label | 0f555f48-420e-5c36-a506-912bf06dfc86 |  | note | • Relevant test reports demonstrating compliance to this clause shall be submitted for review to the Nominated Authority
text | 2a345242-830e-5d7b-b9e0-838a251ba5e7 |  | textbox | Enter: Teambinder Material Approval number
label | e0a71301-bedb-562a-86fd-ee6881dc3318 |  | note | Method - Document Review
label | a1ab10a4-6051-5ded-9b20-0e00a548c0ac |  | note | Frequency - Once for each supplier, 14 days prior to placement of reinforcement
label | a1f26c00-7876-51bb-861c-149de5d78260 |  | note | Category - HP
label | 56435f39-07aa-567f-b640-54c5609faccd |  | note | Responsibility - Nominated Authority
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.4 - Cast-in Bolts, nuts washers
label | b42a2bda-6efa-5d75-b316-d3bd953f2a0e |  | note | Reference - IFC Drawings
label | 52c54432-3953-57bd-941b-a6b37d320f67 |  | note | Acceptance Criteria - Unless the drawings note otherwise all bolts, nuts and washers shall be 8.8/TB galvanised components to AS 4291.1 & AS/NZS 4291.2
label | 8b765e68-13cc-5626-a535-02ce76d4dc0b |  | note | • Washers installed under bolt head and nut. Tapered washers used as required.
label | 34293535-454a-5e1b-b0c9-d581ba09ddd6 |  | note | • Slotted holes and required hardened or plate washers in accordance with AS4100 and AS 5100.6
label | 36b450ae-5ad0-5fef-a1c7-38a56d02e644 |  | note | • If HDG, a certificate is required. HDG thickness should be as per designs.
text | 012fcbe3-c743-5a2f-9bac-e25b968e1e5f |  | textbox | Enter: Teambinder Material Approval number
label | 00270862-b666-50f2-ac68-b9f587b9add2 |  | note | Method - Document Review
label | 7e7f9ec7-d081-5f0f-a285-47b969e6651e |  | note | Frequency - Once for each supplier, 14 days prior to placement of hold-down bolts
label | eee80aa4-6092-5e78-a797-722b707056cd |  | note | Category - HP
label | 0b1dde68-9189-5e65-b13b-d771b9abe077 |  | note | Responsibility - Nominated Authority
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 3. Preliminaries - Procedures & Documentation
checkpoint-status |  |  | checkpoint | 3.1 - Working Platform Certification
label | 9f29000e-66de-57b3-8d96-564c6123e030 |  | note | Reference - Temp Works Design
label | 579a07d4-d155-5402-be7d-53173a774fc8 |  | note | Acceptance Criteria - Satisfies minimum plant bearing pressures requirement
label | 851069cd-ef76-5285-be79-ddf72a75bbba |  | note | Method - Document Review
label | 148cd2a3-9d79-5461-a064-edb4a9856a0a |  | note | Frequency - 14 days Prior to works commencing & after rain event which there is >10mm in a 24hr period.
label | b55c6211-a2aa-5ef7-9cb1-cd9d55cea871 |  | note | Category - HP
label | 9312ae79-0725-5904-8511-2ca4722f6c88 |  | note | Responsibility - Piling Contractor/Geotechnical Engineer/Fulton Hogan Engineer
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - Piling Operations Work Procedure
label | 7f26b1d7-19fc-5834-a97e-8f9ff4967c05 |  | note | Reference - 606.03 (a)
label | b00da05a-45a4-55bc-85de-84b11ce54a5c |  | note | Acceptance Criteria - Piling operations work procedure to be submitted for review to the Nominated Authority.
text | c748efd9-c972-5b29-b80d-e12dadf52864 |  | textbox | Enter: Teambinder Approval number
label | 46f386b0-13e7-513c-9cc1-83683493b6c1 |  | note | Method - Document Review
label | 49ebd2c2-30ba-51d6-80e7-40a0c5e5c9d6 |  | note | Frequency - Once, 4 weeks prior to the commencement of piling
label | ef026562-a544-54d9-8602-fb57014e5521 |  | note | Category - HP
label | 1e4c80cb-cdf3-5e48-86aa-1bc1a8b49d6b |  | note | Responsibility - Nominated Authority
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3 - Temporary Steel Casings
label | 279e82cb-a863-50b3-a1be-501700614838 |  | note | Reference - 606.03 (b)
label | c6d80272-137c-56bd-8418-8168ad377b82 |  | note | Acceptance Criteria - Temporary steel casings shall be free from holes and distortion with a smooth internal surface without any projections.
label | 5c241de0-6a3b-5b16-aca7-3c53ff9376b0 |  | note | • Any splices in the casings shall be able to withstand any stresses induced during installation & removal.
label | 5cc6c354-b7c8-5ddd-b8a4-15ba32b585b5 |  | note | • The casing shall be proof engineered by a proof engineer who is pre-qualified with VicRoads.
text | f9268d82-62cc-5ded-8c51-90c277c8dcf2 |  | textbox | Enter: Teambinder Approval number
label | 9ee4b909-662e-5bf8-8b09-72e4097799c0 |  | note | Method - Document Review
label | a84db535-dd2c-5e53-9344-8b12e2e71f84 |  | note | Frequency - Where applicable, once, 14 days prior to use
label | a5223172-69dc-5aa4-92dd-95406c2f13de |  | note | Category - HP
label | cf98ab81-0fb0-5add-afaa-7cb28034550f |  | note | Responsibility - Nominated Authority
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.4 - Casting Under Water Procedure
label | 8576d00a-2250-5967-8177-fa0cfd35f07c |  | note | Reference - 606.06 (a)
label | 28c2397b-70a3-508a-bc99-2b1132e9e4fe |  | note | Acceptance Criteria - Casting under water procedure and methodology for removing mud, loose rock and other debris to be submitted for review to the Nominated Authority.
text | 43e64cca-a8af-52ba-863b-e81bb8a990d3 |  | textbox | Enter: Teambinder Approval number
label | 25cae0c6-f288-5648-b92b-153cf0781bc5 |  | note | Note: Piling Operations Work Procedure may cover this requirement - if so, use the same Teambinder Approval Number if this is the case.
label | 5442cbc6-c4c7-5f0a-b996-4d0e2731aaea |  | note | Method - Document Review
label | d0deb637-f1a3-593c-a43f-cecb2210b8b6 |  | note | Frequency - Once, 4 weeks prior to the commencement of piling
label | fb0006ff-5181-5c08-9f9c-9caff20795bd |  | note | Category - HP
label | 44312458-299a-5f0b-9c3d-1dfdf2eeeeec |  | note | Responsibility - Nominated Authority
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.5 - Pre-qualified Pile Testing Consultant
label | 14a5b90c-9b89-56f9-a5dd-49cdcc468b31 |  | note | Reference - 606.07
label | f886d670-5e7b-5afd-becf-198422dee91c |  | note | Acceptance Criteria - All testing shall be undertaken by a Vicroads pre-qualified consultant who is independent of the piling contractor. Details of the consultant to be submitted for review to the Nominated Authority.
text | 18b9ccb0-e98d-5370-ab85-b088b3d16818 |  | textbox | Enter: Teambinder Approval number
label | 77070c68-9167-53d7-b5da-03c5ce54a713 |  | note | Method - Document Review
label | 6bca871b-80a2-567f-abc7-7dca90e06889 |  | note | Frequency - Once, 14 days prior to testing
label | 343c6159-256c-50bd-ac83-52782c055f95 |  | note | Category - HP
label | f871650b-f63c-5d1a-98b8-34b63fde7bec |  | note | Responsibility - Nominated Authority
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.6 - Reinforcement Welding Specifications & Qualifications
label | 87cb4b4f-60cb-56aa-b36e-105dd2c35df0 |  | note | Reference - 611.13 (a) AS/NZS1554.3, Clauses 3.3.2 & 3.3.3 611.14 (b)
label | fe56e34d-813a-5a60-998a-488b4b5ec64e |  | note | Acceptance Criteria - Welding of splices in steel reinforcement, including to other steelwork and to continuity bar reinforcement, shall not commence until the welding specification & qualifications (including macro inspection) have been approved by Nominated Authority.
text | f34e8bd7-e34b-5871-a25b-31d0e8ecbcec |  | textbox | Enter: Teambinder Approval number
label | 67ed8a06-2208-5d51-8886-f1d3bd2e4860 |  | note | Method - Document Review
label | 0bf420ba-ea2f-5b00-9e3a-f609e8866785 |  | note | Frequency - Where applicable, once, 14 days prior to welding
label | 32e17da6-d017-56d6-a2f9-748dcdc417ed |  | note | Category - HP
label | b6419123-b8b2-526a-a0c3-7b5278e69b0f |  | note | Responsibility - Nominated Authority
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 4. Pre-construction Activities
checkpoint-status |  |  | checkpoint | 4.1 - IFC Drawings
label | c73052b3-effa-5096-9889-7cacde06dfa2 |  | note | Reference - MRPA Quality Management Plan
label | 1e96ea50-d805-5457-aa60-cdcee0fdc795 |  | note | Acceptance Criteria - Check the revision of the IFC drawings are current as per the drawing register (on Teambinder)
label | 1f9e4cb0-dd2a-5c11-a73b-14bb97e442f8 |  | note | Method - Document Review
label | 81d1f330-b74a-59f1-884e-0230115fbfdb |  | note | Frequency - Prior to starting Works and at regular intervals
label | d622a0d5-165e-5961-8e5b-f27d99a5e548 |  | note | Category - HP*
label | b4e3cd1d-46c1-5e3b-8625-977149694d8f |  | note | Responsibility - All
checkpoint-status |  |  | checkpoint | 4.2 - Survey Set-out
label | 964f790d-0571-5c5f-9940-42d7be632a61 |  | note | Reference - IFC Drawings 606.08 (a - c)
label | 5e8bd243-0831-5936-8c4c-24d34da9f7cc |  | note | Acceptance Criteria - Survey activities undertaken to ensure and validate that all Works meet location requirements of ±75mm.
label | b08859dd-9028-5a7c-9e76-c8fd828df4bb |  | note | Attach: Lot Map, Marked drawing to indicate the location of piles in the Lot
label | 873efcf3-4224-5c15-bc42-60027776ece8 |  | note | Method - Measure, Visual
label | f5e0dd88-8ce8-5393-8133-08594d2d70e5 |  | note | Frequency - Each pile
label | 2325812c-625f-5d5c-846c-410021242c57 |  | note | Category - IP
label | a4e6b916-4fde-5002-92d2-d88ac968dff0 |  | note | Responsibility - Surveyor, SE
checkpoint-status |  |  | checkpoint | 4.3 - Protection of Adjacent Piles
label | 26f5bd55-c2fd-55e0-b774-2724ee122471 |  | note | Reference - 606.04
label | 79345820-1d07-5c5d-8752-8e7764cdb249 |  | note | Acceptance Criteria - Pile construction shall not:
label | 55d2dc7f-5914-5598-ab7e-7403faa7d730 |  | note | i. result in damage to adjacent newly cast piles due to ground vibration.
label | ee04f269-716b-5583-84fe-767bda0ab719 |  | note | ii. commence within 2.5m clear distace from newly cast piles if that pile concrete strength <15MPa
label | 4f78969f-6593-586d-ac50-52c215aebd53 |  | note | iii. involve driving or create significant vibration within 9m until that pile strength ≥15MPa and set for a minimum of 24 hours
label | 569b7f2b-1901-5a15-a240-fcdf66d3965b |  | note | Method - Measure, Visual
label | 0aa62124-995a-525f-97b3-932981574d8f |  | note | Frequency - Each pile
label | 037bd411-07a8-56a6-b016-55815259aaf3 |  | note | Category - HP*
label | 2ed1948c-f27c-5a9d-81a8-f918b31aded2 |  | note | Responsibility - SPE/PE
checkpoint-group |  |  | section | 5. Construction Activities
checkpoint-status |  |  | checkpoint | 5.1 - Boring Operations
label | cd2d3f8d-e1e0-5981-afb1-fc9de6555ead |  | note | Reference - IFC Drawings 606.03 (a)
label | f81a7c13-d588-51f2-96a2-42a572b55b3b |  | note | Acceptance Criteria - Boring performed to the required diameter and depths shown on the IFC Drawings under the instruction of an experienced geotechnical engineer.
label | 305bb588-45a5-5146-8d0b-ba3c5dccd740 |  | note | Where piles are founded on rock, they shall extend a minimum of 2 x pile diameter into the rock shown on the IFC Drawings.
label | f09ec2bd-8fab-52db-b4f7-805ea868d383 |  | note | • Excavation clean and de-watered (where applicable) for inspection.
label | fb7a2608-503f-51ce-9ea3-27c7d5e0525f |  | note | • Excavation made safe by appropriate means and to be protected from site run-off and loose materials falling in
label | 5bf7bb81-d599-5990-a739-7551cda3ce50 |  | note | • Excavated material to be disposed of as appropriate to maintain a clean site.
label | e14df4a5-24f4-55e7-b38d-71b14abad0ca |  | note | Method - Measure, Visual
label | fc3959ad-13cd-5f41-9b63-7078844c36cd |  | note | Frequency - Each pile
label | 8072a5c3-643d-5563-b0cd-f05b3acfa2d2 |  | note | Category - IP
label | 9159d803-a5d2-5893-8e72-75e1728c13e1 |  | note | Responsibility - Surveyor, SE/PE/SPE
checkpoint-status |  |  | checkpoint | 5.2 - Formwork Extension
label | c4335301-7d6a-539d-a18a-694cc67f73d0 |  | note | Reference - IFC Drawings
label | fe7a4089-17d2-5ce5-8880-cb932d43116d |  | note | Acceptance Criteria - Where applicable, formwork shall be used to ensure the top of the pile is at the required RL.
label | 7822377d-e072-52c3-87d1-ba68d4a828fb |  | note | Method - Measure, Visual
label | b5731e02-4390-52ff-b2b7-437fa5e75b10 |  | note | Frequency - Where applicable, each pile
label | 05371a94-8af5-5bbf-8348-bf44128bdefc |  | note | Category - IP
label | e5286642-e1e2-5925-ba0a-3dc54e5bf1a6 |  | note | Responsibility - Surveyor, SE/PE/SPE
checkpoint-status |  |  | checkpoint | 5.3 - Inspection of Pile Excavation
label | fdcf1290-15ed-5129-8f7f-ab3947ab60c1 |  | note | Reference - 606.05
label | b99a24b2-1e55-5e03-b845-19320b30b46e |  | note | Acceptance Criteria - Pile walls and base to be inspected by the geotechnical engineer to confirm that the geotechnical strength of the materials in the pile wall base have satisfied the design assumptions.
label | 6762ad50-35a0-5a1b-946d-79a0a9d17f58 |  | note | Attach: Geotechnical Field Sheet or Report
label | f309504e-9538-5900-b4cb-dbd1b1d29a46 |  | note | Method - Measure, Visual
label | 147a7617-e838-5286-9ba4-3c2b71468755 |  | note | Frequency - Each pile
label | c58f1d53-4ce0-5451-96e7-5ebab150a890 |  | note | Category - HP
label | 9332fae0-5f79-587e-a083-4c3bf532d209 |  | note | Responsibility - Geotechnical Engineer
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 5.4 - Reinforcement - Placement
label | 3ddbc32d-79f9-58b1-8fcb-cab38725149f |  | note | Reference - IFC Drawings
label | 22f0a37a-0759-5d97-b938-e14d00bdedd4 |  | note | • 611.06
label | 8821d8ac-5b47-50a2-8467-b75e4c60f106 |  | note | • 611.09
label | a28ef638-9618-5646-b957-ffe3e5cf327c |  | note | • 611.10
label | c1fa1dca-2451-544c-b6e4-d1732118c4fe |  | note | • 611.11
label | 7087fe2c-1c3a-51c9-a571-1a9d5e3035d5 |  | note | • 611.12
label | 2400728a-06aa-5f3a-844c-1832c0ae2c8d |  | note | • 606.06 (a)
label | df48c7e4-df2c-5719-8388-62071a4e51f1 |  | note | Acceptance Criteria - The correct reinforcement grade, quantity, size, orientation, location and spacing as shown on the structural drawings.
label | a2b6f7b2-27c1-51af-81ee-8655cf03a137 |  | note | • Projecting reinforcement is the correct length and location.
label | 8307663d-0fb8-5a30-82b9-40d7116e7765 |  | note | • Splice lengths achieve the minimum length and are in contact for this length.
label | 15a41a7a-c723-5411-9a86-b474484a0af0 |  | note | • The reinforcement surface condition is free from dirt, debris and damage.
label | 6960de71-7ba1-5ec3-b354-d9d6fed69791 |  | note | • The resulting cage securely held with sufficient ties to limit displacement or deformation during the concrete pour.
label | be10078d-16b2-54d7-8ec2-dbe2c1b3f400 |  | note | • Bar chairs or wheels used at no greater than 2m centres so that the minimum cover as shown on the structural drawings all around and has been achieved (including tie wire locations).
label | 6f9afb94-00c8-55c3-8293-2d5d4f602008 |  | note | Method - Measure, Visual
label | 46359370-45d2-590d-91be-b4491706de9e |  | note | Frequency - Each pile
label | 45662c3a-6516-5ea9-a9ee-1a4d865c7e5c |  | note | Category - IP
label | c4971259-2404-5551-bb43-689ec1a07f23 |  | note | Responsibility - Foreman, SE/PE/SPE
checkpoint-status |  |  | checkpoint | 5.5 - Reinforcement - Electrical Continuity and HD Bolts - Electrical Continuity
label | 23ee3623-34ef-52b7-8dbd-c9a771d30276 |  | note | Reference - IFC Drawings 610.29 (d) 610.43
label | eeb49aa2-770f-5f64-868d-c7e000266ee3 |  | note | Acceptance Criteria - Pile reinforcement cage to be made electrically continuous by:
label | 42960a89-e349-5db7-b217-f0d6378cf348 |  | note | i. tack welding 4 no. min. longitudinal bars to all intersections of the helix at 2.0m centres max. (at every intersection is preferable.
label | 646fad0e-d432-52f9-9cd8-600f34cd5467 |  | note | ii. tack welding the selected longitudinal bars at all splices (2 tacks minimum per bar)
label | b8f7edab-e38c-59d7-bc3e-cabf2c07151d |  | note | iii. tack welding or fastening the grounding clamps to the longitudinal reinforcement
label | 48ffab99-7a68-558f-880f-a8701b634a25 |  | note | • Evidence that the resistance across the cage has a maximum value of 0.01Ω / 10,000µΩ is required.
label | e2711c70-f516-5bd3-913e-586baa82bef7 |  | note | • Overhead wiring structures shall be fully earthed, by bonding the hold-down bolts to the pile reinforcement
label | 9a57ec7e-486c-5376-aba9-48f9f7a828f0 |  | note | • A minimum of 2 No. hold down bolts shall be electrically continuous with the pile reinforcement. This is achieved by tack welding 70mm of stranded copper cable between the hold-down bolts and reinforcement
label | 5ff3eb2f-841e-5f26-ae12-3f9d9fcda88d |  | note | • Photograph or attach: Ohmmeter reading across the splice or end to end of the reinforcement cage
label | e05aac24-6128-5668-b6cf-ca784e5f4f4d |  | note | Method - Measure, Visual
label | cae85551-cb14-515f-8f08-3bdda3f0e399 |  | note | Frequency - Where applicable, each pile
label | 1ff87e74-1287-5030-97f4-49babc390d1f |  | note | Category - IP
label | 246c2fcf-070a-576b-9202-5c845638839e |  | note | Responsibility - SE/PE/SPE
checkpoint-status |  |  | checkpoint | 5.6 - Cast-in Items
label | f7c2cb84-6d28-5a3c-beab-3f061921ce49 |  | note | Reference - IFC Drawings
label | 0c51b5f1-1da3-501f-ad0e-02211659fbf1 |  | note | • 610.46 (a), Table 610.462
label | b0b11e8c-4230-5ee3-9e55-05aa7556639a |  | note | • 610.47 (a), Table 610.472
label | 11b86482-6301-57d1-8a1b-eefc9b3357ea |  | note | • AS3810.1 Table 3.3.6.2
label | 1714f3cc-ccbd-5b4b-8b7a-61d0c107bab1 |  | note | Acceptance Criteria - All cast-in items are the correct type, grade, quantity, size, orientation and location as shown on the structural drawings and are securely fastened or restrained to withstand impact and pressure during the concreting operations to prevent dislodgement.
label | cab9f2f9-127e-5de2-b93d-9bde65634498 |  | note | • Any exposed threads, conduits, ducts or voids shall be protected by suitable means to prevent concrete or grout ingress.
label | af570cac-ecb1-5a40-b013-7d7bb051b138 |  | note | • Tack welding of any cast-in items shall be performed by someone pre-qualified to do so.
label | 73ca8b28-ffa3-58cd-ada5-2b9a99423c42 |  | note | • Grout tubes shall be fastened at regular intervals to prevent kinking
label | 4d005527-b2fc-545f-b026-00709e3a0824 |  | note | • Placement tolerances to comply with the IFC drawings, if not specified, use the following:
label | 8faed02e-8fc1-5a95-80f1-b681db5384d2 |  | note | i. Bolts, ferrules, projecting bars & couplers = ±3mm
label | 4c0318df-786e-59f4-904d-7638d5589513 |  | note | ii. Running dimensions of a group of the above = ±6mm
label | 264c1400-d2f9-5ff3-8e2f-c7eb6afac2cf |  | note | iii. Ducts and conduit location = ±12mm
label | 12440b87-01d4-5b4a-abe9-5b4e8d2f2815 |  | note | iv. Diameter of ducts and conduits = ±3mm
label | 4426e964-cecb-5256-bfb4-7d7281a1d56d |  | note | Method - Measure, Visual
label | 0d211bf6-7918-5a5a-876d-ac842e039d5a |  | note | Frequency - Where applicable, each pile
label | 4c1fc625-0293-5a02-97cb-b70f7ac19a70 |  | note | Category - IP
label | 984d3d19-1860-5364-94fe-3002addec2bd |  | note | Responsibility - Foreman, SE/PE/SPE
checkpoint-status |  |  | checkpoint | 5.7 - Pre-pour Inspection
label | 8bf500a9-9a11-5f78-b74b-08049278c10f |  | note | Reference - IFC Drawings 610.18 (a) (ii) & (iii)
label | d9137330-9211-58ae-b59d-4a0098b5165b |  | note | Acceptance Criteria - Evidence that the forms, reinforcement, electrical continuity and other cast-in items conforming to the requirements of this specification and the drawings has been reviewed by the Nominated Authority. All foreign material has been completely removed from the excavation.
label | 46d6c2b5-f95b-5ce1-bbde-3b8c2865168d |  | note | Attach: Pre-pour inspection checklist
label | a0a05d0d-7abe-510d-aba1-114ffd525450 |  | note | Method - Measure, Visual
label | 687c66a7-b304-5fbb-9c63-73c0d44ced6b |  | note | Frequency - Each pile
label | e2e527e9-87cb-5a15-9bc5-9530af507c68 |  | note | Category - HP
label | 8c5f222e-4d88-5644-a95a-b41807dc9a2b |  | note | Responsibility - Nominated Authority
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 5.8 - Weather Conditions & Evaporation Limits
label | 9d0653cb-b665-5f54-ac33-5071799136a2 |  | note | Reference - Hot and/or Cold Weather Concreting Procedure
label | 0b5e2a2e-41a3-5f05-8fd7-0b42bd742c16 |  | note | 610.17, 610.17 (a) & (e), Table 610.171
label | 0f08bd8f-871e-59b5-bed2-32163f3b07f2 |  | note | Acceptance Criteria - All freshly finished concrete surfaces shall be protected where required from the sun, wind or rain, until curing is implemented.
label | 88b67b5d-b899-5158-b670-086864d48f0f |  | note | • The temperature of concrete, measured immediately prior to placing, shall not be less than 10°C or greater than 32°C
label | 0307caa5-7349-5e81-9e28-6e22a68e40c4 |  | note | • The air temperature, relative humidity, concrete temperature and wind velocity are measured to determine the evaporation rate of water from the concrete.
label | 9ad479c0-f7ee-5506-a7e0-4745bcd15fe4 |  | note | • When the evaporation rate exceeds 0.50 kg/m²/hr apply evaporation retardant at the rates specified on the manufacturer’s TDS.
label | 1b9260d9-9ab2-5153-864d-a5d26d9959ed |  | note | • Record: Required information on the Concrete Pour Record.
label | ddfcbb24-da72-55e6-ad5e-da3d6b2dc0e2 |  | note | Method - Measure, Visual
label | cd21ec00-1d6d-50e7-85e1-591f77988559 |  | note | Frequency - Each pile
label | 18248744-c3b1-53d7-842e-330731c7489b |  | note | Category - IP
label | 6fee3abb-c959-5911-ab1f-495d6d63ae18 |  | note | Responsibility - Foreman, SE/PE/SPE
checkpoint-status |  |  | checkpoint | 5.9 - Concrete Testing - Sampling Frequency
label | 8eeddd14-b72d-5c5a-9e8d-80f5b84d0dfe |  | note | Reference - Site Sampling & Testing Procedure 610.16 (b), Table 610.161
label | 713c4888-dd43-58ab-8528-ecf5bdbf9528 |  | note | Acceptance Criteria - Concrete cast in one continuous operation to be tested at a frequency as shown below:
label | bca3e040-cc8b-5376-a40a-2877e407408b |  | note | • 0m³ to 10m³ = 1 sample
label | b1b0c46f-f233-5474-a704-9a6d2b593acd |  | note | • 10m³ to 25m³ = 2 samples
label | 59394e8c-4a49-580e-b832-5f1288f0636a |  | note | • 25m³ to 50m³ = 3 samples
label | 4c20e2bb-380e-539a-a439-9373b5a0e754 |  | note | • 50m³ to 100m³ = 4 samples + 2 no. VPV cylinders.
label | 8f68cfd5-25e9-52bc-b1a3-1fdb165db829 |  | note | • For each additional 50m³ and additional sample shall be taken.
label | 5a6d3145-a585-5293-b01c-992fb35e4258 |  | note | • Where the time interval between the end of discharge of one truckload of concrete and the beginning of discharge of the next truckload exceeds 45 minutes, the minimum number of test samples shall be one (1) per truckload of concrete.
label | 53030561-2bfa-5b21-bedf-727ff0f0c3ab |  | note | • Each sample shall consist of 1 no. slump or spread test and 3 no. compressive strength cylinders minimum.
label | 68242425-c4b5-5cc8-98d1-3a5737b5557b |  | note | • Compressive strength cylinders = 1 no. 7 day strength, 2 no. 28 day strength.
label | 649dd1b7-f901-5aa1-b76f-708d8ac48336 |  | note | • Note: Additional cylinders may be required for other purposes such as early strength determination of adjacent piles.
label | fc61a5c7-6b89-5fe1-ba13-1029c2a8a1c6 |  | note | • Record: Required information on the Concrete Pour Record.
label | 5e370827-8dfa-5ab9-a21a-a154f76e3756 |  | note | Method - Test
label | bb60f5fd-245d-543d-9960-923f3b821062 |  | note | Frequency - Each pile
label | 5e39e021-52ee-589c-8afb-bafaee88595f |  | note | Category - IP
label | 876550a9-0b80-53da-8e2b-c82ff2bc8983 |  | note | Responsibility - Concrete Tester, Foreman, SE/PE/SPE
checkpoint-status |  |  | checkpoint | 5.1 - Concrete Testing - Spread, Passability & Viscosity
label | 4fd63c90-c2a5-533c-a3d7-41f842951b06 |  | note | Reference - 610.13 (b)
label | b0fa7e0f-5390-5485-af11-db399d236f42 |  | note | Acceptance Criteria - Spread range = 550mm to 750mm
label | 2509fbdd-c889-5ff3-adda-da84a455e05d |  | note | • T500 = 2 seconds to 5 seconds (to reach a spread of 500mm)
label | b4ea97b7-05b7-5c14-b2d6-f67de6e91643 |  | note | • Passability = ≤10mm (aggregate height differential)
label | 105459bb-e163-5d58-8816-779320aab1ca |  | note | • Record: Required information on the Concrete Pour Record.
label | 2abe00b6-6a3b-530a-8d30-7755a3132fde |  | note | Method - Test
label | 7ae6dcf0-d350-58fd-8370-ef76e0507bf7 |  | note | Frequency - Each sample of Self-compacting Concrete
label | f19dd149-a682-5d44-987f-5f4f8812a157 |  | note | Category - IP
label | eefc5dea-863a-57f3-b034-8bf7ad63ec6c |  | note | Responsibility - Concrete Tester
checkpoint-status |  |  | checkpoint | 5.11 - Concrete Testing - Slump Test
label | d99ec75f-1055-5eb7-b9f5-1ebfb9228917 |  | note | Reference - 610.16 (c), Table 610.162
label | dead5f38-8ef7-5fc5-8aec-059ee8b1e919 |  | note | Acceptance Criteria - Consistency of concrete to be determined by a slump test in accordance with AS 1012.3.1
label | bcaf3224-3c36-5e7e-bcfd-ca22b53b20bb |  | note | • Slump to be within limits as per Table 610.162
label | dd47b8f7-94d5-5e2f-9852-e897d4c8b1d3 |  | note | Method - Test
label | 965959b7-49a8-5b94-8949-8514cad7882e |  | note | Frequency - Each sample
label | bc9fd9f3-a106-5efc-8da4-f7cfb030f863 |  | note | Category - IP
label | b9ccd22e-92b7-51cd-9d4a-6227ea5bb085 |  | note | Responsibility - Concrete Tester
checkpoint-status |  |  | checkpoint | 5.12 - Concrete Testing - Compressive Strength Cylinders
label | 339954d6-5b46-5144-bc19-d6db95bd3162 |  | note | Reference - Site Sampling & Testing Procedure 610.16
label | d4f22888-65f3-55cc-88e5-ed7190a7eedc |  | note | Acceptance Criteria - Correct quantity of cylinders manufactured per sample.
label | 15701cd4-c497-587b-a117-49d86291f76c |  | note | • Record: Required information on the Concrete Pour Record.
label | 581ec8b8-a397-5634-9446-4953b4cae242 |  | note | Method - Test
label | d93be502-314f-5f32-9e4f-951181640ef0 |  | note | Frequency - Each sample
label | 010debe7-b34f-5329-b23e-ec48fb9c2760 |  | note | Category - IP
label | 3af187e7-55fd-59bc-a27d-a509f7f5fd8a |  | note | Responsibility - Concrete Tester
checkpoint-status |  |  | checkpoint | 5.13 - Placement & Compaction (Dry or Wet Excavation Conditions)
label | dbc8a8c7-75ca-5e31-87c2-6e3c73bc7c6d |  | note | Reference - Piling Quality Procedure 610.18 (a) & (b) 610.18 (d) (i) 606.06 (a & b)
label | 3dcdb867-6568-5ca1-8f9c-76d071c87d27 |  | note | Acceptance Criteria - Concrete shall be placed within 24 hours of excavation - where this has not been achieved, the internal wall & base of the excavation shall be cleaned to an additional depth of 25mm. All concrete batches are traceable.
label | 11a4e1bb-40ed-5dde-ae1e-b0f7cb7cb706 |  | note | Concrete shall be placed through either a tremie pipe or concrete pump and not dropped freely from a height exceeding 2m. The initial discharge is pumped to waste until a consistent workable mix is discharged. the ends of the discharge pipe shall not be lifted off the base of the excavation until a 2m head is created, which shall be maintained until the completion of the pour.
label | 85e4f450-9452-507d-a0b7-088402647ecb |  | note | Where a casing is used, it shall be withdrawn with care and at a rate to ensure that the free surface of the concrete is at least 1.5m above the bottom of the casing.
label | 0c2566b5-77eb-5015-8866-1bb38ea90c93 |  | note | Pile height is to be 300mm above the cut-off level (or 400mm in wet piles) to allow for breaking back of sound concrete.
label | 8ce9632b-7270-5ca2-b460-022071444a71 |  | note | Record: Required information on the Concrete Pour Record.
label | 26b3aaed-5909-5797-b2d1-e2ded171c841 |  | note | Attach: Concrete Pour Record Attach: Concrete Dockets
label | e4892247-f154-548a-9dae-2f9f5386b1e2 |  | note | Method - Visual
label | 9998f7ec-f779-5721-8efc-237dadfea111 |  | note | Frequency - Each load
label | 029b8402-81fa-553f-b494-edb4458de2a3 |  | note | Category - SP
label | 2d58e2da-f96c-55fd-b1f0-5db22ab3799e |  | note | Responsibility - Foreman SE/PE/SPE
checkpoint-status |  |  | checkpoint | 5.14 - Surface Finishes
label | ebcc2c88-7092-5196-a6ce-7574510af960 |  | note | Reference - IFC Drawings 610.31 610.20
label | 8215324d-1f7d-5f4a-96af-45f31354094e |  | note | Acceptance Criteria - Surface finish as per IFC drawings. Where surface finish is not detailed, the VicRoads class finishes will apply as per 610.31. Construction joints shall be roughened in locations shown on the drawings - any proposed changes to construction joints shall be subject to approval from the Nominated Authority.
label | 5ed93a94-a990-5187-9ce3-930fdde8c54b |  | note | Method - Visual
label | 3aeaff0f-1473-5b08-8023-5adde69bd308 |  | note | Frequency - Each pile
label | 246e8753-009f-5563-8341-0976abd48111 |  | note | Category - IP
label | 1009122c-5ea5-5717-93c7-e6e53c300070 |  | note | Responsibility - Foreman SE/PE/SPE
checkpoint-group |  |  | section | 6. Post-construction Activities
checkpoint-status |  |  | checkpoint | 6.1 - Compressive Strength Test Results
label | 0973e628-d3e7-58bb-b352-3951da99b9f2 |  | note | Reference - IFC Drawings Table 610.05.051 610.16 (g)
label | 8119428a-0323-5172-ab4b-84d8abd0926d |  | note | Acceptance Criteria - 7 day compressive strength to comply with table 610.051 for early indication that the strength is tracking correctly. 28 day compressive strength (average of the 2 no. cylinders) per sample comply with the design strength.
label | eab6cff9-4608-5f85-ba4a-e4bc23f766df |  | note | Note: 1 of the 2 no. 28 day cylinders per sample may be as low as 90% of the required strength, so long as the average meets the required strength.
label | 80d51d73-ee8c-51a8-90aa-c866e5be4c47 |  | note | Attach: Compressive Strength Test Results
label | c9ac4376-61a3-5f95-ae3a-4d8a7a4b095d |  | note | Method - Document Review
label | 1e5e60c5-087d-5c40-ba2a-f86d4f380729 |  | note | Frequency - Each cylinder
label | 33f05b57-578f-5f8c-a281-7b11ff23898a |  | note | Category - IP
label | e2345867-8ac3-590a-97f3-56ee9319e253 |  | note | Responsibility - SE/PE/SPE
checkpoint-status |  |  | checkpoint | 6.2 - Pile Integrity Testing
label | c22ade0c-dda3-57dc-a64e-cb5b67d8eb5e |  | note | Reference - 606.07 (a, d & e) AS2159 Clause 8.8
label | 814cdc9f-47e6-528c-b2ce-e863e8a62fcd |  | note | Acceptance Criteria - Pile integrity testing shall be conducted after the concrete strength has reached 25MPa but not less than 7 days from casting.
label | af9f1f02-777d-5b55-86cd-de6cf8c31d02 |  | note | Cross-sectional area = ≥95%
label | 97001915-0b07-5513-be75-a517a7df65ff |  | note | If any test fails, all piles shall be tested.
label | 237f731b-9d0f-5529-a8be-60ffe1d26ebd |  | note | Attach: Pile Integrity Test Report
label | 47574f8e-5309-59ea-affb-f447859d5446 |  | note | Method - Document Review
label | e9de3542-9864-54e0-ab64-67e16fc5e5c2 |  | note | Frequency - Piles #1 - #6. Reduced to 1 test per 3 piles if the first 6 tests pass
label | 49edb50f-d575-5f5e-8b1d-fbc695211e0f |  | note | Category - IP
label | 6d4eae9c-85d9-579b-ba4d-44ba0fa92e68 |  | note | Responsibility - Testing Consultant SE/PE/SPE
checkpoint-status |  |  | checkpoint | 6.3 - As-built Survey
label | 2b2ccff2-65d2-5a37-93a3-5ba65670dfc4 |  | note | Reference - IFC Drawings 606.08 (a - c) AS2159 Clause 7.2.2
label | bdcacaff-3c90-5dc9-8185-f03b5fd81c2a |  | note | Acceptance Criteria - The following tolerances apply to piles:
label | 141ab626-67ee-501b-94aa-fec165e189f9 |  | note | i. Pile head plan location = ±75mm
label | 8c5b2f19-8213-5f12-a8e3-60346ad5a09d |  | note | ii. Variance from vertical or rake = 1:100
label | 5821696a-04ea-5cff-8e3b-e576b2748de7 |  | note | iii. Irregularities in straightness = 1:100
label | a4a4631c-bfcf-5eef-b900-2dd334487343 |  | note | iv. RL = ±25mm
label | 1a353006-949c-5649-9628-16fd953fa526 |  | note | Attach: Survey As-builts / Survey Report
label | 9454da16-37c3-579d-b497-3df33bc73ba4 |  | note | Method - Document Review
label | 65d89804-763d-58fd-8beb-4b9c917f79bd |  | note | Frequency - Each pile
label | d0ef343f-3ab0-58af-bee5-cbd3ebc27c40 |  | note | Category - IP
label | 632a0b7c-eb07-55ae-bfd5-151f31d1483a |  | note | Responsibility - Surveyor SE/PE/SPE
checkpoint-status |  |  | checkpoint | 6.4 - Non-conformance Report (NCR) Closure
label | 9479bb22-7c38-51bd-a8ee-9ef528490f8e |  | note | Reference - MRPA Quality Management Plan
label | caa202db-4072-5fa8-a436-223c35d66fb0 |  | note | Acceptance Criteria - Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed.
label | e92c41b0-6433-57c7-8fff-cda37693eaae |  | note | Method - Document Review
label | ea1c2c0f-33b5-50d7-8a45-d9e959cefbc3 |  | note | Frequency - Once, prior to closure of this lot / element / Work area
label | 6418e0e5-c293-5280-979b-6aacfab4d81a |  | note | Category - HP*
label | 0574440d-5a98-5f6d-a6d7-e8924b29de34 |  | note | Responsibility - SE/PE/SPE
checkpoint-status |  |  | checkpoint | Final Inspection
label | e89e164d-af14-5769-9f17-83bc764556f0 |  | note | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed above have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
text | a7889a08-5a4f-5cdc-9f3a-b4fc04857e42 |  | textbox | Name:
text | 91964bd5-627c-5354-93c2-6453626f5222 |  | textbox | Position:
text | 26297967-63df-5eb0-8506-f500a7a5df1e |  | textbox | Date Completed:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | ITP-018-CIV - Rail Delineation Temporary Fencing |  |  |  |  | Yes | ITP-018-CIV - Rail Delineation Temporary Fencing | d5893295-6f23-44df-9977-9016088197db
checkpoint-group |  |  | section | 1. Referenced Documentation
checkpoint-no-status |  |  | checkpoint | 1. Referenced Documentation
label | 49a60d57-6123-55aa-b7be-8a3ac319df20 |  | note | ITP-018-CIV-Brunt - Rail Delineation Temporary Fencing
label | 004e7bf7-04cc-5797-a0c8-f77b5bfeb28a |  | note | Rail Delineation Temporary Fencing
label | 05937d5e-05eb-503f-8173-a4a5afb41186 |  | note | CIV
label | 39b8aecc-a924-52bd-a916-1d3d6d511c72 |  | note | B
label | 26157d17-12a8-5451-88c0-67dabf0e4bf4 |  | note | 12/01/2023
label | f5e170dd-c3cd-5fc0-97c5-ad2808e9b949 |  | note | Casey Knowles
label | 71fbd623-fa48-56fa-b525-8b5ecacdeccf |  | note | Jon De Castro
label | 42a58549-c3ab-5734-92f9-4aca1ffce1dd |  | note | ITP for Brunt Rd only
checkpoint-status |  |  | checkpoint | 1.1 - Non Dependent
label | 2a8dffb2-68f4-56ab-8267-6b79039a65a2 |  | note | Reference - IFC Drawings L1-CHE-STD-005 L1-CHE-STD-025
checkpoint-group |  |  | section | 2. Preliminaries - Materials
checkpoint-status |  |  | checkpoint | 2.1 - Concrete Mix
label | 47a88c6d-99ce-56d9-b81c-4296f94a7690 |  | note | Reference - IFC Drawings
label | 1f8f3773-4552-5da2-8fca-4e45f9ea0688 |  | note | Acceptance Criteria - 32MPa concrete to be used as per IFC drawings. Attach concrete delivery docket.
label | fad838b6-117d-5c25-8bfa-8f3fec182da1 |  | note | Method - Document Review
label | 465f6575-e2da-5ee4-b4a4-17b91c139182 |  | note | Frequency - Each Mix
label | c65899e4-f70a-5dd7-b994-f192d1f1d8e2 |  | note | Category - HP
label | 37647053-5974-590b-86c9-32fcf9a52e62 |  | note | Responsibility - SE/Site Supervisor
label | f50fafae-c8a3-53d1-9a60-d87721ed1afe |  | note | Verifying Documents - Supplier Certificate of Compliance Deivery Docket
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.2 - Steel components
label | 43f5e242-67a4-53d0-9f15-d42f95ea2531 |  | note | Reference - IFC Drawings AS41000 AS1163
label | aad9508b-99cd-5949-a2a6-c0879564fce3 |  | note | Acceptance Criteria - All Steel must comply with Australian Standards. All dimensions relevant to setting out and site work are to be checked on site by the project engineer prior to works commencing. Erection and fabrication tolerances for structural steelwork as per AS4100. Steel section sizes must be checked on site. Steel posts to be CHS with a grade of C250.
label | 68e38571-4c53-55f4-9706-1b5e67fee084 |  | note | Method - Document review Visual and Measure Order Acceptance Checklist
label | 7e5e872f-74be-5056-b114-360a394a55a1 |  | note | Frequency - All elements
label | d9013d35-bae3-5ab0-ae7d-18c7c680d90c |  | note | Category - IP
label | 8b909d21-7bfa-5c6b-81bc-ec20c9e003c0 |  | note | Responsibility - SE/Site Supervisor
label | 31969b90-b953-5ff5-9610-ddd905d0d0c7 |  | note | Verifying Documents - Supplier Certificate of Compliance
checkpoint-group |  |  | section | 3. Preliminaries - Documentation
checkpoint-status |  |  | checkpoint | 3.1 - Excavation works
label | 746f05a8-9cb3-5aef-99a8-97e1b6741361 |  | note | Reference - IFC Drawings L1-CHE-STD-005
label | 0b971038-b61c-5974-ac75-f8b8416c5882 |  | note | Acceptance Criteria - Excavation for post foundation must not undermine track and comply with PTDT requirements. Follow asset owners guidelines for work around their service. Where posts are within 1m of an underground service, or whereelse nominated, post footing installation shall be via Non Destructive Digging. Direct driven installation method to be used for all other posts.
label | 13dbafa5-7241-5964-8836-36c8a07348c5 |  | note | Method - Document Review Visual
label | 13176b84-2181-5f95-9bdd-4dd04ea67f58 |  | note | Frequency - Each Post
label | 3a345071-3c5c-55e4-bcd9-dbaf004afc52 |  | note | Category - IP
label | f7b83b8e-1327-527a-bef4-e217b1ff5d9c |  | note | Responsibility - SE/Site Supervisor
label | 51ec3f16-acc9-5089-886e-3423c124400f |  | note | Verifying Documents - This ITP
checkpoint-group |  |  | section | 4. Pre-construction / Pre-installation Activities
checkpoint-status |  |  | checkpoint | 4.1 - Survey Set-out
label | 4354b5ad-148a-5feb-b0c5-a4fd6827327a |  | note | Reference - IFC Drawings
label | 8b11fcad-069d-5452-bb6f-51152ab69e64 |  | note | Acceptance Criteria - Survey to set out the following but not limited to: existing services, post locations, refuge bays, gate locations, tie in points. Offset checked against the running edge prior to installation of posts. Up track & Down track: Minimum offset 2135mm from centreline of track. (1285mm outside edge of track - Engineer to verify with timber jig template)
label | e3a55277-3c60-5aaf-a95f-8d2993c5c464 |  | note | Method - Measure Visual inspect
label | 85f06c05-df5a-5869-8e77-1177888cb636 |  | note | Frequency - Each element
label | 6e26e5a2-dc02-59e2-b5f4-1ccb78c62dd3 |  | note | Category - IP
label | ed5ece6c-530e-5cab-ab49-ddfa30530145 |  | note | Responsibility - Surveyor SE/PE/SPE
label | 2c880b13-ccda-526d-aa13-f4f4dad1ba24 |  | note | Verifying Documents - This ITP
checkpoint-group |  |  | section | 5. Construction / Installation Activities
checkpoint-status |  |  | checkpoint | 5.1 - Ground Conditions
label | 23486828-33da-5083-a2c5-d4e1dd7d80b7 |  | note | Reference - IFC Drawings
label | ef49b2f3-119a-56ef-908e-0324f4e85a7b |  | note | Acceptance Criteria - All post foundations to be inspected by the site team prior to installing the posts. All foundations are to be free of water and loose material.
label | a78e4402-7058-5d25-bec6-1baae39cad42 |  | note | Method - Visual
label | 89f204c9-bd12-5f35-9504-48cc4fa9f1f6 |  | note | Frequency - Each post
label | 2bb05fad-3eba-56be-9338-60100d6af1de |  | note | Category - IP
label | 71baf2cf-e7a8-59f9-b6ec-ab5cb7e8f375 |  | note | Responsibility - SE/Site Supervisor
label | 8fafa8f8-3cff-5286-9bd5-177d8174624f |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.2 - Post Foundation
label | 1f6c1322-3b7f-5fa6-b463-6c4ae1a99851 |  | note | Reference - IFC Drawings
label | 4ca189e9-92c6-5c08-b722-e6f4381ff4c3 |  | note | Acceptance Criteria - Post into 101.6x4 CHS Sleeve - 300mm Dia - 1300mm Depth - 2700mm Typical Spacing
label | 8b83fb41-283f-5030-91bb-70f89dea38be |  | note | Concrete Footing (for Steel & Timber Posts) - 300mm Dia - 700mm Depth - 2700mm Typical Spacing - 600mm Post Embedment
label | f7bc3401-a5dd-51de-8928-fce8d4965834 |  | note | Direct Driven 88.9x4CHS Posts - 300mm Dia - 1500mm Depth - 2700mm Typical Spacing
label | cfffcb64-04df-5ccf-867a-040ac64c6489 |  | note | Gates - 350mm Dia - 1100mm Depth - 1000mm embedment depth - 1350mm end span spacing
label | e6d1c2f2-e6b6-56d2-a2b0-0abf480a0fd9 |  | note | Where post is installed through a slope/embankment, increase the depth of embedment by 600mm from the above requirements.
label | 1a67751d-98eb-50a0-8524-78039394ee95 |  | note | Section 610.161 Concrete testing at frequency as per 610.161. Minimum of 2 samples per truck.
label | 4e960bab-f889-5d87-b090-e541877b7d70 |  | note | Method - Measure
label | d604e622-e325-54e6-a093-1541c34e78d7 |  | note | Method for Section 610.161 - Concrete Testing
label | 9636d6a0-6913-5b7a-9dd4-fad18142c44e |  | note | Frequency - Each footing
label | 4ea90bdb-d70d-5df3-9851-505be07bc053 |  | note | Frequency as per 610.161
label | 7fc7ce7b-7c2c-5c96-9090-179e3b6b6ad9 |  | note | Category - IP
label | b10326f6-3ce3-56ea-a6e0-828a4a18dff1 |  | note | Responsibility - SE/Site Supervisor
label | 4bfec945-e638-560f-aff6-14088bd969b9 |  | note | Responsibility for Section 610.161 - Testing Report
label | 3e3fcdb0-146f-5c53-83d8-2ff6f1c3708e |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.3 - Post Installation
label | cf971ca5-ad2c-5529-83ad-b513cef13a2f |  | note | Reference - IFC Drawings L1-CHE-STD-005
label | e532c69b-3dc0-5a93-8961-159cacc277ab |  | note | Acceptance Criteria - Up track & Down track: Minimum offset 2135mm from centreline of track. (1285mm outside edge of track - Engineer to verify with timber jig template)
label | f001543d-2005-514a-a4c0-fef2cc86b2fc |  | note | Maximum post spacing to be 3.1m to avoid clashes (localised only).
label | 5afe9b53-8275-5ada-aa78-904369e93aa3 |  | note | Two spans at 1350CTRS at the end and at Refuge bays.
label | c548d363-c92a-5aa4-a9ac-d5ef9d0e6305 |  | note | Max. post height 1800mm above ground level.
label | 5dd8fac0-9455-5edc-9a6b-afad0faab199 |  | note | Vertical Tolerance: ±20mm from the design line.
label | 6fe7376b-c944-59b7-976c-93b69f877b12 |  | note | Timber Post to be installed directly either side of OHLE footings (existing and future).
label | d784857a-6fd5-5f4f-a8fc-545c410ebfbb |  | note | Method - Measure
label | 211b8e04-a859-5287-a305-6f5bd032cce1 |  | note | Frequency - Each post
label | 8796a8d0-5340-57fa-8672-12aae4ddd175 |  | note | Category - IP
label | 2794f13c-ae4f-52fd-8c38-df1ad9f798e9 |  | note | Responsibility - SE/Site Supervisor
label | edb3e090-070e-50b1-b86c-78253cbe27c3 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.4 - Chain Wire Mesh Installation
label | 6d38b241-4e87-5069-9878-e5af856b25ba |  | note | Reference - IFC Drawings
label | 5678344b-dcfa-5ad0-8707-fed1bd27e053 |  | note | Acceptance Criteria - Chain-wire mesh 1800x50x2.50 to be fixed to fence post with 1.57mm tie wires.
label | 9193df3b-210d-5e64-8eac-5f52ef496631 |  | note | Chain shall be tightened and securely fastened to posts at max. 400 crs and tension wires at max. 500 intervals with 2.5 dia. galv. tie wire or approved clips.
label | 9688de5d-4bfa-59b4-b9fd-a422901f0a09 |  | note | PVC coated mesh and tie wire to be installed for 2m extent either side of OHLE footings (existing and future).
label | 49f21903-d3f4-55cd-88b1-b229b0fb1df7 |  | note | Distance between ground and bottom of chain mesh and ground to be 50mm.
label | e22a3857-59eb-5150-bc72-631cb139a45c |  | note | Method - Visual
label | 77ba1fda-0dc5-51e4-9d45-38feaa67d47b |  | note | Frequency - Each element
label | 81b8af1d-342e-5835-bfd0-ae5a1c4fdfb8 |  | note | Category - IP
label | fc72415e-c29a-54dd-816b-e6ff69a3ba6b |  | note | Responsibility - SE/Site Supervisor
label | c2ba6288-f9ae-5341-98a2-22d7d7800fd6 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.5 - Bracing
label | e285804e-4544-5d5d-9831-6d345a5e4c1c |  | note | Reference - IFC Drawings
label | 04aeb4a0-044a-558f-8cda-8daa90cd63ff |  | note | Acceptance Criteria - 48.3 X 4 CHS brace at end bays and corners fixed each end via approved proprietary post and rail clamps.
label | 0d2055fc-371a-5e89-bb13-10119de679cd |  | note | Bracing to be installed on both sides of the fence at the fence corners
label | ab353d7a-98ba-5b9b-86ea-ac8498c7c7b0 |  | note | LVL Brace to be used between timber and steel posts either side of OHLE footings (existing and future).
label | 5cbedd33-eb2c-5564-8040-45785cec9eeb |  | note | Method - Visual
label | a0a30cc2-6f4e-5294-8f21-6e6c3505d6cb |  | note | Frequency - Each element
label | 9ff30c8b-b87c-55d9-8b2c-3478781e9e00 |  | note | Category - IP
label | 8de83fba-2a21-5502-9f27-e4ef089e1801 |  | note | Responsibility - SE/Site Supervisor
label | f3669e03-cf21-560f-baee-b0825ee65f31 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.6 - Refuge Installation
label | 0be0407d-2057-54df-8164-da8777a31d32 |  | note | Reference - IFC Drawings
label | 9826e0e2-62f2-5c02-9232-b5e98c6c7ceb |  | note | Acceptance Criteria - Refuge Access to only open from track side.
label | e580def4-c676-566f-8ebc-71c06b91e480 |  | note | No chain wire mesh to be installed at refuge access.
label | 91b6cf41-f7ca-552f-b589-bea179eb35be |  | note | Refuges at southern fence shall be staggered in relation to the northern fence refuges. Refuges to be at maximum 20m c/c spacing.
label | 777a0624-bc31-5ba4-a541-f578a8a342ca |  | note | 50dia PVC pipe push out bars to be installed. PVC tubes to be pushed off from track side only.
label | c488423c-2815-5386-801c-0060493cb192 |  | note | Method - Visual
label | 54cc27cf-531c-5349-a92a-9e14bb54ed2e |  | note | Frequency - Each element
label | e7e5bf24-af5f-5779-8b11-f1dd7253171c |  | note | Category - IP
label | 37f5601d-984d-5029-bda6-1c8cd3d1c816 |  | note | Responsibility - SE/Site Supervisor
label | abb6bb21-04d9-5cb3-a619-bde27e5129ba |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.7 - Refuge Signage
label | 5e62ca1f-ed75-5861-a660-b11a7afcd564 |  | note | Reference - IFC Drawings
label | 5784ab9b-c4db-5195-bd3a-ad8942d3b413 |  | note | Acceptance Criteria - Sign shall be installed on fence half way between refuges indicating distance to adjacent refuges. Max size of signage to be A3 or smaller (297mmx420mm MAX)
label | 64208897-0291-5a5d-8c81-2d79384a80c6 |  | note | Method - Visual
label | fd13c10c-5c46-52a1-a655-937897db63e6 |  | note | Frequency - Each element
label | 9b3d222e-7fb4-5487-8885-8df0da101902 |  | note | Category - IP
label | 77f57202-29f3-53f1-a6b0-e60ba98262ea |  | note | Responsibility - SE/Site Supervisor
label | 8005ca26-59e4-5a78-ba8a-52c61864b319 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.8 - Fence Tie In
label | 8c9bc60a-c6d7-5afa-b50e-8540dfc89cd2 |  | note | Reference - IFC Drawings
label | 0ab05ce6-09ba-5ee1-8652-3c775917ee7c |  | note | Acceptance Criteria - 200mm Air Gap to be provided to existing fence to provide electrical discontinuity.
label | 797b4484-ed2f-5765-a4ba-9a5eb07215e2 |  | note | Method - Measurement
label | b7636286-e696-5a1b-9e0a-6f0080041231 |  | note | Frequency - Each Tie In
label | d92fa36a-aa5e-5b74-9cbd-fb024a05789a |  | note | Category - IP
label | d0aaf000-801e-5163-9aff-3bba0499ee90 |  | note | Responsibility - SE
label | 223e1f94-4634-57b0-b2fb-e12555c90ac9 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 5.9 - Gates
label | 9aeb0f06-0da3-5114-bf79-80593abcdda9 |  | note | Reference - IFC Drawings
label | e4f35f63-2865-52b8-8731-cd212c8841ee |  | note | Acceptance Criteria - Gates to be installed as per IFC drawings. Location may be moved nominally to avoid service clashes.
label | 0fcf76bb-bc05-5aaf-9ee6-864ebcecef9f |  | note | Method - Inspection
label | 704048f5-3aca-50f1-9c3e-b34dda0158ec |  | note | Frequency - Each element
label | 9d4a3491-a19e-55cf-b7b9-170ef9dc1653 |  | note | Category - IP
label | 7b2c7f3a-5328-572e-9cc1-5f116b2da8fd |  | note | Responsibility - SE
label | 7bcfc6b9-7795-5569-a402-6fadf7936430 |  | note | Verifying Documents - This ITP
checkpoint-group |  |  | section | 6. Post-construction / Post-installation Activities
checkpoint-status |  |  | checkpoint | 6.1 - Fence Height and Track Clearance
label | cf442c4e-c33d-5cef-aa37-a000215ef6de |  | note | Reference - IFC Drawings
label | d7dbecd1-e4f7-551a-b5a5-d85ea510f3f0 |  | note | Acceptance Criteria - Posts are to be checked for verticality and ensure offset is not less than required from near face of post to centreline of track or as shown on alignment drawings. Attach as-built survey.
label | ba894dc1-d999-57d8-b7b2-7dc7c4b0b016 |  | note | Method - Survey / Measure
label | 391efbbc-fb16-56c4-8b1c-a71ed9d76952 |  | note | Frequency - Each lot
label | f0d79ab1-2a5b-535b-ab43-c9b09e3ce516 |  | note | Category - IP
label | 5b6ca6e8-8518-5231-91b6-1d5f62f87ebd |  | note | Responsibility - Surveyor SE/Site Supervisor
label | ade9378e-84ef-564f-ab93-88b1339d7aa7 |  | note | Verifying Documents - As-built survey
checkpoint-status |  |  | checkpoint | 6.2 - Compressive Strength Test Results
label | c9093542-6ed3-54b3-aa62-17ef9dab268a |  | note | Reference - IFC Drawings Table 610.05.051 610.16 (g)
label | 6874aee7-3030-527f-9c9a-3bede66730bb |  | note | Acceptance Criteria - 7 day compressive strength to comply with table 610.051 for early indication that the strength is tracking correctly. 28 day compressive strength (average of the 2 no. cylinders) per sample comply with the design strength.
label | 1468fd3c-5f67-5ee6-8ace-40cb9bb08173 |  | note | Note: 1 of the 2 no. 28 day cylinders per sample may be as low as 90% of the required strength, so long as the average meets the required strength
label | d972ca36-b0d2-53e5-8fc7-1805498efb8d |  | note | Attach: Compressive Strength Test Results
label | 0a9644b9-5a87-5eb6-aaf8-422b17750f14 |  | note | Method - Document Review
label | f8217460-d5e0-5c0e-9508-cba33f895b43 |  | note | Frequency - Each cylinder
label | 62c960da-f1b9-5e61-b25f-56bc1abe4abf |  | note | Category - IP
label | eaf7232a-fb89-5a48-825a-b5e7976d0b08 |  | note | Responsibility - SE/PE/SPE
label | 20fe5757-37dd-59f0-b6a8-a9fe0c090f7a |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | 6.3 - Non-conformance Report (NCR) Closure
label | f0af6660-3bba-5898-b888-8be70ed9bc64 |  | note | Reference - MRPA Quality Management Plan
label | 73d8010c-9604-53b0-aeb0-feb9c5b536cd |  | note | Acceptance Criteria - Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed.
label | 295d5bf7-383b-5205-bb6c-ca4fa06fa177 |  | note | Method - Document Review
label | 59e3d294-acfa-5f1e-97cf-ef9315d54327 |  | note | Frequency - Once, prior to closure of this lot / element / Work area
label | 8f32cf8f-7c6d-5da9-a4d4-44447eaf85a5 |  | note | Category - HP*
label | 3a82e2e4-cfdd-59ac-840b-591962fba7b9 |  | note | Responsibility - SE/PE/SPE
label | 55c1dbc2-4996-5ab3-8198-4ea381913302 |  | note | Verifying Documents - This ITP
checkpoint-status |  |  | checkpoint | Final Inspection
label | f8699205-a213-5aa7-a73a-06b8836c5969 |  | note | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed above have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
text | aed79ae8-abf3-5f0e-bc61-ab0724ab1db6 |  | textbox | Name:
text | 6a91607d-f6d8-5917-8f37-c45d98e89380 |  | textbox | Position:
text | 09b6037e-8554-5bf4-80df-69f833451586 |  | textbox | Date Completed:
holdpoint |  |  | signoff | Sign ITP