## Resources
type | name | values | prefix | postfix | Template Name
checklist | 0012 Street Pole Foundation and Erection |  |  |  | 0012 Streetlight
section | Preliminary Inspections and Tests
checkpoint | RDM & Consent Approval
signoff | Nominated Authority Sign off
checkpoint | Define LOT Area
checkpoint | Understanding of the Scope of works
checkpoint | Ensure materials available
checkpoint | Site inspection and SWMS
section | Street Light Foundation & Erection
checkpoint | Pre-start meeting
checkpoint | Site Inspection, JRA .
checkpoint | Drawings referenced. (3)
checkpoint | The LOT is not defined by an area/zone, it is defined by the Lights listed in the Summary Report. (2)
checkpoint | Excavation completed. (6)
checkpoint | Foundation Installed. (6)
Completed 20040-5 SK01 Foundation Inspection and signed off by qualified person. (6)
checkpoint | Pole Installation and equipment (Luminaire, Fusing and Earthing) as per AS/NZS 3000:2007. (6)
checkpoint | Grouting completed within 7 days of installing the pole as per Specification references 26. (6)
checkpoint | All test sheets completed as per AS/NZS 3000:2007.
checkpoint | All refuse removed from work area.
checkpoint | Photos to be taken of critical elements above as evidence of QA. (6)
section | Completion Inspections and Tests
checkpoint | Inspection by supervisor
checkpoint | Notice of Completion
signoff | Nominated Authority Sign off
checklist | 0011 GPO/Electrical Equipment |  |  |  | 0011 GPO/Electrical Equipment (V2)
section | GPO & Electrical Install
checkpoint | Drawings referenced. (3)
checkpoint | The LOT is not defined by an area/zone, it is defined by the equipment listed in the Summary Report. (2)
checkpoint | Installed as per AS/NZS 3000:2007. (6)
checkpoint | Photos to be taken of critical elements above as evidence of QA. (6)
section | Completion Inspections and Tests
checkpoint | Notice of Completion
signoff | Nominated Authority Sign off
checklist | 0005 Earthing/Bonding |  |  |  | 0005 Earthing/Bonding (V3)
section | Earthing & Bonding
checkpoint | Drawings referenced. (3)
checkpoint | Define LOT Area. (2)
checkpoint | Weld copper wire to steel pile as specified on pile plan. (6)
checkpoint | Feed and cable tie copper earth wire to correct point. (6)
checkpoint | All Earth, Bonding and Equipotential Bonding to AS/NZS 3000:2007. (6)
checkpoint | Complete McKay I&T Form 20 - Earthing Resistance Test sheet. (6)
checkpoint | Photos to be taken of critical elements above as evidence of QA. (6)
section | Completion Inspections and Tests
checkpoint | Notice of Completion. (8)
signoff | Nominated Authority Sign off
checklist | 0003 Containment |  |  |  | 0003 Containment (V4.2)
section | Containment
checkpoint | Drawings referenced. (3)
checkpoint | Define LOT Area. (2)
checkpoint | Ensure cable ladders and trays are provided to support cable. (6)
checkpoint | Ensure cable ladders and trays have enough support, and 50% spare capacity. (50% spare capacity as per original design.) (6)
checkpoint | Ensure cable ladder and tray is installed to manufacturer’s instructions, complete with all necessary splice plates, bends, and fixings. (6)
checkpoint | Ensure adequate access for replacing, inspecting, or adding cable. (as at time of install.) (6)
checkpoint | Ensure seismic supports and bracing installed according to KCL design.) (7)
checkpoint | Photos to be taken of critical elements above as evidence of QA. (6)
section | Completion Inspections and Tests
checkpoint | Notice of Completion. (9)
signoff | Nominated Authority Sign off
checklist | 0002 Cable Installation |  |  |  | 0002 Cable Installation (V3.1)
section | Cable Installation
checkpoint | Drawings referenced. (3)
checkpoint | The LOT is not defined by an area/zone, it is defined by the cables listed in the Summary Report. (2)
checkpoint | Provide logical cable management and reticulation system coordinated with other trades. (6)
checkpoint | All cable routes rationalised where possible. (6)
checkpoint | Maintain Minimum Separation Distances as per 22.2.3. (6)
checkpoint | Catenary Installed. 6 cables/cat wire max. No excessive sag. Cable tied regularly. (6)
checkpoint | Conduit installed. 22.5.2-fix conduit saddles at a maximum of 1m intervals in horizontal runs and 2m intervals in vertical runs. (6)
checkpoint | 22.2.8-Fixing with nylon ties to slab or roof structure at max intervals of 1500mm (for 1/2 cables only). (6)
checkpoint | All wiring systems adequately protected as per 22.2.4 (6)
checkpoint | All cables and supports concealed as per 22.2.6 (6)
checkpoint | Cables installed as per manufacturer’s instructions. (6)
checkpoint | As required: Acoustic sealing completed for the cables included in the ITP. (6)
checkpoint | Written approval obtained where cables/conduits must be run surface mounted as per 22.2.7 & 22.6.1. (6)
checkpoint | Photos to be taken of critical elements above as evidence of QA. (6)
section | Completion Inspections and Tests
checkpoint | Notice of Completion (8)
signoff | Nominated Authority Sign off
checklist | 0009 Cables and Conduit Underground (V2) |  |  |  | 0009 Cables and Conduit Underground
section | Preliminary Inspections and Tests
checkpoint | RDM & Consent Approval
signoff | Nominated Authority Sign off
checkpoint | Define LOT Area
checkpoint | Understanding of the Scope of works
checkpoint | Ensure materials available
checkpoint | Site inspection and SWMS
section | Conduit & Cable Works
checkpoint | Pre-start meeting
checkpoint | Site Inspection, JRA .
checkpoint | Ensure HD conduits are used
checkpoint | Each length of duct is to be fully inserted into the next and glued
checkpoint | Ensure separation of Low Voltage cables from Telecommunication cables is as AS/NZ 3000 2007
checkpoint | Entry and exit of ducts are at the correct location as per set out
checkpoint | Conduits installed
checkpoint | Cable installed
checkpoint | Push snake through fully completed duct install and pull through draw wire (string)
checkpoint | Seal off open ends of ducts with tape
checkpoint | Photos to be taken of critical elements above as evidence of QA
section | Completion Inspections and Tests
checkpoint | Inspection by supervisor
checkpoint | Notice of Completion
signoff | Nominated Authority Sign off
checklist | 0007 Switchboards |  |  |  | 0007 Switchboards (V2)
section | Preliminary Inspections and Tests
checkpoint | RDM & Consent Approval
signoff | Nominated Authority Sign off
checkpoint | Define LOT Area
checkpoint | Understanding of the Scope of works
checkpoint | Confirm Position
checkpoint | Site inspection and SWMS
section | Switchboard Installation
checkpoint | Drawings referenced. (3)
checkpoint | The LOT is not defined by an area/zone, it is defined by the cables listed in the Summary Report. (2)
checkpoint | FAT (Factory Acceptance Test). (6)
checkpoint | Arrived and checked. (6)
checkpoint | Pre-start meeting
checkpoint | Site Inspection, JRA .
checkpoint | Drawings referenced in Reference Documentation.
checkpoint | Layout drawing confirmed as current.
checkpoint | Installed as per AS/NZS 3000:2007. (6)
checkpoint | Position confirmed. (4)
checkpoint | Terminations checked. (6)
checkpoint | CCT labelling completed. (6)
checkpoint | All Cable glands compressed. (6)
checkpoint | Seismic Restraints installed as required. (7)
checkpoint | Incoming submain terminated and photographed. (6)
checkpoint | Complete McKay Test Forms as required: (6) McKay I&T Form 0 - Visual Inspection McKay I&T Form 19B-1 - Local DB Power Cable: Inspection and Test McKay I&T Form 20 - Earthing Resistance Test Sheet McKay I&T Form 19B-2 - Local DB Power Cable: Inspection and Test – Live : To Be Completed once the Pre-livening tests and inspections are complete, and will be submitted with Commissioning Results.
checkpoint | All ASNZS 3000:2007 tests sheets completed.
checkpoint | All Refuse removed from work area.
checkpoint | Photos to be taken of critical elements above as evidence of QA. (6)
section | Completion Inspections and Tests
checkpoint | Inspection by supervisor
checkpoint | Notice of Completion
signoff | Nominated Authority Sign off
checklist | 0006 Seismic Checklist |  |  |  | 0006 Seismic Checklist (V3)
section | Preliminary Inspections and Tests
checkpoint | RDM & Consent Approval
signoff | Nominated Authority Sign off
checkpoint | Define LOT Area
checkpoint | Understanding of the Scope of works
checkpoint | Site inspection and SWMS
section | Seismic
checkpoint | Pre-start meeting
checkpoint | Site Inspection, JRA .
checkpoint | Drawings referenced in Reference Documentation.
checkpoint | Layout drawing confirmed as current.
checkpoint | Installation as per Referenced Drawings.
checkpoint | Ensure seismic supports and bracing installed as per NZS 4219:2009.
checkpoint | Installation on cable trays only if below 400 mm from ceiling.
checkpoint | Photos to be taken of critical elements above as evidence of QA.
section | Completion Inspections and Tests
checkpoint | Inspection by supervisor
checkpoint | Notice of Completion
signoff | Nominated Authority Sign off
checklist | 0008 Underground Submains |  |  |  | 0008 Underground Submains (V3)
section | Preliminary Inspections and Tests
checkpoint | RDM & Consent Approval
signoff | Nominated Authority Sign off
checkpoint | Define LOT Area
checkpoint | Understanding of the Scope of works
checkpoint | Trench Inspection
checkpoint | Drum Delivery Test Certificate
signoff | Nominated Authority Sign off
checkpoint | Site inspection and SWMS
checkpoint | Trench inspection
checkpoint | Cables for Route installed in trench
checkpoint | Install cables into buildings and contain to prevent damage
checkpoint | MAG Slab installed
checkpoint | Test cables installed when installed in trench and building containment
section | Underground Submains
checkpoint | Pre-start meeting
checkpoint | Site Inspection, JRA .
checkpoint | Drawings referenced in Reference Documentation
checkpoint | Drawing and Schedule confirmed as current.
checkpoint | Installed to AS/NZS 3000:2007 and AS/NZS 3008:2007.
checkpoint | CCT labelling completed.
checkpoint | McKay I&T Form 19A – Single Phase Power Cable Inspection and Test McKay I&T Form 19B-1 - Local DB Power Cable: Inspection and Test Pre-Livening McKay I&T Form 19D – Three Phase Power Cable Inspection and Test completed as required.
checkpoint | Seismic Loops installed as required.
checkpoint | All AS/NZS 3000:2007 tests sheets completed as required.
signoff | Nominated Authority Sign off
checkpoint | All refuse removed from work area.
checkpoint | Photos to be taken of critical elements above as evidence of QA.
section | Completion Inspections and Tests
checkpoint | Inspection by supervisor
checkpoint | Notice of Completion
signoff | Nominated Authority Sign off
checklist | 0004 Lighting Install |  |  |  | 0004 Lighting Install (V3.1)
section | Lighting Install
checkpoint | Drawings referenced. (3)
checkpoint | The LOT is not defined by an area/zone, it is defined by the lights listed in the ITP Summary Report. (2)
checkpoint | Installed as per AS/NZS 3000:2007. (6)
checkpoint | As required: Seismic Restraints installed. (6)
checkpoint | Photos to be taken of critical elements above as evidence of QA. (6)
section | Completion Inspections and Tests
checkpoint | Notice of Completion (8)
signoff | Nominated Authority Sign off
checklist | 0001 In Slab Conduit |  |  |  | 0001 In Slab Conduit (V3)
section | In Slab Conduit Install
checkpoint | Drawings referenced. (3)
checkpoint | Define LOT Area. (2)
checkpoint | Ensure at least 50mm thick continuous poured concrete above conduit (ASNZS 3000:2007). (6)
checkpoint | Each length of duct is to be fully inserted into the next and glued. (6)
checkpoint | Space conduit/duct at a minimum of twice the diameter apart of conduit/duct used horizontally (32mm=64mm Etc), as far as construction allows. (6)
checkpoint | Entry and exit of ducts are at the correct location as per set out. (6)
checkpoint | Ensure conduits/ducts are securely fixed and cable tied to the reo bottom mat parallel, but not hard up, to reo. (6)
checkpoint | Extend duct to a minimum of 300mm past FFL. (6)
checkpoint | Push snake through fully completed duct installation, and pull through draw wire (string). (6)
checkpoint | Seal off open ends of ducts with tape. (6)
checkpoint | Photos to be taken of critical elements above as evidence of QA. (6)
section | Completion Inspections and Tests
checkpoint | Notice of Completion
signoff | Nominated Authority Sign off