## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned | 3ca51c3b-264b-4ef4-b4be-e90173ab7762 |  | checklist | 0012 Street Pole Foundation and Erection |  |  |  |  | Yes | 0012 Streetlight | 3086f25c-de28-4030-8c1c-8840eba17993
checkpoint-group | 2090193f-4b35-4ef2-bde0-2af4816b4631 |  | section | Street Light Foundation & Erection
checkpoint-status | e4d3819e-ff51-4328-9550-ca3d55fe7333 |  | checkpoint | Drawings referenced. (3)
checkpoint-status | 96342f21-1373-43c8-bcb1-864ab2125ab3 |  | checkpoint | The LOT is not defined by an area/zone, it is defined by the Lights listed in the Summary Report. (2)
checkpoint-status | 46a3afd2-76b7-4f5f-9251-1f645883c70d |  | checkpoint | Excavation completed. (6)
checkpoint-status | 8186337d-2696-4724-a7e9-cf4cb7b6d224 |  | checkpoint | Foundation Installed. (6)
checkpoint-status | f1389254-bdd0-4864-9289-fada4c51ad3d |  | checkpoint | Completed 20040-5 SK01 Foundation Inspection and signed off by qualified person. (6)
checkpoint-status | a19515b6-4364-44ad-b3d8-70d264a1aa70 |  | checkpoint | Pole Installation and equipment (Luminaire, Fusing and Earthing) as per AS/NZS 3000:2007. (6)
checkpoint-status | a663e626-28f1-4b98-84b6-384d13b93e03 |  | checkpoint | Grouting completed within 7 days of installing the pole as per Specification references 26. (6)
checkpoint-status | afcb9c04-ce62-4de6-9428-ca4b045a01b9 |  | checkpoint | Photos to be taken of critical elements above as evidence of QA.
checkpoint-group | ab431783-6412-4b5b-bee1-bc8045d5ebdc |  | section | Completion Inspections and Tests
checkpoint-status | 07fa9cf5-20e1-47ce-b90b-d50bf5df166a |  | checkpoint | Notice of Completion
holdpoint | 2ef9f62d-60c9-48e7-93ec-1607c12bd1dc |  | signoff | Nominated Authority Sign off
checklist-sectioned |  |  | checklist | 0011 GPO/Electrical Equipment |  |  |  |  | Yes | 0011 GPO/Electrical Equipment (V2) | 32c98170-f4a3-43e8-b074-d6f3d44b5bca
checkpoint-group |  |  | section | GPO & Electrical Install
checkpoint-status |  |  | checkpoint | Drawings referenced. (3)
checkpoint-status |  |  | checkpoint | The LOT is not defined by an area/zone, it is defined by the equipment listed in the Summary Report. (2)
checkpoint-status |  |  | checkpoint | Installed as per AS/NZS 3000:2007. (6)
checkpoint-status |  |  | checkpoint | Photos to be taken of critical elements above as evidence of QA. (6)
checkpoint-group |  |  | section | Completion Inspections and Tests
checkpoint-status |  |  | checkpoint | Notice of Completion
holdpoint |  |  | signoff | Nominated Authority Sign off
checklist-sectioned | 60014fdf-9105-47f9-8304-e559d99d15d5 |  | checklist | 0005 Earthing/Bonding |  |  |  |  | Yes | 0005 Earthing/Bonding (V3) | 451d6c59-bd33-472b-a2ec-c41d98d424b7
checkpoint-group | 710eb025-8e2e-4dd0-b2cb-0d2d44552c13 |  | section | Earthing & Bonding
checkpoint-status | 8498f83a-5837-49a5-bc3d-0f91623f1e16 |  | checkpoint | Drawings referenced. (3)
checkpoint-status | d0970ce9-05b0-46c6-a499-c183ac42ea11 |  | checkpoint | Define LOT Area. (2)
checkpoint-status | 63efb68d-a5ab-47e6-b4d8-d1f3e37dfc90 |  | checkpoint | Weld copper wire to steel pile as specified on pile plan. (6)
checkpoint-status | fad2afa9-2f03-4bbf-be5b-3e81bed0146e |  | checkpoint | Feed and cable tie copper earth wire to correct point. (6)
checkpoint-status | 0d278f1f-2631-4a52-b2d4-bdddf461436a |  | checkpoint | All Earth, Bonding and Equipotential Bonding to AS/NZS 3000:2007. (6)
checkpoint-status | 74708096-e048-4188-823c-2f40c207d668 |  | checkpoint | Complete McKay I&T Form 20 - Earthing Resistance Test sheet. (6)
checkpoint-status | bee5838b-03d2-4dac-b41d-5a32edec81c5 |  | checkpoint | Photos to be taken of critical elements above as evidence of QA. (6)
checkpoint-group | 96a5e48b-6f82-4cb0-9471-a0aabf0ee3d8 |  | section | Completion Inspections and Tests
checkpoint-status | 14181720-77cb-4063-b049-b19079cef6a7 |  | checkpoint | Notice of Completion. (8)
holdpoint | c4629d0f-2991-458e-ab10-c03759e13530 |  | signoff | Nominated Authority Sign off
checklist-sectioned | 585cb687-44ae-477b-85cd-c929edc7b665 |  | checklist | 0003 Containment |  |  |  |  | Yes | 0003 Containment (V4.2) | 5865c30e-67ee-4224-9ace-e89df108cc02
checkpoint-group | 19342d71-7cd2-4b92-96f9-8b8c2627ea7d |  | section | Containment
checkpoint-status | 3923872d-832e-4067-a5ce-24425f26e29c |  | checkpoint | Drawings referenced. (3)
checkpoint-status | 1bc929c3-b388-46f8-8478-01e4fc8759cf |  | checkpoint | Define LOT Area. (2)
checkpoint-status | b33f867b-8380-4720-8418-f56b09a1e7e4 |  | checkpoint | Ensure cable ladders and trays are provided to support cable. (6)
checkpoint-status | 0b7eec3d-9a4a-487a-9f29-201da09a7921 |  | checkpoint | Ensure cable ladders and trays have enough support, and 50% spare capacity. (50% spare capacity as per original design.) (6)
checkpoint-status | 64f21cfa-beaf-46e6-9d4f-c6f114d57f58 |  | checkpoint | Ensure cable ladder and tray is installed to manufacturer’s instructions, complete with all necessary splice plates, bends, and fixings. (6)
checkpoint-status | 04292fd4-ae7e-46d9-ab9b-6e8d8dfc1310 |  | checkpoint | Ensure adequate access for replacing, inspecting, or adding cable. (as at time of install.) (6)
checkpoint-status | 6bf38176-5e31-4a98-acab-eba56462a34d |  | checkpoint | Ensure seismic supports and bracing installed according to KCL design.) (7)
checkpoint-status | 13035bf5-dac2-40a8-ab6f-dcbeb400e6b5 |  | checkpoint | Photos to be taken of critical elements above as evidence of QA. (6)
checkpoint-group | 1eff88ca-eb7d-46ce-a10a-d4d3afa5cf04 |  | section | Completion Inspections and Tests
checkpoint-status | b32e14da-245b-4805-8efb-87553d3e2762 |  | checkpoint | Notice of Completion. (9)
holdpoint | b53030b2-4e5e-4477-bc0e-79f0e4512b0b |  | signoff | Nominated Authority Sign off
checklist-sectioned | 30da7a31-b19e-4630-b627-4fa79d4d3365 |  | checklist | 0002 Cable Installation |  |  |  |  | Yes | 0002 Cable Installation (V3.1) | 704efd8d-80cc-4063-959e-4b8966ff98eb
checkpoint-group | 75c0a5a5-a7b2-4117-9eaf-2874a2577a79 |  | section | Cable Installation
checkpoint-status | 066e46ea-2534-4dc9-bb34-8cdb2ff4ffff |  | checkpoint | Drawings referenced. (3)
checkpoint-status | 75a8e19a-c14c-417a-bc53-a71f5d0adbcd |  | checkpoint | The LOT is not defined by an area/zone, it is defined by the cables listed in the Summary Report. (2)
checkpoint-status | 7a5d3467-3e37-4634-8253-22eb73b02334 |  | checkpoint | Provide logical cable management and reticulation system coordinated with other trades. (6)
checkpoint-status | dc675be1-0345-4601-a520-59e6ff97c947 |  | checkpoint | All cable routes rationalised where possible. (6)
checkpoint-status | 31b42514-37c0-4b83-b588-6d2e3f79787e |  | checkpoint | Maintain Minimum Separation Distances as per 22.2.3. (6)
checkpoint-status | db18d5ef-8fda-414e-9c25-dc59932a476e |  | checkpoint | Catenary Installed. 6 cables/cat wire max. No excessive sag. Cable tied regularly. (6)
checkpoint-status | 60bd696c-3539-4af4-9c29-9d1257ee5c69 |  | checkpoint | Conduit installed. 22.5.2-fix conduit saddles at a maximum of 1m intervals in horizontal runs and 2m intervals in vertical runs. (6)
checkpoint-status | 4c8fa3dd-4ebf-4be3-aff9-26e35852e967 |  | checkpoint | 22.2.8-Fixing with nylon ties to slab or roof structure at max intervals of 1500mm (for 1/2 cables only). (6)
checkpoint-status | 4aaac39e-eae9-4d10-a24f-dadb7c4e5613 |  | checkpoint | All wiring systems adequately protected as per 22.2.4 (6)
checkpoint-status | 307778f8-621a-4517-baea-01db54fa822a |  | checkpoint | All cables and supports concealed as per 22.2.6 (6)
checkpoint-status | 99b784f5-2cee-4030-8a46-e3670b2d804a |  | checkpoint | Cables installed as per manufacturer’s instructions. (6)
checkpoint-status | 9f2532d5-b61b-41c8-ad87-c35531a4d61b |  | checkpoint | As required: Acoustic sealing completed for the cables included in the ITP. (6)
checkpoint-status | 96e77b73-1e25-40e5-a4e9-c313853e3589 |  | checkpoint | Written approval obtained where cables/conduits must be run surface mounted as per 22.2.7 & 22.6.1. (6)
checkpoint-status | cf6cfcee-bbe0-4858-8d36-cd16cca1f3a4 |  | checkpoint | Photos to be taken of critical elements above as evidence of QA. (6)
checkpoint-group | 3e811288-36c6-43db-833f-bf546f40770f |  | section | Completion Inspections and Tests
checkpoint-status | a1e0c054-98dc-438f-9436-70041ec34eae |  | checkpoint | Notice of Completion (8)
holdpoint | d38c5410-babb-47bd-938b-5bc04b4e5e94 |  | signoff | Nominated Authority Sign off
checklist-sectioned | 07ee10a2-5484-426a-932d-48bdbbc17063 |  | checklist | 0009 Cables and Conduit Underground (V2) |  |  |  |  | Yes | 0009 Cables and Conduit Underground | a0c315e8-a9fb-4a4a-b8a5-6dddfcb54018
checkpoint-group | a798ea2d-8932-4c0a-8e84-85b408732697 |  | section | Preliminary Inspections and Tests
checkpoint-status | 9c6125c3-34f8-44ec-9bd8-53bbbadf6c38 |  | checkpoint | RDM & Consent Approval
holdpoint | d7b88643-81b2-4d11-a14d-83e37519131c |  | signoff | Nominated Authority Sign off
checkpoint-status | b97d6788-31ca-4355-89ba-9aa1f6fc6331 |  | checkpoint | Define LOT Area
checkpoint-status | 676b9552-060e-4628-80c7-dfcbf165ec74 |  | checkpoint | Understanding of the Scope of works
checkpoint-status | 25d30646-65ff-4143-8e78-fa9d64750314 |  | checkpoint | Ensure materials available
checkpoint-status | 3bb49a59-d61c-4611-8427-6a8ec31b7b5a |  | checkpoint | Site inspection and SWMS
checkpoint-group | a6f01adb-d43f-4c71-924d-b0ff99016c36 |  | section | Conduit & Cable Works
checkpoint-status | cfdf60fd-34d3-4e4c-975c-7b484a61f2ca |  | checkpoint | Pre-start meeting
checkpoint-status | d9e0ff5a-344e-4f7f-8288-8c5d22117df6 |  | checkpoint | Site Inspection, JRA .
checkpoint-status | c76a8aaf-2b65-4469-be96-c271b695e30d |  | checkpoint | Ensure HD conduits are used
checkpoint-status | db5bb278-7536-4ed7-98c4-67fffe1b409b |  | checkpoint | Each length of duct is to be fully inserted into the next and glued
checkpoint-status | 1258fb54-133b-444b-8838-a358a40b8be2 |  | checkpoint | Ensure separation of Low Voltage cables from Telecommunication cables is as AS/NZ 3000 2007
checkpoint-status | c4346834-5150-470e-a63f-e2831e1d910c |  | checkpoint | Entry and exit of ducts are at the correct location as per set out
checkpoint-status | 67de3896-1425-40ba-a9ac-ff7b15e8aba6 |  | checkpoint | Conduits installed
checkpoint-status | c65fc3fa-02bd-4d32-b709-d38c42a53e70 |  | checkpoint | Cable installed
checkpoint-status | 71f10e17-a4e7-4136-bc8f-8c5cdbf129a9 |  | checkpoint | Push snake through fully completed duct install and pull through draw wire (string)
checkpoint-status | c0316206-1592-4bb9-a573-25baa60d397d |  | checkpoint | Seal off open ends of ducts with tape
checkpoint-status | e69cd797-7376-4337-8f47-0a180f5c0b2e |  | checkpoint | Photos to be taken of critical elements above as evidence of QA
checkpoint-group | 556e73a1-6e7f-4fb4-b694-13c19e6ff25c |  | section | Completion Inspections and Tests
checkpoint-status | 6363b694-0769-40b6-9fd6-9c09d9a5b04a |  | checkpoint | Inspection by supervisor
checkpoint-status | 65372bfe-fc32-41eb-9068-3ae1cb81d1d5 |  | checkpoint | Notice of Completion
holdpoint | 227bc081-36c0-4429-ab9c-760ba44ba5b2 |  | signoff | Nominated Authority Sign off
checklist-sectioned | cc1f0cf6-f293-4911-a271-c373efa54d40 |  | checklist | 0007 Switchboards |  |  |  |  | Yes | 0007 Switchboards (V2) | a1ca54e5-57b9-4c4e-8a4b-a43d6436b56e
checkpoint-group | 529599f5-5c72-45c9-91fa-ba31b9691ff1 |  | section | Switchboard Installation
checkpoint-status | a775104c-4d4b-474f-aeb7-285ba601b0d6 |  | checkpoint | Drawings referenced. (3)
checkpoint-status | 9a9c1961-fd05-4a4b-8237-b09a25ca34de |  | checkpoint | The LOT is not defined by an area/zone, it is defined by the cables listed in the Summary Report. (2)
checkpoint-status | 3d811f74-542c-42a1-bb14-9d84ded8dfd9 |  | checkpoint | FAT (Factory Acceptance Test). (6)
checkpoint-status | 79b6ff14-b789-467c-820c-6189ee99d22e |  | checkpoint | Arrived and checked. (6)
checkpoint-status | 93114088-1f9c-4cee-9e20-3caa02f66c33 |  | checkpoint | Installed as per AS/NZS 3000:2007. (6)
checkpoint-status | cd6b42bc-688a-4858-8eee-d2b003df1e07 |  | checkpoint | Position confirmed. (4)
checkpoint-status | efdc3469-2c28-4357-ba2b-100fe3307447 |  | checkpoint | Terminations checked. (6)
checkpoint-status | 75f2883f-599c-4190-9926-97c147cf7e8a |  | checkpoint | CCT labelling completed. (6)
checkpoint-status | 8bbd78cc-48fc-469e-bd0b-4b4c0a89a299 |  | checkpoint | All Cable glands compressed. (6)
checkpoint-status | dc3d8dd3-09f9-45c4-bf7a-4358c3f1adda |  | checkpoint | Seismic Restraints installed as required. (7)
checkpoint-status | 188d2aa8-802e-4fc8-b159-4459fec4bf6f |  | checkpoint | Incoming submain terminated and photographed. (6)
checkpoint-status | 91d941d9-6e95-4a39-aae5-37e6da4665c0 |  | checkpoint | Complete McKay Test Forms as required: (6) McKay I&T Form 0 - Visual Inspection McKay I&T Form 19B-1 - Local DB Power Cable: Inspection and Test McKay I&T Form 20 - Earthing Resistance Test Sheet McKay I&T Form 19B-2 - Local DB Power Cable: Inspection and Test – Live : To Be Completed once the Pre-livening tests and inspections are complete, and will be submitted with Commissioning Results.
checkpoint-status | 9f7fa06e-8391-40e5-a7ae-396bad3e3bca |  | checkpoint | Photos to be taken of critical elements above as evidence of QA. (6)
checkpoint-group | 6657ebe8-6f1e-4182-b782-87952070feb7 |  | section | Completion Inspections and Tests
checkpoint-status | ff54724f-68ed-4bd1-aa7e-4b0b887c72be |  | checkpoint | Notice of Completion
holdpoint | 9483e170-9d2c-47c0-b88e-6ad5d1f2c4ac |  | signoff | Nominated Authority Sign off
checklist-sectioned | c76a2e7e-816f-4845-b264-e5a98706683d |  | checklist | 0006 Seismic Checklist |  |  |  |  | Yes | 0006 Seismic Checklist (V3) | baaee9c6-e859-4b35-8b16-a53716148d54
checkpoint-group | d8f673cf-0d17-46ef-9ae1-a72d382fb493 |  | section | Preliminary Inspections and Tests
checkpoint-status | 561fe346-3d01-4be5-aab1-3c55ad154f4a |  | checkpoint | RDM & Consent Approval
holdpoint | 4c1b37a6-b408-411d-a9b8-f469d72dad73 |  | signoff | Nominated Authority Sign off
checkpoint-status | c69e4ba6-dc8e-4fbf-bed4-1b7350e1fc9c |  | checkpoint | Define LOT Area
checkpoint-status | ec1e6a87-b224-46a3-aa79-abb97359dca7 |  | checkpoint | Understanding of the Scope of works
checkpoint-status | 86f96877-cfe2-4ffb-979a-1f31d9edb52c |  | checkpoint | Site inspection and SWMS
checkpoint-group | 6aec6bd6-61ae-498b-a117-9a0203c1648a |  | section | Seismic
checkpoint-status | b2bf2f66-c022-42d8-b68a-47a33de6c3f2 |  | checkpoint | Pre-start meeting
checkpoint-status | 4a89086b-b953-44b6-804f-f1e23446bedb |  | checkpoint | Site Inspection, JRA .
checkpoint-status | c4de7717-951d-4070-9117-17f8bc9fc677 |  | checkpoint | Drawings referenced in Reference Documentation.
checkpoint-status | a273149d-fcc9-467b-8dc3-5f1321afc434 |  | checkpoint | Layout drawing confirmed as current.
checkpoint-status | ad10982e-562c-4875-9fb7-47a5a726c923 |  | checkpoint | Installation as per Referenced Drawings.
checkpoint-status | af2709d1-a328-452f-817c-f4b77b74073b |  | checkpoint | Ensure seismic supports and bracing installed as per NZS 4219:2009.
checkpoint-status | 21d6bef6-109a-477b-9a4c-5b90e34e9085 |  | checkpoint | Installation on cable trays only if below 400 mm from ceiling.
checkpoint-status | f5d2b80b-c513-49f0-a263-decfd10cc4c4 |  | checkpoint | Photos to be taken of critical elements above as evidence of QA.
checkpoint-group | c1617767-2f2f-4272-84d0-0eff21e7bb6e |  | section | Completion Inspections and Tests
checkpoint-status | 90461d4c-330b-41d5-8bcf-f26f4956b516 |  | checkpoint | Inspection by supervisor
checkpoint-status | 5f450d77-29cb-4e98-a781-f5c626acbd2a |  | checkpoint | Notice of Completion
holdpoint | 0328ad76-4f66-4628-acd2-7dde695a7551 |  | signoff | Nominated Authority Sign off
checklist-sectioned | f0514c59-2b88-4739-b8b8-9dc2a2e21cd6 |  | checklist | 0008 Underground Submains |  |  |  |  | Yes | 0008 Underground Submains (V3) | bc8f2f76-d631-491e-aa9d-f8761208c34f
checkpoint-group | 3c01f27a-1114-4e82-9072-85259a17e918 |  | section | Preliminary Inspections and Tests
checkpoint-status | 0b895769-122c-42b3-b868-494c91a8a1ea |  | checkpoint | RDM & Consent Approval
holdpoint | 00260159-8bb0-4270-ba4d-3ad255983b55 |  | signoff | Nominated Authority Sign off
checkpoint-status | 616597d4-2f46-4c4d-8219-74366473c5f5 |  | checkpoint | Define LOT Area
checkpoint-status | 6e6a867b-faa3-44f7-8e51-bb81ade026ec |  | checkpoint | Understanding of the Scope of works
checkpoint-status | bbc9cdac-8c11-45fc-bba6-6c9a57b81ae3 |  | checkpoint | Trench Inspection
checkpoint-status | 6736cdcf-e443-43a1-8632-94438dd98f11 |  | checkpoint | Drum Delivery Test Certificate
holdpoint | c43c72d0-5217-4e2b-bb50-84dde8acb09c |  | signoff | Nominated Authority Sign off
checkpoint-status | 7b1e228f-6bf6-4395-b5ed-9a92408b19f0 |  | checkpoint | Site inspection and SWMS
checkpoint-status | 5cd89973-cbe3-4cef-af70-a4e5f67ca0d3 |  | checkpoint | Trench inspection
checkpoint-status | c58701d4-ead9-4d32-ac56-4693852a7e4e |  | checkpoint | Cables for Route installed in trench
checkpoint-status | 4bd264ac-4a44-4351-bb57-80a35d93902c |  | checkpoint | Install cables into buildings and contain to prevent damage
checkpoint-status | f1d6f193-25b7-4fff-b331-682454483963 |  | checkpoint | MAG Slab installed
checkpoint-status | ceefe5ce-828d-4ade-bc6c-7aec1acb3cbe |  | checkpoint | Test cables installed when installed in trench and building containment
checkpoint-group | bbb2c1bb-2887-478b-a7a9-becd3824fdde |  | section | Underground Submains
checkpoint-status | 2712202c-e4e5-4954-8bcc-d5638d5a8ce4 |  | checkpoint | Pre-start meeting
checkpoint-status | 0face4b8-bce4-4f45-af63-bb6eb5aa7503 |  | checkpoint | Site Inspection, JRA .
checkpoint-status | 3d87bf35-455b-41c0-83d8-d872bd5e66ba |  | checkpoint | Drawings referenced in Reference Documentation
checkpoint-status | 72824c5b-2da6-49b0-87b6-af177ac60395 |  | checkpoint | Drawing and Schedule confirmed as current.
checkpoint-status | 829a8cdf-2b4d-43c7-a7e0-6e9eb41cc501 |  | checkpoint | Installed to AS/NZS 3000:2007 and AS/NZS 3008:2007.
checkpoint-status | d6a087c3-0471-4946-90ef-5790aba3c89c |  | checkpoint | CCT labelling completed.
checkpoint-status | 37380ff3-df66-4809-a959-e4c5d66308b1 |  | checkpoint | McKay I&T Form 19A – Single Phase Power Cable Inspection and Test McKay I&T Form 19B-1 - Local DB Power Cable: Inspection and Test Pre-Livening McKay I&T Form 19D – Three Phase Power Cable Inspection and Test completed as required.
checkpoint-status | b5a57db1-1c5a-4c6b-befc-dee65c36f709 |  | checkpoint | Seismic Loops installed as required.
checkpoint-status | adb1e6ac-6c54-46f4-a5b0-9fe95e24e94f |  | checkpoint | All AS/NZS 3000:2007 tests sheets completed as required.
holdpoint | 4ca482eb-468a-4414-9f1a-b6939940a254 |  | signoff | Nominated Authority Sign off
checkpoint-status | 219496bf-bbbc-482e-9892-3898401de745 |  | checkpoint | All refuse removed from work area.
checkpoint-status | a0d97cf8-29bf-4f5e-9549-2b10141cf78b |  | checkpoint | Photos to be taken of critical elements above as evidence of QA.
checkpoint-group | d78e78b6-b126-4ea5-954a-30f0081e98c6 |  | section | Completion Inspections and Tests
checkpoint-status | 884362d6-36f2-4ddc-a50b-fadaa922a8a6 |  | checkpoint | Inspection by supervisor
checkpoint-status | b032ddf6-e0d1-4c8e-a051-e836bdb45b4b |  | checkpoint | Notice of Completion
holdpoint | 15db91a5-70bf-4791-8448-a686ec5e5b13 |  | signoff | Nominated Authority Sign off
checklist-sectioned | 4cd17713-8a4f-4823-abd6-10088cca2f07 |  | checklist | 0004 Lighting Install |  |  |  |  | Yes | 0004 Lighting Install (V3.1) | dc8c0825-3668-4e8b-a525-111a8425b7e8
checkpoint-group | 4e98e3be-0927-4132-a079-5dbbbc7149a0 |  | section | Lighting Install
checkpoint-status | 1abf3824-a12b-4078-b4ad-8ed639bc3c9d |  | checkpoint | Drawings referenced. (3)
checkpoint-status | 6bff9fe0-1ad0-4dae-9a43-00c9d666511c |  | checkpoint | The LOT is not defined by an area/zone, it is defined by the lights listed in the ITP Summary Report. (2)
checkpoint-status | aaef0859-841c-49bb-8760-215ecd6388d9 |  | checkpoint | Installed as per AS/NZS 3000:2007. (6)
checkpoint-status | 50e652a5-1646-4f54-88c3-1ef04266934e |  | checkpoint | As required: Seismic Restraints installed. (6)
checkpoint-status | 90e7ae7c-e91a-4723-bd2d-4996ce959860 |  | checkpoint | Photos to be taken of critical elements above as evidence of QA. (6)
checkpoint-group | 446ead77-cf44-433f-a493-b92df949fe7a |  | section | Completion Inspections and Tests
checkpoint-status | 41db3ef5-6824-425c-a32b-817da147c672 |  | checkpoint | Notice of Completion (8)
holdpoint | 24290d78-9547-45b8-81ae-6ef25c3fdeea |  | signoff | Nominated Authority Sign off
checklist-sectioned |  |  | checklist | 0001 In Slab Conduit |  |  |  |  | Yes | 0001 In Slab Conduit (V3) | fe6e2f69-cbfd-497b-ba4d-3055bbb30946
checkpoint-group |  |  | section | In Slab Conduit Install
checkpoint-status |  |  | checkpoint | Drawings referenced. (3)
checkpoint-status |  |  | checkpoint | Define LOT Area. (2)
checkpoint-status |  |  | checkpoint | Ensure at least 50mm thick continuous poured concrete above conduit (ASNZS 3000:2007). (6)
checkpoint-status |  |  | checkpoint | Each length of duct is to be fully inserted into the next and glued. (6)
checkpoint-status |  |  | checkpoint | Space conduit/duct at a minimum of twice the diameter apart of conduit/duct used horizontally (32mm=64mm Etc), as far as construction allows. (6)
checkpoint-status |  |  | checkpoint | Entry and exit of ducts are at the correct location as per set out. (6)
checkpoint-status |  |  | checkpoint | Ensure conduits/ducts are securely fixed and cable tied to the reo bottom mat parallel, but not hard up, to reo. (6)
checkpoint-status |  |  | checkpoint | Extend duct to a minimum of 300mm past FFL. (6)
checkpoint-status |  |  | checkpoint | Push snake through fully completed duct installation, and pull through draw wire (string). (6)
checkpoint-status |  |  | checkpoint | Seal off open ends of ducts with tape. (6)
checkpoint-status |  |  | checkpoint | Photos to be taken of critical elements above as evidence of QA. (6)
checkpoint-group |  |  | section | Completion Inspections and Tests
checkpoint-status |  |  | checkpoint | Notice of Completion
holdpoint |  |  | signoff | Nominated Authority Sign off