## Piling Overarching
Piling Overarching Inspection and Test Plan
Project: Arnold Dam
Number and Revision: DS2672-ITP-S104 - Rev 1
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
3.01 | Site Requirements
3.01.01 | Construction Pack | Submit a Construction Pack including a Methodology and JESA to the Engineer before works | Downer | Construction Pack | Submit Prior to commencement of works | H | PE
3.01.02 | Survey Setout | Survey Set out as per contract drawings and specification, capturing pre-construction levels where needed. | Downer | Survey Records | Prior to Works | H | SV
3.01.03 | Service Location | Complete the Excavation permit process to identify, locate and protect all services. | Downer | Excavation Permit | Prior to Excavation | H | SE
3.01.04 | Internal Permits | Complete internal Permits as required to complete works including but not limited to: Hot works, concrete saw, lift, confined space, working at height etc. | Downer | Internal Permits | Prior to Excavation | H | SE
3.01.05 | External Permits | Obtain External Permits as required to complete works including but not limited to: Close approach, Worksafe Notice etc. | Downer | External Permits | Prior to Excavation | H | PE
3.01.06 | Approved Construction Drawings | Prior to starting works, Ensure that the construction drawings are both IFC and the Current Version. | Downer | IFC Drawings | Prior to works start | H | PE
SECTION 7 – CONSTRUCTION ACTIVITY – PILING
7.01 | Piling General
7.01.01 | Method Statements | A detailed method statement shall be prepared by the Constructor for the Designer’s review for each piling operation undertaken on the site. | 51/33669 - 3.2, 4 | Method Statement | 3 weeks prior to the commencement of each piling operation | HP | ENG
7.01.02 | Piling Change | When a change is made to the piling crew, excavation method or other change (e.g. variations in ground conditions) that could influence the quality of the works, the Designer may adjust the inspection requirement and frequency to suit the revised risk profile of the works. | 51/33669 - 6.3.2 | Notice | When a change is made | W | ENG
7.01.03 | Jointing of permanent casing Inspection | Designer inspection of jointing of permanent casings for the first pile at every structure with the Opportunity to inspect (at random for subsequent piles at the same structure) | 51/33669 - 9.4 | Hold Point Release | First pile at every structure | HP | ENG
SECTION 10 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
10.01 | Site Post Construction Activities
10.01.01 | Construction Record Compilation | Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted. | Downer | Records | Post construction | H | SE
10.01.02 | Survey Records | Ensure all items have been surveyed and records are assembled for asbuilting | Downer P&G 20.1 | Records | Post construction | H | SV
10.01.03 | Redline Drawings | Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen. Red-pen mark-up copies of the Drawings and Specifications and other design documentation showing any deviations from the specified details and requirements produced in accordance with industry good practice. | Downer P&G 20.1 | Redlines | Post construction | H | PE
10.01.04 | Defect, Snag and Punch List | Update the project Defect, Snag and Punch List Register | Downer | Register | Post construction | H | PE

## Pile Construction Card
Pile Construction Card Inspection and Test Plan
Project: Arnold Dam
Number and Revision: DS2672-ITP-S105 - Rev 1
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 7 – CONSTRUCTION ACTIVITY – PILING
7.02 | Setout and Excavation - (Pile Construction Card)
7.02.01 | Pile Set Out | The position of all piles shall be accurately set out and checked by a suitably experienced surveyor prior to installation | 51/33669 - 3.7 | Survey Records: | Each Pile | D | SV
Location Co-Ordinate - X:
Location Co-Ordinate - Y:
Ground Surface Elevation - RL:
Expected Stratum Elevation - RL:
7.02.02 | Nature of Ground and Subsurface Conditions | The Constructor shall inform the Designer where circumstances indicate that ground and / or groundwater conditions differ from those presented in the reports, indicated on the Drawings or interpreted from proof bores. | 51/33669 - 3.5 | Notice | Ongoing | S | SE
7.02.03 | Pile Logging Inspection | The logging of selected piles shall also be undertaken by the Designer to agree with the Constructor in identifying the founding stratum. | 51/33669 - 6.2.2 | Site Log | Each Pour | W | ENG |  |  | Add First Pile Hold Points Checksheet and / or Selected Logging Hold Points Checksheet as required.
7.02.04 | Pile Logging | The Constructor shall keep an excavation log for each pile that records the types of materials encountered and the depths at which those materials were encountered and any groundwater levels and inflows inside the pile | 51/33669 - 6.2.2 | Site Log | Each Pour | I | SE
Casing Type - Permanent or Temporary:
Casing Finished elevation top (RL):
Casing Finished elevation bottom (RL):
Casing Depth (m):
Casing Thickness (mm):
Excavation Commencement - Date and Time:
Detail Materal Type and when it Chages - Type and Depth:
The Depth to the Founding Stratum (m)
Actual Stratum Elevation (RL):
Water Ingress - Depth (m) and Details:
Excavation Completion - Date and Time:
7.02.05 | Pile Dimensions | Constructed piles shall not deviate outside the tolerances, unless otherwise shown on the Drawings or as accepted by the Designer. | 51/33669 - 3.8.1 | Site Record | Each Pile | D | SV / SE
Actaul Diameter:
Actaul Length:
7.02.06 | Pile Pumping | Pumping from pile excavations are permitted provided the Constructor can demonstrate that the excavation has been sealed against further water entry (e.g. through sufficient keying into rock) or that the pile excavation is stable and will allow pumping to take place without ground disturbance below or around the pile. | 51/33669 - 6.2.1 | Site Record | Each Pour | I | SE
7.02.07 | Full Length of Pile | Unless shown otherwise on the Drawings, each pile shall be in intimate contact with the ground over its full length. | 51/33669 - 6.2.3 | Site Record | Each Pour | I | SE
7.02.08 | Pile Hole Side Cleaning | On completion of the pile excavation and immediately prior to installation of the reinforcement cage Loose and / or smeared material shall be removed from the sides of the rock socket | 51/33669 - 6.3.1 | Site Record | Prior to installation of the reinforcement cage | I | SE
7.02.09 | Pile Hole Base Cleaning | On completion of the pile excavation and immediately prior to installation of the reinforcement cage Loose, disturbed and / or softened materials and any sedimentation shall be removed from the pile base | 51/33669 - 6.3.1 | Site Record | Prior to installation of the reinforcement cage | I | SE
7.02.10 | Pile Hole Inspection and Acceptance | The reinforcement cage shall not be installed, nor concreting begin for any pile, until the as-built founding level of the pile, the condition of the rock socket (where relevant) and the condition of the pile base has been accepted by the Designer | 51/33669 - 6.3.2 | Hold Point Release | Each Pile | HP | ENG
7.03 | Permanent Casings - (Pile Construction Card)
7.03.01 | Pile Annulus | Permanent casings shall be installed in such a manner as to minimise any annulus between the outside of the casing and the in-situ ground. | 51/33669 - 6.1.1 | Site Records | Each Pile Post Installation | D | SE
7.03.02 | Installed Casing Profile | The installed casing profile shall be circular, with a deviation from the specified completed pile diameter of not greater than +5%, –0% of the pile diameter and with no distortions, dents, gouges or similar. | 51/33669 - 6.1.1 | Site Records | Each Pile Post Installation | D | SE
7.04 | Temporary Casings - (Pile Construction Card)
7.04.01 | Up-stand | As a minimum, an up-stand of temporary casing of at least 1 m above existing ground level shall be provided to prevent material falling into and contaminating the pile bore prior to and during excavation and concreting works. | 51/33669 - 6.1.2 | Site Records | Each Pile | S | SE
7.04.02 | Annulus Extra Concrete | Prior to the temporary casing being extracted, concrete shall be poured to the pile cut-off level plus the minimum over-cast allowance plus an allowance for the volume of annulus created by the extracted casing. | 51/33669 - 6.1.2 | Site Records | Prior to the temporary casing being extracted | I | SE
7.04.03 | Extraction Top-up Concrete | When the temporary casing is being extracted, a sufficient quantity of concrete shall be maintained within such that the pressure from external water or soil is exceeded and that the pile concrete is not reduced in section or contaminated. | 51/33669 - 6.1.2 | Site Records | Each Pour | S | SE
7.04.04 | Temporary casing Removal | The temporary casing shall be extracted whilst the concrete within the pile remains sufficiently workable such that the concrete is not lifted. The temporary casing shall be removed vertically without applying lateral force. The rate of extraction shall not exceed 1 m per 5 seconds. The time at which the temporary casing is extracted shall be recorded by the Constructor. | 51/33669 - 6.1.2 | Site Records | Each Casing | S | SE
7.04.05 | Permanent Temporary Casings | Temporary casings that are in contact with concrete and which are not withdrawn prior to the initial set of the concrete has taken place, shall be left in place and the Designer notified. | 51/33669 - 6.1.2 | Site Records | Each Occurrence | M | SE
7.05 | Concreting in Dry Conditions (Preferred) - (Pile Construction Card)
7.05.01 | Dry Hole Concrete Placement | Where a dry excavation can be maintained and the depth of water at the base of the pile at the commencement of concrete placement is less than 25 mm, concrete may be chuted into piles and allowed to free-fall to the pile base by no more than 5 m and without striking the pile reinforcement cage. | 51/33669 - 6.5.2 | Pile Construction Record Card | Each Dry Pile Pour | I | PE
7.05.02 | Groundwater Inflow Measurement | Unless clearly not significant, the rate of groundwater inflow shall be measured prior to placing concrete. Concrete shall be placed using under water concreting techniques, unless otherwise accepted by the Designer, when The rate of groundwater inflow compared to the rate of concrete placement is such that more than 5 litres of groundwater per cubic metre of concrete could be incorporated into the completed pile, or when The depth of water at the base of the pile at the commencement of concrete placement is more than 25 mm. | 51/33669 - 6.5.2 | Pile Construction Record Card | Each Dry Pile Pour | I | PE
7.06 | Concreting under water (Alternative) - (Pile Construction Card)
7.06.01 | Concreting Under Water - Timing | The time taken between placement of the reinforcement cage and commencement of concreting shall not exceed 4 hours. Reasonable efforts must be made to achieve this requirement. Where this requirement cannot be reasonably met, then the Designer shall re-check pile cleanliness and, if deemed necessary, the Constructor shall re-clean the pile immediately prior to concreting. | 51/33669 - 6.5.3 | Pile Construction Record Card | Each Wet Pile Pour | R | PE
7.06.02 | Concreting Under Water - Loss of Immersion of Discharge Pipe | When the immersion of the discharge pipe is lost during concreting (for example, to repair breakages or to remove a blockage), further placement of concrete shall not proceed unless The concrete into which fresh concrete is to be placed has maintained its workability, The discharge pipe is re-immersed sufficiently deep into the previously placed concrete, and No water or other contaminant is introduced into concrete that will remain below the final pile cut-off level. If these conditions cannot be met, concrete placement shall be suspended, the discharge pipe shall be removed and alternative measures shall be agreed with the Designer to form a sound pile. | 51/33669 - 6.5.3 | Pile Construction Record Card | When Required | R | PE
7.07 | Pile Concreting - (Pile Construction Card)
7.07.01 | Cleaning of the Excavated Pile Bore | Cleaning of the excavated pile bore, as specified in subsection 6.3.1 of this Specification, shall be completed immediately prior to the installation of the reinforcement cage. | 51/33669 - 6.4 | Site Record | Each Pile Prior to the Cage Installation | I | PE
7.07.02 | Cleanliness State of the Pile Excavation | The Constructor shall confirm, prior to the commencement of concreting, that the cleanliness state of the pile excavation has been maintained at the level required by this Specification and no circumstances have arisen that could change the condition at the base of the pile. | 51/33669 - 6.5.1 | Site Record | Each Pile Prior to the Commencement of Concreting | I | PE
7.07.03 | Loose and / or disturbed material during pour | No loose and / or disturbed material shall remain along the sides of the pile excavation nor lie at the pile base when concreting is started, nor be permitted to fall into the concrete as concreting proceeds. | 51/33669 - 6.3.1 | Site Record | Each Pile | I | SE
7.07.04 | Reinforcement Cage Cover | Pile reinforcement cages shall be located centrally within the pile excavation, such that final concrete cover to the extremities of the reinforcement cages is not less than 75 mm at any location. | 51/33669 - 3.8.2 | Site Record | Each Pile | D | SV / SE
7.07.05 | Pile Head casting Level | The heads of bored piles shall be over-cast by a minimum of 300 mm (concreting in dry conditions) / 1000 mm (concreting under water) above the cut-off levels. | 51/33669 - 3.8.3 | Site Record | Each Pile | D | SV / SE
7.07.06 | Concreting Timing | Concreting shall commence in a timely manner following installation of the reinforcement cage to minimise the potential for water ingress and/or collapse of the hole and/or sedimentation on the pile base, all of which could adversely affect the performance of the completed pile. Where it is suspected that these adverse conditions exist, the Designer shall re-check pile cleanliness and, if deemed necessary, the Constructor shall re-clean the pile immediately prior to concreting | 51/33669 - 6.5.1 | Site Record | Each Pile | W | ENG
7.07.07 | Pile Concrete Compaction | The concrete in the upper 2 m of the pile is to be thoroughly compacted using vibrators. | 51/33669 - 6.5.1 | Site Record | Each Pour | R | PE
7.07.08 | Piling Timing | The time period between commencement of pile excavation and completion of concreting shall not exceed 24 hours | 51/33669 - 6.2.1 | Site Record | Concreting shall not exceed 24 hours | S | SE
8.02 | Concrete Pour - (Pile Construction Card)
| General Details |  |  | Pre-Pour Checksheet
Pre Pour Date
Concrete Strength (mPa)
Volume (m3)
Mix Design
Additives
| Reinforcing has been checked and conforms to the drawings included: |  |  | Pre-Pour Checksheet
Bar Size & Grade, Lap Lengths, Lap Locations, Bar Supports, Bar Spacing, Cover
8.02.03 | Reinforcement Washdown | Washdown all steel reinforcement prior to pouring concrete to remove salts. | RSV - CS - 1.19 | Pre-Pour Checksheet | Prior to Pour | R | SE
8.02.04 | Pre-Pour Inspections | Pouring of any concrete must be inspected by the Engineer prior to further work being carried out in the area. | P&G 14 | Signed Pre-Pour | 48 Hours Notice Prior to Each Occurrence | HP | ENG
Pour Details
Pour Commencement Date and Time:
Weather
Water level in pile from top - Distance from top of casing (m)
Break in Continuity
Tremie pipe to elevation - Distance from top of casing (m)
Concrete top elevation - Distance from top of casing (m)
Actual concrete volume
Pour Completion Date and Time:
Casing removal - Date and Time:
8.02.05 | Delivery Dockets | The delivery docket of each batch delivered certifying the mix designation, cement type, specified strength, slump, date, mixing time, water added during batching and maximum aggregate size. | RSV - CS - 1.9 | Dockets | Each Pour | R | PE
8.02.06 | Slump Testing | Slump tests shall be taken for each delivery of concrete and the results recorded by the Contractor. | RSV - CS - 1.12 | Pre Pour | Each Pour | R | PE
8.02.07 | Compression Testing | A set of specimens for concrete tests shall consist of four specimens from each major pour of concrete, one of which shall be tested at 7 days and the remaining three at 28 days after casting. | RSV - CS - 1.12 | Test Results | Each Pour | R | PE
7.08 | Pile Post Pour - (Pile Construction Card)
7.08.01 | Pile Head Break Back | Pile heads shall be broken back to achieve A slightly convex profile so that the middle of the pile is nominally 25 mm above the average level at the perimeter of the pile and A Type B construction joint in accordance with standard NZS3109:1997. | 51/33669 - 3.8.3 | Pile Construction Record Card | Each Pile | I | SE
7.08.02 | Pipe Asbuilting | On completion of pile installation and prior to incorporating any piles into the permanent works, the actual pile locations and verticality shall be confirmed by a suitably experienced surveyor. | 51/33669 - 3.7 | Survey Records | 5 working days prior to incorporating any piles into the permanent works. | D | SV
7.08.03 | Bored Pile Construction Record Card | Pile construction records shall be submitted to the Designer within 24 hours of completion of any particular pile. Copies of the records shall be retained on site and made available for inspection by the Designer as required. | 51/33669 - 7 | Pile Construction Record Card | Within 24 hours of completion of any particular pile | W | ENG

## Piling First Pile Hold Points
Piling First Pile Hold Points Inspection and Test Plan
Project: Arnold Dam
Number and Revision: DS2672-ITP-S106 - Rev 1
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 7 – CONSTRUCTION ACTIVITY – PILING
7.07 | First Pile at Every Structure
7.07.01 | Inspection of any Reinforcement Cage Extension | Designer inspection of reinforcement cage extensions for the first pile at every structure with the Opportunity to inspect (at random for subsequent piles at the same structure). | 51/33669 - 9.4 | Reinforcement Cage Inspection Record | First pile at every structure with the Opportunity to inspect remainder | HP | ENG
7.07.02 | Inspection of Reinforcement Cages Prior to Installation | Designer inspection of the reinforcement cage for the first pile at every structure with the Opportunity to inspect (at random for subsequent piles at the same structure). | 51/33669 - 9.4 | Reinforcement Cage Inspection Record | First pile at every structure with the Opportunity to inspect remainder | HP | ENG
7.07.03 | Concreting of Piles | Designer inspection of concreting for the first pile at every structure with the Opportunity to inspect (at random for subsequent piles at the same structure). | 51/33669 - 9.4 | Pile Construction Record Card | First pile at every structure with the Opportunity to inspect remainder | HP | ENG
7.07.08 | Pile Head Initial Inspection | Designer inspection of the pile head prior to incorporation into the connecting structure for the first pile at every structure with the Opportunity to inspect (at random for subsequent piles at the same structure) | 51/33669 - 9.4 | Hold Point Release | First pile at every structure | HP | ENG

## Piling Logging Hold Points
Piling Logging Hold Points Inspection and Test Plan
Project: Arnold Dam
Number and Revision: DS2672-ITP-S107 - Rev 1
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 7 – CONSTRUCTION ACTIVITY – PILING
7.06 | Class 2 Pile Inspection Requirements
7.06.01 | Logging of Spoil Excavation | Class 2 – 25% of piles, First 2 No. piles constructed and then at random as advised by the Designer, Geological conditions match ground model and design assumptions. Designer to complete material logging for the first pile for all structures with the Opportunity to complete (at random) for subsequent piles. | 51/33669 - 6.3.2 | Pile Construction Record Card | First 2 No. piles constructed and then 25% at random as advised by the Designer | HP | ENG
7.06.02 | Shaft Cleanliness – Video | Class 2 – 10% of piles, First 3 No. piles constructed and then at random as advised by the Designer.[3], Clearly visible along the sides of the rock socket: The asperities or indentations created by the drilling process. Sand grains in the sandstone. No smear or loose debris. Designer to visually inspect the sides of the excavation in the rock socket zone | 51/33669 - 6.3.2 | Video | First 3 No. piles constructed and then 10% at random as advised by the Designer | HP | ENG
7.06.03 | Shaft Cleanliness – Visual | Class 2 – 25% of piles, First 2 No. piles constructed and then at random as advised by the Designer.[3], Clearly visible along the sides of the rock socket: The asperities or indentations created by the drilling process. Sand grains in the sandstone. No smear or loose debris. designer's acceptance of rock socket cleanliness (where visibility permits) | 51/33669 - 6.3.2 | Site Record | First 2 No. piles constructed and then 25% at random as advised by the Designer | HP | ENG
7.06.04 | Base Cleanliness | Class 2 – 25% of piles First 2 No. piles constructed and then at random as advised by the Designer Average base rating = 1 (for piles cast in dry conditions). Average base rating ≤ 3 (for piles cast under water, i.e. via tremie method). Designer’s acceptance of cleanliness at the base of the pile and confirmation of pile founding level | 51/33669 - 6.3.2 | Pile Construction Record Card | First 2 No. piles constructed and then 25% at random as advised by the Designer | HP | ENG

## Piling Materials
Piling Materials Inspection and Test Plan
Project: Arnold Dam
Number and Revision: DS2672-ITP-S108 - Rev 1
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 4 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
4.07 | Piling Materials
4.07.01 | Piling Supervisor | A suitably qualified and experienced person shall be nominated by the Constructor as the ‘Piling Supervisor’. | 51/33669 - 3.9 | Supervisor Approval | Prior to any piling works commencing. | W | ENG
4.07.02 | Pile Mix Design | The Designer shall be provided with the proposed concrete mix design for review, prior to any piling works commencing. | 51/33669 - 5.1 | Mix Design | Prior to any piling works commencing. | HP | ENG
4.07.03 | Spiral Reinforcement Welding | Spiral reinforcement shall not be lapped. Spiral reinforcement shall start and stop with 1.5 x pile cage circumference overlap and a single sided lap weld. Laps in longitudinal bars shall be made with D-clamps or similar means accepted by the Designer. Lapped joints shall achieve the full strength of the bar. | 51/33669 - 5.2 | TPI Report | Prior to Installation | HP | ENG
4.07.04 | Reinforcement Cage Fabrication Inspection | Designer inspection of reinforcement cage fabrication process for the first pile at every structure with the Opportunity to inspect (at random for subsequent piles at the same structure) | 51/33669 - 9.4 | Hold Point Release | First pile at every structure | HP | ENG
4.07.05 | Permanent Casings | The casing dimensions shall comply with the outside diameter, wall thickness and internal diameter as shown on the Drawings | 51/33669 - 6.1.1 | Mill Certs and Dimensions | Prior to Installation | R | PE
4.07.06 | Temporary Casings | the Constructor shall confirm that the properties of the casing are such that the bored piles are constructed to the dimensions, shape and depth. | 51/33669 - 6.1.2 | Dimensions | Prior to Installation | R | PE
4.07.07 | Bored Pile Construction Record Card Template | Supply a Template for the bored pile construction record card a minimum of 3 weeks prior to the commencement of any piling works. | 51/33669 - 9.1 | Construction Record Card Template | 3 weeks prior to the commencement of any piling | R | PE
4.08 | Concrete Materials
4.08.06 | Reinforcement | Reinforcing bars and mesh shall comply with AS/NZS4671:2001. | RSV - CS - 1.19 | Mill Certs | Prior to Installation | R | PE