## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | CS-4102 - Pressure Rebound Test | [5 empty] | CS-4102 - Pressure Rebound Test
section | DETAILS
checkpoint-no-status | Details
textbox | Contract:
textbox | Sub Work Area(s):
textbox | Sublot(s):
textbox | Work Area(s):
textbox | Lot(s):
date | Date:
checkpoint-no-status | Personnel Conducting Test
textbox | Drain Layer:
textbox | Site Engineer:
textbox | CPS Engineer
section | Pressure Testing Record Sheet For Pressure Pipelines
checkpoint | Pressure Testing Record Sheet For Pressure Pipelines
textbox | Pipe Material and Rating:
textbox | Test Length (m) L:
textbox | Pipe Internal Diameter (mm) D:
textbox | Depth of Pipe Below Water Table:
label | Attach Test Section Sketch (show heights, air valves, gauges and filling points)
textbox | Ambient Air Temperature: |  |  | °C
textbox | Water Temperature: |  |  | °C
section | Pressure Rebound Method
checkpoint | Standard Test Pressure
textbox | Pressure Applied: |  |  | kPa
checkpoint | Preliminary Phase
label | P60 > 70% STP
textbox | Acceptance:
checkpoint | Air Volume Assessment
label | 1. Reduce pressure by 10%-15% STP (ΔP)
label | 2. Measure water volume bled out (ΔV)
label | 3. Calculate ΔV max allowable
label | Where: 〖∆𝑉〗_max⁡𝑎𝑙𝑙𝑜𝑤𝑎𝑏𝑙𝑒 =1.2𝑉∆𝑃(1/𝐸_(𝑤 ) +𝐷/(𝑒𝐸_𝑅 ))
label | Acceptance: ΔV < ΔVmax allowable
label | – – – – – – – – – – – – – – – – – –
label | Air Volume Assessment Parameters
label | – – – – – – – – – – – – – – – – – –
textbox | Nominal Size (mm):
textbox | Mean Bore (mm):
textbox | Tested Length (m):
textbox | V (m3):
textbox | e (mm):
textbox | Ew (kPax103):
textbox | Er (kPax103):
textbox | ΔP (kPa):
textbox | ΔVmax allowable (L):
textbox | ΔV (L):
textbox | Acceptance:
checkpoint | Main Test Phase
label | Observe and record pressure for 0.5 - 1.5hrs
label | Acceptance:
label | 1. No failure of any thrust block, pipe, fitting, joint or other pipeline component present
label | 2. No visible leakage present
label | 3. Pressure rises or remains static for 30min period
label | 4. If doubt exists extend pressure recovery to 90min where pressure drop is to be < 20kPa
checkpoint-no-status | Comments:
checkpoint-no-status | General Methodology Details
textbox | Process for removal of air
textbox | Details of water meter
textbox | Details of pressure gauge
textbox | Details of pump
textbox | Water source
textbox | Water Disposal
section | Signoff
checkpoint | Checked and Signed by Site Engineer
date | Date:
holdpoint | Signature
checkpoint-no-status | Site Photo Records