## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | CS-4103 - Water Loss Test | [5 empty] | CS-4103 - Water Loss Test
section | DETAILS
checkpoint-no-status | Details
textbox | Contract:
textbox | Sub Work Area(s):
textbox | Sublot(s):
textbox | Work Area(s):
textbox | Lot(s):
date | Date:
checkpoint-no-status | Personnel Conducting Test
textbox | Drain Layer:
textbox | Site Engineer:
textbox | CPS Engineer:
textbox | Qualification:
section | Pipe Material and Rating
checkpoint | Pipe Material and Rating
textbox | Pipe Internal Diameter (mm) D:
textbox | Depth of Pipe Below Water Table:
textbox | Ambient Air Temperature: |  |  | °C
textbox | Water Temperature: |  |  | °C
section | Water Loss Method
checkpoint | Water Loss Method
label | Procedure
label | 1. Remove air from pipeline
label | 2. Apply test pressure to pipeline
label | 3. Allow pressure to settle for 12 hours
label | 4. Re-apply and maintain test pressure for 5 hours by successively pumping a sufficient amount of water
label | 5. Measure water volume required to maintain pressure between Hour 2 and Hour 3 - V1
label | 6. Measure water volume required to maintain pressure between Hour 4 and Hour 5 - V2
label | 7. Calculate:
label | Where:
label | Q = allowable make up water, (L/hr)
label | D1 = nominal diameter of pipe size #1, (m)
label | L1 = length of pipe size #1, (km)
label | D2 = nominal diameter of pipe size #2, (m)
label | L2 = length of pipe size #2, (km)
label | D3 = nominal diameter of pipe size #3, (m)
label | L3 = length of pipe size #3, (km)
label | H = average test head of pipeline, (m)
textbox | Standard Test Pressure: |  |  | kPa
label | – – – – – – – – – – – – – – –
label | Water Meter Readings
label | – – – – – – – – – – – – – – –
label | Test Time ¦¦ Time of Day ¦¦ Reading (m3)
textbox | Start ¦¦ 0:00:00 ¦¦
textbox | 2 hr ¦¦ 2:00:00 ¦¦
textbox | 3 hr ¦¦ 3:00:00 ¦¦
textbox | 4 hr ¦¦ 4:00:00 ¦¦
textbox | 5 hr ¦¦ 5:00:00 ¦¦
label | – – – – – – – – – – – – – – –
label | Water Loss Method Parameters
label | – – – – – – – – – – – – – – –
textbox | L1 (m)
textbox | D1 (mm)
textbox | H (m)
textbox | Q (L/hr)
textbox | V1 (L)
textbox | V2 (L)
textbox | 0.55 V1 + Q
textbox | V2 ≤ 0.55 V1 + Q
checkpoint | Acceptance
label | The test length shall be acceptable where:
label | 1. No failure of any thrust block, pipe, fitting, joint or any pipeline component
label | 2. No visible leakage present
label | 3. 𝑉_2≤0.55𝑉_1+𝑄
checkpoint-no-status | Comments:
label | Attach Test Section Sketch (show heights, air valves, gauges and filling points)
checkpoint-no-status | General Methodology Details
textbox | Process for removal of air
textbox | Details of water meter
textbox | Details of pressure gauge
textbox | Details of pump
textbox | Water source
textbox | Water Disposal
section | Signoff
checkpoint | Checked and Signed by Site Engineer
date | Date:
holdpoint | SIGNATURE
checkpoint-no-status | Site Photo Records