## Sheet1
checklist-flat | DX AC Unit Install
checkpoint | Is the location drawing approved for construction
checkpoint | Is site safe for work start, report discrepancies (floor, walls etc)
checkpoint | AC Unit is correct for the system and position shown on drawings
checkpoint | Check casing, fans, coils &amp; duct for damage, report observations
checkpoint | All pipework (Pair coil &amp; Condensate drain) is correct and ready for installation
checkpoint | Is AC Unit installed level &amp; plumb
checkpoint | Fill drain tray to test condensate drain
checkpoint | Are supports and fixings installed adequately
checkpoint | Verify &amp; record on drawing As-Built dimensions (if differ or required)
checkpoint | Check Electrical Supply to Indoor &amp; Outdoor Units
checkpoint | Photos taken
signoff | Signoff by Main Contractor or Engineer, if required
checklist-flat | FCU Template
checkpoint | Is the location drawing approved for construction
checkpoint | Is site safe for work start, report discrepancies
checkpoint | FCU is correct for the system and position shown on drawings
checkpoint | Check casing, fans, coils &amp; duct for damage, report observations
checkpoint | Filters installed, size recorded
checkpoint | Is FCU installed level &amp; plumb
checkpoint | Are supports and fixings installed adequately
checkpoint | Verify &amp; record on drawing As-Built dimensions
checkpoint | Photos taken
signoff | Signoff by Main Contractor or Engineer, if required
checklist | HTM02-01 B3_4 Leakage Test
section | Leakage test
checkpoint | Details
textbox | File number:
note | During a test period of 2 hours, the maximum pressure loss should be ≤ 0.2 kPa for 400 kPa systems,
note | ≤0.5kPa for 700 kPa systems, 1 kPa after 1 hour for vacuum with source of supply isolated.
note | Systems should be tested at a working pressure of;
note | For compressed medical gas systems - pipeline distribution pressure;
note | For medical compressed air systems for surgical use - pipeline distribution pressure;
note | For vacuum systems - pipeline distribution pressure.
checkpoint | A certified gauge was used
textbox | Number
textbox | Date last tested
checkpoint | Gas Tested (Pass or Fail at end of test)
textbox | Test Pressure (kPa)
textbox | End Pressure (kPa)
textbox | Pressure Change (kPa)
textbox | Time started
textbox | Time ended
textbox | Initial temp
textbox | Final temp
checkpoint | Were any links made - make a note in the comments
checkpoint | Photos taken
signoff | Signoff by Main Contractor or Engineer, if required
section | Pipework 2nd Fix QA Checks
checkpoint | Copper to AS/NZS 1571 Table B
checkpoint | Silfos 15%
checkpoint | Terminal Outlets 2nd Fix Fitted
checkpoint | Alarm Pressure Sensors Fitted
checkpoint | Flexible Hose Fitted
checkpoint | Safety Valves Fitted
checkpoint | Pressure Gauges Fitted
checkpoint | Labelling of AVSU’s &amp; LVA’s
checkpoint | As-Builts Marked Up
checkpoint | Photos taken
signoff | Signoff by Main Contractor or Engineer, if required