## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
eacdf556-7493-5d31-8b67-b3ac4559ccfa | checklist | FH-ZU2-QU-ITP005 - Stormwater Drainage - Rev 1 | itp | ITP005 - Stormwater Drainage
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
54e098fd-2875-533c-ae63-868a90e30081 | note | Frequency - Prior to commencing activity
3a9488af-ceef-526d-a9e6-e8a30e966b9f | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
471f36d6-b4b4-5388-a9d2-5ae7ece93b5f | note | ○ using the correct and complete set of drawings
8f7a1599-66cb-573c-9016-a55fbc589bc8 | note | ○ all drawings are the latest revision.
c2e5a589-5901-5b02-9701-76e4ce132a9a | note | Reference Documents - Drawings and Aconex Register
a2ee1067-eb31-532d-8b47-6005b527fbc3 | note | Inspection/Test Method - Visual Inspection
bfafb1b0-e9c1-591c-b5de-dc2927d5d9b0 | note | Record of conformity - Up to date drawing sets & ITP
839ea919-c7d7-547f-a4c5-a127348d8a0e | note | HP*
95bf2957-8d71-57ca-98d9-f701505fe279 | note | Responsibility - Project/Site Engineer
16f17a8f-429d-5221-b86f-2a3ff34b50bc | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
2b1c2541-a2e3-53ee-acdf-59d7d816963e | note | Frequency - Prior to commencing activity
56e020d7-7c16-5716-9b87-daa768345924 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: CEMP, TMP, SWMS & WP.
bc2543d4-aa2d-54cf-a7b6-1c651c7eef89 | note | Reference Documents - CEMP, TMP, SWMS & WP
b2945d35-791b-5282-9eab-f1096aae2e5c | note | Inspection/Test Method - Verify
6743976f-a864-5448-8b47-d3bd43ab57a1 | note | Record of conformity - Site and Office Inspection
f3bde6b2-9eeb-5f16-a6fd-7ab73df5c502 | note | HP*
7247c46e-49a4-5101-afd6-c19f89422b74 | note | Responsibility - Project/Site Engineer/Supervisor
a959ad58-ba7b-515e-934e-cfe533042728 | date | Date Completed:
ddc68377-ad92-57e5-8ab0-c671f713640c | checkpoint | 1.3 - Excavation Permit
67c58622-d040-5817-8e40-c14ba3c81201 | note | Frequency - Prior to commencing activity
858c6e33-5f6d-5f36-b9be-131e6512679b | note | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
d89748f0-3fe4-5f6e-bd16-db487ca14c10 | note | Reference Documents - Excavation Permit
5ac316e1-5683-5604-bf46-2f6aa45e1fe3 | note | Inspection/Test Method - Verify
2a3b06da-8a9d-55ae-a1b3-00d7413308e1 | note | Record of conformity - Proof of signed permit
62992194-6156-50b2-81f9-ef93471b5596 | note | HP*
11702d77-2c52-5332-81a8-f6e2b636d283 | note | Responsibility - Project/Site Engineer
5da7027f-4163-53a4-8cf3-0db8251e49d5 | date | Date Completed:
8a938930-5b81-5c2a-981f-3429c2180500 | section | 2.0 - Stormwater Products and Materials
5f7ce117-da10-5b8f-8bce-12ebc1eaf9df | checkpoint | 2.1 - Drainage Pipes (RCPs)
41d9fad8-a375-534c-a828-f397d7515358 | note | Frequency - Prior to commencem ent of works
6f00cc3b-c4a0-5f15-b5f6-bf98b9efe43f | note | Acceptance Criteria - Drainage pipes supplied in accordance with AS4058.
bb56e26e-19e7-566c-ba5d-74cdce66240b | note | ○ Material submission approval.
b162d0c8-25a1-5911-b3f4-0422cfa98d99 | note | Reference Documents - CL16.6.1
8228597f-c73b-526f-af9d-351be9066490 | note | Aconex ref: DCWC Mgt-GCOR-009281
25943020-9f4e-5ca1-bb79-37472b1edede | note | Inspection/Test Method - Document Review
ad6d63b5-fe57-5348-bd57-1d841f377ee4 | note | Record of conformity - Aconex
d8eba816-e46c-541d-aec8-fefd40c15961 | note | HP
57487e94-4c41-5a5e-8e96-638ad350df34 | note | Responsibility - Project/Site Engineer, Beca
179683db-9a8d-5462-955f-c7ee24fced30 | date | Date Completed:
e3753df8-916f-5363-bbda-b521a4126ecb | signoff | AUTHORITY HOLDPOINT
1b2eb359-4c69-5a42-8120-5367c623b1bb | checkpoint | 2.2 - Pipe Support Cradles
8d618c69-5b5e-5645-817f-836c8e834b02 | note | Frequency - Prior to commencem ent of works
9c03adc9-e7de-52a6-993c-ccf61071cfe7 | note | Acceptance Criteria - Pipe to sit on firm foundation with pipe support cradles.
cea46deb-31cf-5803-af12-5fe92b2db20f | note | ○ Material submission/ Shop drawing submission.
b213bf5e-eb9c-5753-b606-7d40d87cd7e4 | note | Reference Documents - Cl16.5.6.1
a40cf2e5-0db3-51ea-b1c4-75fbd7cbc6d1 | note | Aconex ref: DCWC Mgt-GCOR-009496
076afd1f-35a5-5927-a7fc-edd5de7cec1e | note | Inspection/Test Method - Document Review
3a0220cb-cceb-5803-a539-4a7b71938cac | note | Record of conformity - Aconex
5acb6203-0f4b-5ceb-886a-84cdc070e164 | note | HP*
ec6daf90-e504-55df-a72d-5737e28ea03c | note | Responsibility - Project/Site Engineer
ee87f83a-c632-507e-9a14-1ea8ce2dcacd | date | Date Completed:
71c61f1f-7bf6-51f7-9473-621c8a53ddd0 | checkpoint | 2.3 - Encasement Material
046121b9-b4f0-54f0-8a63-31d5a43a9243 | note | Frequency - Prior to commencem ent of works
cfed6de3-a0e4-56e6-a0f6-bd5a01012fcb | note | Acceptance Criteria - Encasement Material to be 5Mpa lean mix concrete for all RCP’s.
75304e44-4159-53f3-9435-58d198c06a7b | note | ○ Material submission approval.
549db1d7-fd4a-5eab-b6d1-07156f91fe49 | note | Reference Documents - Cl16.5.6.1 & 16.6.2.2 & Tender Clarifications #36
eb1080aa-021d-5be6-b979-d353ecb13764 | note | Aconex ref: BecaCPL-RTRFI-000089
1ed1078f-fff6-57f8-b1e1-0cf5460b2dd8 | note | Inspection/Test Method - Document Review
42d9471f-bd13-5359-b02c-cf38eb141023 | note | Record of conformity - Aconex
be559595-6804-5b57-ac83-af45fe1f80c8 | note | HP
2e927600-b0f8-50f9-b5ef-90d1180e4339 | note | Responsibility - Project/Site Engineer, Beca
378e34be-3bd9-5bee-b76f-f57c9a9a2a99 | date | Date Completed:
d52c4130-ee00-55e4-80f9-ae18f97deb84 | signoff | AUTHORITY HOLDPOINT
ea30ceb6-447f-5f06-879d-cf20a33d83c1 | checkpoint | 2.4 - Backfill Material
fa1e2509-551b-53e2-b3e4-40cc2b17a126 | note | Frequency - Prior to commencem ent of works
00ce685d-1629-5606-af60-85e42324d169 | note | Acceptance Criteria - Backfill material to be 6% cement stabilised sand to pavement formation level or approved otherwise.
b7edf96b-f4dc-56ba-a385-62c46425914d | note | ○ Material submission approval.
1269190a-dcff-5390-9084-4e405c70093c | note | Reference Documents - Cl16.5.6, 16.5.6.3 (a)(i) & 16.6.2.2.
f4389ac0-ef80-594f-bf52-856b6d8aa05b | note | Aconex ref: BecaCPL-GCOR-000802
62c05dc6-f5a7-5245-b8ba-0b49ce5d172c | note | Inspection/Test Method - Document Review
1449f01c-c4aa-5c77-aa84-5af40b4e64e8 | note | Record of conformity - Aconex Ref
affd4a93-a921-5aa2-8cd0-44c441e6648d | note | HP
fd9f3fa5-4bfc-54a0-8e72-7bffd8a90810 | note | Responsibility - Project/Site Engineer, Beca
c7981258-9841-5a6b-88cc-4a9f38a7f6e3 | date | Date Completed:
f9b66524-c85f-5e85-aa46-2367e78ebd6e | signoff | AUTHORITY HOLDPOINT
b45f932a-0d12-5d1d-ac10-211cdf6d5105 | section | 3.0 - Stormwater Delivery
6d60dbb5-efe8-5503-9c41-8894fa297110 | checkpoint | 3.1 - RCP Delivery
88e5903e-8133-58e3-8e64-8e8887c3b17a | note | Frequency - Each Delivery
9ab65ed4-0c52-5684-b951-353241be59b1 | note | Acceptance Criteria - Drainage pipes supplied and delivered as per approved Material submission.
041fa456-d7d6-5468-88a3-8afbf07b794a | note | ○ Manufacturer’s conformance report.
325517ec-3131-5c6c-8485-ad1ddfe7f2ff | note | Reference Documents - CL16.6.1 & AS4058
4f86dc35-1ead-595a-963f-52d63f59fb27 | note | Inspection/Test Method - Verify
6c5cabb9-9f3b-5c37-b5c0-8304d309bcb3 | note | Record of conformity - Order Acceptance Form
5f4e3bae-bc6b-59ba-969b-1387a4915c0c | note | IP
fdf5360e-5800-577c-ad9f-ffc483d77ba0 | note | Responsibility - Project/Site Engineer
67bc3511-85af-51e9-a897-ae6d65695009 | date | Date Completed:
f12fff67-318b-5116-a2de-09fa37e1377f | section | 4.0 - Construction Activities
5c6df739-5258-5ade-9921-36b1301c399e | checkpoint | 4.1 - Survey Setout
184b7804-94df-5c10-9503-064b7e236985 | note | Frequency - Prior to construction and each lot
74e80b21-7b41-5c14-8fd1-0aaea06ed169 | note | Acceptance Criteria - Set out the stormwater drainage as shown on the Drawings to identify the locations, lengths and levels at outlets and inlets of pipes.
c997444a-d4ec-5293-9985-137593984628 | note | ○ This constitutes a Hold Point.
45c2e80c-419c-5521-b8b4-d3401d87004b | note | Reference Documents - Cl16.7.1
f12f3715-d50d-5ab2-ae65-f56d39c25ae4 | note | Inspection/Test Method - Survey
572ef53e-e8d6-50be-be91-ee3ee56e43f0 | note | Record of conformity - ITP Signed
39a0f67d-1725-5c40-9a71-dcb48f857a75 | note | HP
54ba654f-6272-5c0d-b9e1-ea03ebe60ed6 | note | Responsibility - Project/Site Engineer, Beca
fa4a235e-3294-560d-8789-a3d08c871e5a | date | Date Completed:
ff9f951f-7476-5d3f-ba8e-80db7c677589 | signoff | AUTHORITY HOLDPOINT
e4eb01cf-d31f-52a8-b825-5b5a10cd54a0 | checkpoint | 4.2 - Excavation
ae9b32ec-7fff-5d0a-9424-24163091f7a9 | note | Frequency - Each Lot
4d6accd7-8604-53a9-ba80-22e6de486899 | note | Acceptance Criteria - All excavation to be performed to the minimum depths, widths and batter slopes as shown on the Drawings, regardless of the type of material.
923600d7-e22b-5c6b-b9b3-98e96bec5038 | note | ○ Trench excavation is to commence at the downstream end, where practical.
c06bac9c-d541-57f4-9632-d0d3b38d1659 | note | ○ The width of trench to be such that the horizontal clearance from the outside of the pipe to wall of the trench to be minimum 300mm when under the runway and taxiway graded strip. Trench width outside of the runway and taxiway graded strip to be the greater of 150mm and D/6.
f20b6792-e317-56ec-9aab-88b5226f314c | note | ○ Subgrade Inspection to constitute a Hold Point.
107547f8-aa65-500c-ae0e-13c46097e260 | note | Reference Documents - Cl16.8.1 & Cl16.6.2.2
b4c9308b-6d7f-54c9-bb86-94b073803c26 | note | Inspection/Test Method - Verify
e4767b4c-5011-58e6-aed5-79760c673c48 | note | Record of conformity - ITP Signed
2ed83b9e-e250-51d5-9d5f-c97d45d2ec14 | note | HP
68cabd5c-0e9e-5d91-acd3-bdee66617bbb | note | Responsibility - Project/Site Engineer, Beca
a9d66231-9287-5067-8242-cbb0f31407c8 | date | Date Completed:
ff5e91b7-5a2a-57f8-87eb-01651d3a2682 | signoff | AUTHORITY HOLDPOINT
af37bbcb-ba49-5b6e-8c2b-a91b2ba28f0b | checkpoint | 4.3 - Site Dewatering
e99776f6-6cf4-5503-9c98-dd1a53bdacac | note | Frequency - Each Lot
389dad6e-d921-5c6e-84c1-f0e86313a748 | note | Acceptance Criteria - Excavations are to be kept free from water during construction and backfilling and provide pumps, well-points or other equipment as necessary.
b278c28b-7740-546c-9834-724a125c10a8 | note | ○ Any temporary works to be designed such that flooding upstream of the diversion does not occur. This constitutes a Hold Point.
c55d97ae-880c-5161-913e-dea6114660c2 | note | Reference Documents - Cl16.8.4
da00b571-a482-5590-8ee3-bbb311c60c04 | note | Inspection/Test Method - Site Inspection
93d02277-da10-5973-8a27-3ffba730c5a5 | note | Record of conformity - Aconex Ref BecaCPL-GCOR-000891
a7d77778-30f4-570c-a3f4-92e9ce0195a3 | note | HP
c829d6c5-3da0-555f-99f8-f98c7d2adf74 | note | Responsibility - Project/Site Engineer, Beca
8e733820-540c-5f3f-ba59-1d720e847f55 | date | Date Completed:
158e35e2-fa25-5a50-831f-0658256d25c8 | signoff | AUTHORITY HOLDPOINT
7ede9ad6-dd5b-5212-896e-f145ac8b730f | checkpoint | 4.4 - Confirm Ground Conditions
c24d7f4c-211d-512c-8f62-fb8c74c5f909 | note | Frequency - Each Drainage Line
1f1e2149-09a6-5a8a-bf8e-05bcf9343e0e | note | Acceptance Criteria - Min. 1 x DCP test to be undertaken per drainage line / structure to confirm ground conditions. If the first DCP is inconclusive or fails, additional DCP to be taken as needed based on on-site assessment of the ground.
03f1408a-fcfa-59d9-9794-c463a54760c7 | note | ○ Contractor to notify the Contract Administrator of any area of the foundation which contains material that is inadequate to support the proposed drainage structure.
21488094-6570-5bb8-b7d2-27530887acab | note | ○ Inadequate material is deemed to have a bearing pressure less than 130kPa, equivalent to 4 DCP blows per 100mm, per note 4 on drawing ZULU-BECA-012-DWG-07102.
242cba19-a3d8-5f42-88f9-69b17170d46f | note | ○ Inadequate foundation material is to be replaced with a layer of coarse crushed aggregate compacted to 95% relative standard compaction to AS1289 Section 5.5.1 over a geotextile Bidim A29 or approved equivalent.
a504a46e-b0eb-5c9d-97d2-012af669a2a0 | note | Reference Documents - Cl16.8.2 & Tender Clarification 179
b45513b3-79a1-56a5-ad23-95b269d572e3 | note | Inspection/Test Method - Site Inspection
920754ad-5496-5649-ac23-cc159d334d41 | note | Record of conformity - DCP, Test Results
19a4ccca-6f42-515d-a026-65b358677d48 | note | TP
e0837cd8-3bb2-5877-86de-a5278106923e | note | Responsibility - Project/Site Engineer/ Beca
a252e786-e6c8-54d0-8b34-75422fb024b4 | date | Date Completed:
323efbc6-a12c-5e89-ae8a-d285ad22322a | checkpoint | 4.5 - Bedding
61b37c59-fb70-5d0e-a698-20adcac2ec80 | note | Frequency - Each Lot
af9fe81b-be0f-51af-9fc1-0aa0674506f3 | note | Acceptance Criteria - Bedding material/subgrade to be prepared for laying the pipes. Pipe support cradles to be placed on firm bedding. This constitutes a Witness Point.
a494ec9f-64b2-5c1a-adbb-3d56b1681edc | note | Reference Documents - Cl.16.6.2.1
3dbef3ef-2cbd-5041-8907-f8b8307af3a2 | note | Inspection/Test Method - Visual Inspection
1956b3b1-4e04-5e3e-9732-44247b2e39cf | note | Record of conformity - ITP Signed
b97739b7-6d89-55a2-b679-4865132d3009 | note | WP
092f1bf4-ab52-5aea-8233-0f976053f229 | note | Responsibility - Project/Site Engineer, Beca
d2238a42-f78c-584c-9962-043e884ad5b2 | date | Date Completed:
f4714e5d-4d40-5cef-833b-c6bd246f4dd3 | checkpoint | 4.6 - Laying of Pipes (Sample)
b0f015fc-6552-5b29-bc8d-4109aaefe0fa | note | Frequency - First Lot
fdcea21a-b0f1-5a9e-9488-f4881b37681d | note | Acceptance Criteria - Initial sample 20m length of concrete pipeline to be laid and approved by the Contract Administrator for line and level before continuing construction of pipe network, Hold Point.
8154e474-aae9-522a-bb86-a36adaf49a47 | note | Reference Documents - Cl.16.9.1.6
ff430c75-267d-5dc4-9bb9-27ba336032d5 | note | Inspection/Test Method - Verify & Visual Inspection
c912703c-040e-512b-9f93-f947c2067b52 | note | Record of conformity - ITP Signed
0a819ca1-a073-554e-b852-5981530c427d | note | HP
45418fb0-ad6f-55e9-bb76-4c331754f30c | note | Responsibility - Project/Site Engineer, Beca
364dcce2-0e59-5280-b67b-e0c39dfd3bbe | date | Date Completed:
f6289789-09b6-5389-8687-34863a6d111e | signoff | AUTHORITY HOLDPOINT
afa0a0c6-8f35-51b7-8ae2-75ecdc349b39 | checkpoint | 4.7 - Laying and Jointing of Pipes
55ab6429-192d-55db-90d1-e22d55d14f86 | note | Frequency - Each Lot
7ff6eaa5-759b-58da-bcda-b470e99c9620 | note | Acceptance Criteria - Concrete Pipes to be rigidly supported by approved steel pipe cradle during laying.
1ab0c57c-d867-51c9-805d-1cfba53d82cb | note | ○ Pipes to be placed with spigot end facing downstream.
6fe829fb-2d02-5890-ba73-92b42ff58f96 | note | ○ Pipes to be laid with the word ‘TOP’ and or lifting holes uppermost. Lifting holes to be plugged after installation.
3f96e12c-a485-5858-aabe-f2cf56590f05 | note | ○ All Concrete Pipes to be checked and subject to the approval of the Contract Administrator prior to commencement of backfilling, Hold Point.
2fcb497d-7650-53d4-a543-98138cafc299 | note | Reference Documents - Cl.16.9.1.6
eaf88d90-0d84-5b9d-9e63-fcd1e3dd790c | note | Inspection/Test Method - Verify & Visual Inspection
4ad99015-63ff-5ef0-baa5-e0c2fe2c7d66 | note | Record of conformity - ITP Signed
6a597174-ca65-5552-882a-99ff143fd83e | note | HP
c92309d5-ae3a-50f4-9998-027105030665 | note | Responsibility - Project/Site Engineer, Beca
e2eaa18f-509d-5079-a636-1319ae775611 | date | Date Completed:
d20dc25a-fc90-5eff-8bc2-8dcc4456488e | signoff | AUTHORITY HOLDPOINT
5ad7c8ca-97a0-5547-8ef2-3f3b02311170 | checkpoint | 4.8 - Survey
19ba0200-7d70-5c1c-9869-0b767944f1c9 | note | Frequency - Each Lot
ba84b8bd-9cfc-5c75-8319-359bfbd60ead | note | Acceptance Criteria - The alignment, level and grade to be checked on the obvert of every third concrete pipe unit.
051e0e72-b396-5bac-8001-2c429bd84e51 | note | ○ Pipes shall be laid to the lines, grades and invert levels shown on the Drawings. No deviation shall be made without the prior approval of the Contract Administrator.
3bcbb87d-38bc-50b8-854c-b22cd0532cd9 | note | Deviation from Invert Level
9cfa4cdb-4a32-599c-897b-a0be107b8529 | note | ○ Maximum deviation from design invert level to not exceed 20mm and not result in zero grade or reversal of grade in any length of concrete pipe.
b404e9c4-7ff7-5ee3-9781-a07bfd70a889 | note | ○ Where the design pipe grade is less than 1%, maximum deviation from pipe socket to pipe socket does not exceed 20 mm.
bf35ce05-4c92-599f-848f-79c69bdded2a | note | ○ Maximum deviation from design invert level between upstream and downstream structures to not exceed 20mm and not result in zero grade or reversal of grade in any length of concrete pipe.
8ab47876-2624-553a-a091-f979dbe03713 | note | Deviation from Alignment
8746020d-7933-5d0a-94d6-715b8f5b708e | note | ○ Maximum deviation of the concrete pipe from the alignment shown on the Drawings to not exceed 25mm.
00bf8704-8b53-5f6d-90eb-dbeac1b3f060 | note | Reference Documents - Cl.16.7 & 16.9.1.6
98e36215-0999-5d5f-b355-ee54b245c97c | note | Inspection/Test Method - Survey
45d4783a-a78e-5de2-a1e9-a5aaae115305 | note | Record of conformity - Survey Report
e8c5c51b-7c73-5362-bbab-5bc699b81f75 | note | SCP
ec49249a-59ed-5f71-bd09-36378a6def97 | note | Responsibility - Project/Site Engineer
29281e2a-c5e9-596e-a91c-3ba3578fbc68 | date | Date Completed:
a21a4ac7-d74f-52f9-80a8-ed14b5804858 | checkpoint | 4.9 - Backfill Materials
d330036d-185e-5e46-8366-c2c7f4b375fe | note | Frequency - Each Lot
c465880e-2673-5fe3-a924-adb7d7121a49 | note | Acceptance Criteria - RCP’s under Runway and Taxiway Graded Strip
0ff8ca7d-6a9b-587d-82b3-ae0b80d2a9c6 | note | ○ 5MPa wet lean mix to 200mm above pipe obvert.
b7a47116-f844-5054-8ea5-77a8929a72a8 | note | ○ 6% Cement Stabilised Sand to pavement formation level or approved otherwise.
2b325fbd-334e-55c4-a31c-ad9693321040 | note | RCP’s outside Runway and Taxiway Graded Strip
8e1d4e99-575a-5cb3-a0db-2ff00c22e48e | note | ○ 5MPa wet lean mix 150mm above pipe overt completed in stages
a2be7076-28f2-5a0b-989c-7dd7e1330b73 | note | ○ Site won material completed in 200mm loose layer thickness (maximum) or 6% stabilised sand to pavement formation level or approved otherwise.
be32f9d6-757b-5617-af9f-340f9192925c | note | Reference Documents - Cl.16.5.6 & IFC Drawings & Tender Clarification #164
599b4af8-1dfc-5861-8e5c-a43813aff579 | note | Inspection/Test Method - Verify and Site Inspection
c8ab4ca6-dd7b-503d-a5d1-861f531aca8e | note | Record of conformity - Delivery Docket and ITP Signed
0d893b32-e969-5749-b54c-411d59d73362 | note | IP
ada9dd1b-ddca-5e6e-b385-6d121df1925c | note | Responsibility - Project/Site Engineer
5b8512f3-b805-5670-9e2b-46b008eb4aa1 | date | Date Completed:
8f5ad56b-ccbc-5351-8e29-07e076d4b2bc | section | 5.0 - Testing and Inspection
5269f1ff-a783-5266-b983-4f37188b54be | checkpoint | 5.1 - Compaction Requirements (RCPs)
20cf176f-a6b7-5c20-a15f-3a00128219f6 | note | Frequency - 1 test per lot.
130a3c59-641f-510a-aa7a-32754c96dced | note | Acceptance Criteria - Concrete Backfill Under Runway and Taxiway Graded Strip
d7323c0b-d2a3-52ba-b3c3-bdbbc0c3869a | note | ○ 1 compressive strength test for each 50m3 of backfill
b81c3dbe-96d4-5cad-8aaa-3c074b3ed218 | note | Concrete Backfill Outside Runway and Taxiway Graded Strip
13116915-82ef-58ce-a250-2e687f1b84fa | note | ○ 1 compressive strength test for each 100m3 of backfill
5b0edd3d-8dc9-5638-81b6-d2af923ddc36 | note | Backfill Zone - Outside the Runway and Taxiway Graded Strip (for site won material)
28818352-ac85-59f9-9890-d6dc2ad38044 | note | ○ Minimum RD of 95% SMDD (1 lot consists of every 50m3 for concrete backfill and every 2nd layer of backfill zone material every 40m.)
50268ddf-4832-5a04-b762-7344556c95dc | note | Reference Documents - Cl.16.5.6.3 (c), Cl.16.9.6 & AS3798.1 Table 8.1
e4e7c828-7985-5b35-9867-0ed080422016 | note | Inspection/Test Method - Site Inspection
7c2f5a42-9f8d-5f65-b4c2-8ab18d53ae71 | note | Record of conformity - Test Records
c98f2819-da3f-5a3b-9606-d21d1a15883d | note | TP
f5adbcf0-2707-52f6-844c-97e15c83e568 | note | Responsibility - Project/Site Engineer
49e3653e-dbb4-598c-928a-a15de17bcc47 | date | Date Completed:
425ea013-7e49-55f0-b058-434e57d240b7 | checkpoint | 5.2 - Inspection of drainage lines
dc0e3d4b-5cd4-5d5d-a0ed-7e2dd2a289ab | note | Frequency - Prior to constructing pavement
6dd1734b-9742-579c-9bb6-cb16e9c5a269 | note | Acceptance Criteria - CCTV inspection of RCPs required at the completion of the works.
65d7ac9b-b970-5c02-bb61-569d311577b3 | note | ○ Submission of CCTV footage to the Contract Administrator for review is a Hold Point.
21589f61-502d-5693-b289-8a8c5369d97a | note | Reference Documents - Cl.16.10.1
bd1cb358-993c-50bd-b162-888a5e2fe05e | note | Inspection/Test Method - Verify
5bfc6948-2c78-54c6-8b42-5e86765dbe38 | note | Record of conformity - Aconex Ref
5125a29a-784c-58df-bca6-136d172fd69d | note | HP
0a750240-ecff-52c8-9832-f0ad5e348793 | note | Responsibility - Project/Site Engineer, Beca
84fa9f99-d2e5-53e8-991a-df278960a6a1 | date | Date Completed:
cf83799e-b148-56c3-9496-619f3a2b924e | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
07843a40-ad75-597b-8d27-a2d33627f1bb | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
74bea63c-2144-54cf-8d9c-2c5d0a5c32bb | textbox | Print Name:
ceef9121-eb7a-57ad-9b81-0ff6d16629d8 | textbox | Position:
93d9e161-3a8c-5069-bbc8-466eab8fc03c | date | Work Completed On:
4ad221ca-63b8-5fac-8d71-1d492ee82fa6 | date | Date: