## Table 1
[5 empty] | Inspection and Test Plan - Control and Supervision of the Works | [13 empty] | Doc ID: FH-ZU2-QU-ITP039 REV: 0
Client: Melbourne Airport | [6 empty] | Contract No: CP14038-01 | [8 empty] | Prepared By: Jihad Barbar
Project: Taxiway Zulu | [11 empty] | Reviewed By: Jamal Khodr | [6 empty] | Date: 12/07/24
Construction Process: AGL Boring Installation | [11 empty] | Approved By: Giuliano Follacchio | [6 empty] | Date: 12/07/24
Specifications: ZULU-BECA-001-SPC-00004
Structure / Component: AGL
Lot No: |  | Lot Details: | [7 empty] | Lot size/Quantity: |  |  |  | Date:
Item No. |  | Task/Activity Description |  | Inspection/Test | [11 empty] | HP/ WP/ AP/ IP/ TP/ SCP | Responsibility | Checked by:
|  |  |  | Frequency |  | Acceptance Criteria |  | Reference Documents |  |  | Inspection/ Test Method |  | Record of conformity |  |  |  | Project Engineer Principal’s Rep. Surveyor Foreman | Subcontr- actor |  | Principal’s Rep. | FH | Date
1 |  | Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
1.1 |  | Check for correct documentation |  | Prior to commencing activity |  | Ensure that all employees and subcontractors are: - using the correct and complete set of drawings. - all drawings are the latest revision. |  | Drawings / Aconex Register |  |  | Verify |  | Drawings and drawing registers |  |  | HP* | Project Engineer
1.2 |  | Implementation of all measures and controls |  | Prior to commencing activity |  | All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP. |  | PSP, EMP, TMP, JSEA, SWMS, WP |  |  | Visual inspection |  | This ITP signed |  |  | HP* | Project Engineer
1.3 |  | Definition of the work area (survey) |  | Prior to commencing activity |  | Work area has been cleared and surveyed (marked on site). Limits of excavation clearly defined. |  | Drawings |  |  | Visual inspection |  | This ITP signed |  |  | HP* | Project Engineer / Surveyor
1.4 |  | Material Submissions |  | Prior to commencing activity |  | - Ensure material submissions for the conduits and grout are submitted |  | ZULU-BECA-001-SPC-00003 cl. 3.4 AS 1477 AS 2053 |  |  | Verify |  | Aconex reference This ITP signed |  |  | HP | Project Engineer / Principal’s Representative
1.5 |  | Methodology |  | Prior to commencing activity |  | Prepare and implement a Methodology that includes the following at a minimum: - Full details of the steps to be taken for the underbore works; and - Details of equipment to be used. This must be submitted at least 7 days prior to the commencement of site work |  | ZULU-BECA- 001-SPC- 00004 |  |  | Verify |  | This ITP Signed |  |  | HP | Project Engineer / Principal’s Representative
1.6 |  | Locate and prove existing services |  | Prior to commencing activity |  | - Location of services to be found and marked on the ground within the works; - Contractor to obtain excavation permit from APAM prior to any demolition works. - Services located within the works area to be exposed/proven, recorded as survey data and also on a service plan which is to be attached to the Excavation Permit. |  | ZULU-BECA- 001-SPC- 00004 cl. 3.15 |  |  | Verify |  | Melbourne Airport Excavation Permit |  |  | HP* | Project Engineer / Surveyor
2 |  | Construction
2.1 |  | Excavate trenches for Entry and Exit Pits |  | Each lot |  | - Trenches for entry and exit pits shall be excavated to the width and depth required enabling construction of the conduits to the requirements specified on the drawings. - The level at the bottom of the trench shall not be above the required level at any point. - Any over excavation under pavements shall be restored using 5MPa lean mix concrete in conjunction with the embedment. |  | Drawings ZULU-BECA- 001-SPC- 00004 cl. 3.6 |  |  | Visual inspection |  | This ITP signed |  |  | IP | Project Engineer / Foreman
2.2 |  | Existing services crossing new conduits |  | Each lot |  | – Only approved methods of excavation that has been approved by the Principal’s Representative shall be used. – Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file) |  | WMS002 – Working Near Existing Services |  |  | Visual inspection |  | As-built survey report |  |  | SCP | Project Engineer / Surveyor
2.3 |  | Survey as-built |  | Prior to backfilling each lot |  | Surveyor to pick up completed conduit runs |  | FH QMP |  |  | Verify / Inspection |  | Survey report |  |  | SCP / IP | Project Engineer / Surveyor
2.4 |  | Cover |  | Each lot |  | Services installed under road and taxiway pavements and shoulders by under boring must have a minimum cover below the surface as shown in the drawings. Notify the Contract Administrator at the following stages of construction: - At setting up for the commencement of drilling; and - At completion of drilling prior to connection of ducting to pits and backfilling |  | Drawings ZULU-BECA- 001-SPC- 00004 |  |  | Verify |  | Test report Aconex reference This ITP signed |  |  | HP | Project Engineer / Principal’s Representative
2.5 |  | Conduit draw cord |  | Each lot |  | Each duct way in each duct bank shall be fitted with a single unjointed length of draw cord of a length equal to the length of the duct plus 4m. The draw cord shall be nylon rope and be 6mm in diameter, blue in colour. The ends of the rope shall be coiled at the bottom of each pit or wound around a stake. |  | ZULU-BECA- 001-SPC- 00004 cl. 3.10 |  |  | Visual |  | This ITP signed |  |  | IP | Project Engineer / Foreman
2.6 |  | Grout |  | Each Lot |  | 1. Verify that pulling back of 63mm diameter grout lines are limited to 10m. 2. Measure volume of grout used per pull back to identify where full encasement may not have occurred. |  | DCWC Mgt- CONTIN- 000853 |  |  | Verify |  | This ITP signed |  |  | IP | Project Engineer
2.7 |  | Bore Logs |  | Each Lot |  | Submit bore logs for the underbore |  | ZULU-BECA- 001-SPC- 00004 |  |  | Verify |  | This ITP signed JLM Borelog |  |  | HP* | Project Engineer
Final Inspection The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications. Print Name: Position: Signature: Date: / /
Legend:
| HP |  | Hold Point | Work shall not proceed past the HP until released by the Principal’s Representative |  |  |  |  | IP |  | Inspection point |  |  |  | Formal Inspection to be done and recorded
| HP* |  | Fulton Hogan Hold Point | Work shall not proceed past the HP* until released by Fulton Hogan |  |  |  |  | TP |  | Test Point |  |  |  | Product compliance test to be undertaken and recorded/reported
| WP |  | Witness Point | An inspection which must be witnessed by the Principal’s Representative |  |  |  |  | SCP |  | Survey conformance point |  |  |  | A qualified surveyor to check product/section/structure and report
| AP |  | Approval Point | Written or verbal approval given by the Principal’s Representative
Notes