## Checklist Templates
Id | Type | Name | Values | Prompting Name
21a86644-2277-4ab3-bb42-9e1efe02ce0b | checklist | Final Installation Checklist |  | Final Installation Checklist
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
20629547-2a74-4504-a1b1-a686a98fe10d | checkpoint | Fit Off documentation reviewed and circuits ready for testing
02e88a90-6d54-4f2f-8159-178ceaa5f959 | signoff | Add Signature / Request Sign Off
9f092fed-3787-4652-9a5a-815dcd0b0a1c | checklist | PRO_FRM_024_Daily_Site_Report |  | PRO_FRM_024_Daily_Site_Report
b56a7a43-585e-4c85-b7b9-4550b648bb7f | section | General Detail
7dc3052c-4447-4339-873c-b69b00f464e2 | checkpoint | Project Information
c86f245e-91f2-5312-8dfa-dadbe872d060 | textbox | Project Name
899bb5f4-f147-52ae-ad82-f4ef33c594ab | textbox | Project Number
826f18fe-3eca-5f39-bd24-609d1a55034c | textbox | Location
a82afc9f-05ae-574f-8680-47aa2ceefa0c | textbox | Day
ce93b441-9288-5869-90ae-ba859e68a412 | date | Date
a069075d-e82c-5a58-8737-1398aa0c3551 | textbox | Weather & Site Conditions
b64e44b1-7dd8-5bd5-a370-34963ccc9f25 | textbox | Start Time
55b59416-a2ea-5376-a4ad-f8bb38feae8d | textbox | Finish Time
6294d3ce-a3ae-4693-a407-d4b1012debfb | section | Job Progress Details
bbb6ca60-225e-4ad6-a5bd-ec7ecc2f3bbb | checkpoint | 1
c27868a7-2109-5836-b8c7-7aeefa9127b3 | textbox | Item
8f01a165-2aea-57ba-8013-9a7dce87cc42 | textbox | Percentage (%) Complete
47031202-835c-5986-b0e8-1ec110b64a87 | textbox | Additional Information
f0e0d202-5f18-446c-af88-a72a791848d2 | checkpoint | 2
5eeeda2a-d66c-5f34-9f54-10fc7484e589 | textbox | Item
f27c2a9c-13f3-5f9d-a9f8-775a23da5ae0 | textbox | Percentage (%) Complete
8c7f2b95-4063-59a4-859f-699cefcaf89b | textbox | Additional Information
3fefdf44-973b-47e7-8421-b0d9eb78ad0a | checkpoint | 3
38d89290-4efb-51da-885a-63c77ba4fe64 | textbox | Item
72e5f8b9-4c04-5531-bbb7-e20b64e525c5 | textbox | Percentage (%) Complete
6a418214-fe6b-50a4-a540-9f9e8e140ec1 | textbox | Additional Information
dbe7cdfd-364d-4ac5-a132-6f72506e6126 | checkpoint | 4
978013af-352b-5f91-a983-d44a6562dbd8 | textbox | Item
613ae73d-55be-5d70-859a-47cd2dd37814 | textbox | Percentage (%) Complete
275ab9e8-0a4a-5225-a42b-34f5db60f249 | textbox | Additional Information
59cfaf83-2215-4eef-a4e7-7dbde192807b | checkpoint | 5
f651c33e-ef9d-5aea-a240-17a661df35c4 | textbox | Item
e853988d-6c26-58a2-a7e3-df68be2d1427 | textbox | Percentage (%) Complete
4f41791c-21aa-59c7-a924-34c5ce8465fb | textbox | Additional Information
f8fb3642-bffb-4c7a-807f-981ee526c972 | checkpoint | 6
59bc39f9-faa8-5b24-bed7-4a313ff8124e | textbox | Item
5c4c99f7-995b-5796-93c0-900424d22a46 | textbox | Percentage (%) Complete
cc00eb2f-84c5-5d2e-84da-ce8764b9da82 | textbox | Additional Information
78cd8a86-68d0-4ef7-8dcc-87406be4eaf3 | section | Detail Description of Task Activities Installed
57f6db73-beca-4c32-8695-9b6b1b002092 | checkpoint | 1
88b55959-5c95-5360-aa1b-340babfbe700 | textbox | Item
722cf462-36a4-517e-88d9-d9533067853e | textbox | Percentage (%) Complete
373b770c-07f1-5860-af6e-624b37e8b62a | textbox | Additional Information
0655c91b-5b1c-43f8-9efe-9072125ca4cc | checkpoint | 2
ed46c896-4230-5c4d-8810-c22231cfbb6f | textbox | Item
3885e94a-682b-5925-b42d-009a2d5782b7 | textbox | Percentage (%) Complete
8b209f79-c7ea-59ea-a902-29afe74f7403 | textbox | Additional Information
414c938b-5803-4c38-9f1b-cbf2b02624ec | checkpoint | 3
d561542f-ba3c-508a-a7f0-f2782b25e949 | textbox | Item
457af8de-edeb-5794-afbb-ad00d90032d2 | textbox | Percentage (%) Complete
4e39cf57-916e-50e2-8871-87449d0eba35 | textbox | Additional Information
8f798a00-246c-40d8-a889-b111001c4cfe | checkpoint | 4
c1c8fb52-317e-5543-a506-e1acb30f9cb6 | textbox | Item
75b32e9a-4949-5e62-b3ba-145fde00f59e | textbox | Percentage (%) Complete
e01d63b1-1783-5e4f-a235-f21dd2b56486 | textbox | Additional Information
675aef20-8d15-490b-b79e-5cdfcb4647df | checkpoint | 5
551fdb59-8c6e-560e-babd-12285b33dc16 | textbox | Item
7b5dbdd2-be91-5f99-8c77-fd00da0462f4 | textbox | Percentage (%) Complete
3e32680d-3aa6-5799-a7b4-44d1cd6f995c | textbox | Additional Information
ce8dfa51-d5df-4613-abe2-08581c0d9c3b | checkpoint | 6
ce3cc756-d5ce-5c16-9af3-7477f7d1d7a0 | textbox | Item
1e1125b1-01ea-55a9-9e00-ac978bd70b7d | textbox | Percentage (%) Complete
2c125c9d-9857-53ed-8644-05e13fd2b952 | textbox | Additional Information
4a81ce8f-3897-4f3b-a3a3-3a00ec7b4e91 | section | Equipment On/Off Hire
3ecd43f3-d560-4146-a53f-7c1b24f5da9e | checkpoint | Record all relevant information
39c00f82-62f6-55c5-b861-80a2e593240d | textbox | Details
ac9ff225-f2ea-433b-a72d-b5251ee8532b | section | Delays
85528c3f-c8ec-4360-90b5-8d026c349390 | checkpoint | Record all relevant information
a6d5968d-47af-5941-9aa3-2063e69fbdb5 | textbox | Details
85de2072-9a07-4d91-8d62-b99b1ab2c8f5 | section | Other Information
84d436ce-3fc6-4401-994d-b2ee4fe05f27 | checkpoint | Record all relevant information
83664120-ba54-515d-b1e5-06f8fb938a85 | textbox | Details
4e964b81-0bd7-4008-903c-36b4ffde890a | section | Variations
1931fd67-6e96-4c2d-a85f-2dd0e376d87f | checkpoint | 1
c453f0ca-c449-5451-b1da-ffc8bce36eeb | textbox | Variation Number
8a716f59-5fb9-5b45-8f41-ae96debe158f | textbox | Variation Description
b2c1a4f7-29b3-5265-9d55-7a678cd12dc3 | textbox | Percentage (%) Complete
ab4f5073-7a62-4845-9938-b4f4c8a6d363 | checkpoint | 2
a838ad04-9338-5420-84b0-055ca32321d9 | textbox | Variation Number
dd9f3f3c-d202-5b59-a351-ce5d50102144 | textbox | Variation Description
833f4e47-111b-52ed-9c87-00928383857a | textbox | Percentage (%) Complete
eae72698-2da1-47af-8e09-b43ea1f2c99d | checkpoint | 3
632bc23b-b7f5-5bfa-a964-fc925cb4e691 | textbox | Variation Number
967b5480-32a0-549e-b708-e516169ec87e | textbox | Variation Description
6bdad834-dcc6-5473-b3f5-b45f610e6d1c | textbox | Percentage (%) Complete
c363b3f1-7321-434f-8b8e-8641de2b5df6 | section | Project
ba26d16b-2bcf-4516-9c19-2249309310cc | checkpoint | Meetings
c87b3790-2458-5394-8639-64a1f12c3009 | textbox | Details
5f6fea4c-1d4e-4b01-bcd7-dde80c43f6f8 | checkpoint | Visitors
02f836df-1c38-5c2b-85b7-f36381cc5aa0 | textbox | Details
7e2f2833-2818-4ad1-ab39-b8692ec7edf6 | section | Safety
26682a1d-c237-47de-9174-cbfda3b0bbbe | checkpoint | Incidents
2ad202c3-7bd8-571f-9f49-cbfc2dc2c748 | textbox | Details
d5565e87-a6e3-4fca-8b03-84f545820ff2 | checkpoint | Problems
93d9b35a-17d4-56d6-903a-62dcd2faff85 | textbox | Details
e8f28f99-159e-403e-9808-da773c000dde | section | Next Shift Task Activities
6cd3c92d-01f7-4bcb-b78f-78f7d44a2bd1 | checkpoint | Record all relevant information
ee99a56d-1af9-5fe0-9364-c1f4def342e9 | textbox | Details
212a6e5f-445e-4147-b595-6e9a867b85b5 | checklist | QA_TEM_061_Construction Lighting |  | QA_TEM_061_Construction Lighting
0c80477f-0402-4171-a3bd-881dc47bd517 | section | Details
dee59dab-ca5c-4653-b642-ddf8dc2be636 | checkpoint | Check Light fittings are securely fitted
c54084ef-2469-4914-9095-31879c2dc140 | checkpoint | Check Emergency Exit signs visible and clear from obstructions
f8bc1cd1-5a54-42ad-9c3a-d82c0227fc3b | checkpoint | AS3012:2019 - 2.7.1 - Ensure minimum lighting levels are at least 40 lx for walkways and 160 lx for general areas, lunch rooms and site offices. Record results on layout drawing and attach to this ITC
32916f2d-d988-5831-98aa-d6d19e5cb93b | textbox | Record Drawing Reference:
15d604b0-1f6a-4dcf-96d9-613036f724fb | checkpoint | AS3012:2019 - 2.7.2 - Light fittings are the correct type for the application and are protected against Mechanical damage
626505aa-69d4-482f-8029-ebe593ccd329 | checkpoint | AS3012:2019 - 2.7.3.1 - Emergency lighting is provided in designated access and egress paths
8cd2dbba-1085-4b77-8b08-2f35d4417863 | checkpoint | AS3012:2019 - 2.7.3.1 - Emergency lighting is provided directly above and in front of switchboards (if natural lighting unavailable)
5634a23e-15aa-4ba4-aebc-2b7932159d5e | checkpoint | AS3012:2019 - 2.7.3.1 Complete fields for one of the following : Item (a) or Item (b) below
371e7025-3c10-5812-9bfc-de4cbc30624f | tickbox | a) An average of 20 lx at 900 mm above floor level along the centre line of the corridor containing the emergency luminaires has been achieved. Record results on layout drawing and attach to this ITC
bcb8a3c4-a4e1-5069-abde-c729328ac29c | tickbox | b) Emergency lighting has been installed using luminaires complying with AS2293.3:2018 luminaire classification and the mounting height and spacing, as specified in AS3012:2018 Tables 2,3,4 and 5.
304731a1-bdff-5bea-b52e-1309b63e0408 | textbox | EM Light Type or Model No.
4c6e4a7d-4fef-5864-83b4-a02e2dba6ab8 | textbox | Fitting Classification
69f75610-b648-5252-b4d7-e902c294a591 | textbox | Table No.
68aebe90-c7b0-5428-b02d-2838d63757fe | textbox | Mounting Height
497c14fc-c8cf-536d-a566-63918f49500d | textbox | Max Spacing between fittings (C 90, C 0)
c34932fb-5f0f-4d41-87cf-188c93d2216b | checkpoint | AS3012:2019 - 2.7.3.1 - Emergency lighting levels are maintained for at least 60 mins following loss of normal lighting in the area.
78a314c4-4c47-474b-83f8-c5c869224c93 | checkpoint | Log book is completed and copy on-site
e5c2c95a-8626-4f5d-92d8-aa168671b2f7 | checkpoint | Emergency light fittings are correctly identified in line with log book
de050211-acb2-46e8-b6e0-2aff610cfef5 | checklist | QA_TEM_062_Construction Main Switchboards |  | QA_TEM_062_Construction Main Switchboards
690b459a-8e4e-4b2b-8448-ee13e128f0a0 | section | Details
6a86f453-ef69-4e45-9758-281fcb52d741 | checkpoint | AS 3012:2019 - 2.3.1.1 - Switchboard is legibly and indelibly marked to identify the source of supply from which it originates. (min 6mm letters)
61f1d055-fe82-4652-8540-89fcbde911be | checkpoint | AS 3012:2019 - 2.3.1.1 - The switchboard shall be readily accessible and protected from damage
e14f02cf-787a-4fb2-bd15-26cc619edd77 | checkpoint | AS 3012:2019 - 2.3.2.1 (a & b) - The switchboard shall be of robust construction with a minimum IP 23 rating
58f87f24-8316-476d-b2c9-1d2e93d2ed17 | checkpoint | AS 3012:2019 - 2.3.2.1 (c) - Live parts are eﬀectively protected at all times against contact by personnel operating equipment located on the switchboard, including the connection or disconnection of plugs to socket-outlets.
29277115-07c2-4b48-b009-eeaf920ca2b0 | checkpoint | AS 3012:2019 - 2.3.2.1 (c) - All penetrations are closed oﬀ, with propriety fittings, i.e. bungs & lock rings for unused penetrations and pole fillers for unused circuit breaker poles
3afdf8e3-3e34-4ab8-a2af-7b2798d36699 | checkpoint | AS 3012:2019 - 2.3.2.1 (e) (i) - The door or lid requires the use of tool for removal
2bce4d74-2d63-48d5-8e87-96e20822e5f0 | checkpoint | AS 3012:2019 - 2.3.2.1 (e) (ii) - The door or lid is fitted with a facility for locking
575dcbda-68c3-47b5-9089-299ff00a3c8b | checkpoint | AS 3012:2019 - 2.3.2.1 (f) - Switchboard is clearly labelled to distinguish one board from another. (by means of numbers, letters or both)
1f457de5-74bd-4f5f-bc91-ab0046237209 | checkpoint | AS 3012:2019 - 2.3.2.1 (g) - Switchboards is marked in accordance with appendix C to indicate presence of live parts
2bba9939-0fdf-4454-aacb-3d41adccf2ca | checkpoint | An electric shock risk sign is displayed in locations where additional attention is required in the removal of covers, e.g. covers for switchboards or cable junctions
9d3b92e3-0be2-4243-9794-5f3e18cb2ee2 | checkpoint | A danger sign with an additional message indicating the presence of live parts within, is conspicuously displayed on the enclosure
d8e1e1c7-de3e-4a25-83da-1844f958e4d4 | checkpoint | AS 3012:2019 - 2.3.3 - Switchboard is securely fixed in position, attached to a pole, post, wall, floor. (if it is not fixed down for any reason the board should not be in service)
7e117a3c-56a7-49dc-99e2-1fdf816f5365 | checkpoint | AS 3012:2019 - 2.4.1 - Switchboard has one isolation switch marked in accordance with clause 2.4.3. (6mm Text) ‘MAIN SWITCH’ and confirm switch interrupts supply to all downstream circuits
d05a0407-b30e-4ec8-8994-a027292c3b5e | checkpoint | AS 3012:2019 - 2.4.2 - Isolating switches are lockable or located within a lockable enclosure
548b267d-9917-46d4-9096-c91408b83773 | checkpoint | Current single line drawing is readily available within the switchboard
0f8cc6b6-ec8b-4556-b6a7-2da9bc55632e | checkpoint | Switchboards have signage attached with correct Q Electrical site contact details
4f606af6-f482-411d-80f2-761c7a231aed | checkpoint | Switchboards have up to date schedules and are correctly labelled
dce96076-9829-4a5d-a320-522ffcc1233d | checkpoint | All conduit entries into Switchboard have adaptors fitted and glued
19e6cfac-1532-446a-88f0-6acc0c976fd0 | checkpoint | All cables are correctly glanded into the switchboard
f8e19f00-ea93-47c8-ab11-baf769561611 | checkpoint | All spare penetrations are eﬀectively sealed by use of a propriety fitting e.g. screwed bung and lock ring
d64a0df2-f169-4566-9c9a-5405ec8ce168 | checkpoint | Check cubicle has been cleaned of all rubbish, dust, filings, tools, etc
c54a3969-c930-4bdc-9805-b9ffdabb03ed | checkpoint | Check all cable terminations and Bus bar connections are secured correctly & tensioned: (Attach reference documents)
024c1fbb-10e4-56db-9090-0a05a00bc850 | textbox | Item or Part
3c38df23-8ef4-59ad-ae55-782cd81fdc90 | textbox | Torque Setting
c0b88ad6-3b2c-4e1c-8c7c-8b706a5a9ccc | checklist | QA_TEM_063_Construction Distribution Boards |  | QA_TEM_063_Construction Distribution Boards
c3e7ba2d-8fef-408a-bfba-7fbe3f65356a | checkpoint | AS/NZS 3012:2019 - 2.3.1.1 - The distribution board is legibly and indelibly marked to identify the source of supply from which it originates. (min 6mm letters)
83d0dd6c-de3d-4038-8b07-c1b080872f10 | checkpoint | AS/NZS 3012:2019 - 2.3.1.1 - The distribution board shall be readily accessible and protected from damage.
a3ccde46-45ad-414f-92ba-4f72a3db236f | checkpoint | AS/NZS 3012:2019 - 2.3.1.2 - The distribution board shall be positioned in a manner that eliminates the need for leads to be run between levels.
5fbaa70d-a874-41a7-a91c-81eb4aaf43f1 | checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (a & b) - The distribution board is of robust construction with a minimum IP 23 rating.
1dd678ea-5c68-4faa-b27c-68c8a29d5a26 | checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (c) - Live parts are eﬀectively protected at all times against contact by personnel operating equipment located on the distribution board, including the connection or disconnection of plugs to socket-outlets.
0a1fb9cf-4124-4307-a318-10951c670d82 | checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (c) - All penetrations are closed oﬀ, with propriety fittings, i.e. bungs & lock rings for unused penetrations and pole fillers for unused circuit breaker poles.
3c68b9ec-5e48-4354-8003-d42f2f16d30a | checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (d) - An insulated tie bar is fitted for extension leads to prevent strain on socket/outlets.
c55030a5-07e0-45bd-aeac-862d3d855f74 | checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (e) (i) - The door or lid requires the use of tool for removal.
0af75657-e87b-41ed-afb6-b8c71273daca | checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (e) (ii) - The door or lid is fitted with a facility for locking.
41cf8f80-6ca3-40ad-b838-4ad1f66afe89 | checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (e) (iii) - The door or lid shall be fitted with means of retention in the open position.
bd6bd54a-3d8c-49eb-8f31-66a89e613d47 | checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (e) (iv) - The door or lid shall not damage leads and allow the safe entry of leads.
034d1018-da4d-4d54-a055-24ea6f46a1f8 | checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (e) (v) - A clearly visible and legible sign shall be fixed on the external surface. "KEEP CLOSED - RUN ALL LEADS THROUGH BOTTOM"
cfc92646-4903-4a90-91e7-8edb10383876 | checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (f) - Distribution board is clearly labelled to distinguish one board from another. (by means of numbers, letters or both)
54c12acf-d4a4-475c-9aff-c5bf75dbb69c | checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (g) - Switchboards is marked in accordance with appendix C to indicate presence of live parts.
21a6c51b-7694-4a13-b215-d806dd9f45b2 | checkpoint | An electric shock risk sign is displayed in locations where additional attention is required in the removal of covers, e.g. covers for switchboards or cable junctions.
9368d701-c57c-4abd-947a-4a51de92bd46 | checkpoint | A danger sign with an additional message indicating the presence of live parts within, is conspicuously displayed on the enclosure.
f191fc0a-0213-4983-b0db-4c216c755587 | checkpoint | AS/NZS 3012:2019 - 2.3.3 - Distribution board is securely fixed in position, attached to a pole, post, wall, floor. (if it is not fixed down for any reason the board should not be in service)
ef48fe3d-f109-4ab1-90df-5b1452556df6 | checklist | QA_TEM_064_Construction Wiring & Accessories |  | QA_TEM_064_Construction Wiring & Accessories
fdc2352e-2e38-4658-8c4e-5246eee9aa27 | section | Details
774b35dc-03e9-4ec3-86bd-ee68033a4cb6 | checkpoint | Check that the accessories are the correct type
0379558f-64d6-52e0-85c3-58cdb0ffebfb | textbox | Reference Document:
b13e55a8-f4ea-4021-9c0e-b5a9f2f88451 | checkpoint | Check that the accessories are located in the correct position
2b754d57-251d-5f72-9043-592192be780f | textbox | Reference Document:
a909bee7-63c1-4d38-bd8a-ee7aea950c02 | checkpoint | Are securely fitted and field equipment and cabling is clearly labelled
c138bce1-0d6b-4ac5-9626-3ce322115cef | checkpoint | Are fitted in accordance with manufacturers recommendation :
8a42cfe7-7e5f-4996-8d1f-46a1471f2bb6 | checkpoint | AS 3012:2019 - 2.5.2 - Check wiring is not tied, bundled or grouped with permanent wiring; nor attached to free-standing fencing.
abd1550b-fbe0-495a-ba5a-d283094f28cb | checkpoint | AS 3012:2019 - 2.5.3 - Check wiring is mechanically protected in accordance with previously conducted risk assessment.
cac66cdd-9933-579b-b83c-58e99e693ce9 | note | (QA_TEM_057_Construction Wiring Risk Assessment)
d8797585-df91-5ef7-bed3-801ba331f0b6 | note | Or not less than;
dfa86f7d-da28-5e86-874a-1fd09613c820 | note | (a) medium duty rigid or corrugated conduit of insulating material;
7fa8b1c0-3874-5bfc-b9e1-664b57b3e825 | note | (b) heavy-duty rigid or corrugated conduit of insulating material;
5e301452-4083-5326-a292-2f7d36b7eb5b | note | (c) flexible electrical hose;
4b50c382-0be2-5248-86e8-f2a378e6553a | note | (d) armoured cable; or
ac28c072-5742-55ba-8409-d933875db4ba | note | (e) other means that provide equivalent protection against mechanical damage.
d8f32213-399c-4603-9cd7-8e2974d64466 | checkpoint | AS 3012:2019 - 2.5.4 - Construction wiring is readily distinguishable from permanent wiring by using cable sheath of a diﬀerent colour or by attaching iridescent yellow tape spaced at intervals not exceeding 5m and marked with the words "CONSTRUCTION WIRING"
7d374179-1174-4b26-a8dd-1272ee339e9a | checkpoint | AS 3012:2019 - 2.5.4 - If live permanent wiring is located where construction wiring is occurring, or its location, check that it be marked with the words "LIVE WIRING" at interval not exceeding 5m.
db80f6c5-f162-4c55-9f68-05073c168bc1 | checkpoint | Confirm all Field wiring to Isolators, Socket outlets and point off supply has been terminated correctly