## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | QA_TEM_014_Cable Terminations |  | QA_TEM_014_Cable Terminations |  | cdfebefc-d5cf-49e7-ac53-f81381fc6752
| section | Cable Terminations
| checkpoint | Correct type and size gland
| checkpoint | Gland properly and securely fitted
| checkpoint | Correct cable identification (Cable Size/Cable Type) (Photo required)
| checkpoint | Correct core identification (Photo required)
| checkpoint | Cores loomed properly
| checkpoint | Cores on correct terminals (Photo required)
| checkpoint | Terminals properly tensioned as per manufactures specification:
3318cb51-0852-5e57-b463-a2fe5e4c0eb2 | textbox | Torque Setting (NM):
ef986c6c-6049-56b6-8613-0c2103ea63c2 | textbox | Torque Wrench Serial #
| checkpoint | Calibration Exp. Date:
| checkpoint | Cores correctly lugged
| checkpoint | Lugs correctly insulated
| checklist | QA_TEM_011_Mains & Submains Installation |  | QA_TEM_011_Mains & Submains Installation |  | 420a7781-2bee-4e7a-a428-d602d98810bd
| section | Confirm following items comply with requirements:
| checkpoint | Ensure when using a winch to install cables that the correct breakaway pin/fuse and swivel is utilised to ensure the maximum pulling tension is not exceeded.
e43e2fd4-52ca-5553-93a0-cb5a28a08b07 | textbox | Maximum pulling tension: (kN)
2ddaaf50-7f67-5b90-bb48-923c2758646b | textbox | Breakaway pin/Fuse size: (kN) (Attach data sheets)
| checkpoint | Cable is in good condition and free from damage and defects
| checkpoint | Cable has correct origin and destination
68155f0c-9633-5029-80a9-09390c76728b | textbox | Origin
fd89e163-15f3-517e-ac19-3a728eddb5b3 | textbox | Destination
a952ff97-3755-5974-b6e1-da2f8054129c | textbox | Reference Document/s:
| checkpoint | Cable Type, Number of Cores, Size and Configuration is as specified
4263b996-77c1-508b-8a63-2490b0c27e94 | textbox | Size (mm2)
a32e2500-5c29-576b-9de6-544e9c9d7bda | textbox | Cores
773a9455-018a-5818-a9a0-3549ef83bf48 | textbox | Cable Type
9244be0b-35f1-5a88-b50c-8c026d9d920d | textbox | Earth Size (mm2)
0fec3bec-0659-53ed-81a0-e0996f58787b | textbox | Cores
1ce746ba-2b36-59ba-8586-0a08dbd5ddda | textbox | Cable Type
53b82c0f-1f3f-5369-9d80-db2ea9b8dcd7 | textbox | Reference Document/s:
| checkpoint | Bending radius recommended by the cable manufacturer has been observed
4da24eca-22b2-5a80-9194-359c147b8b77 | textbox | Bending Radius (mm)
38443967-8867-5897-9db5-41190454fafb | note | Where manufacturer’s information is not available, the following minimum internal radii may be considered suitable
1491e186-b3c7-5d66-a894-a6c8954eccbd | note | Unarmoured sheathed cables = 6 times the cable diameter
234e64e8-1f33-576d-bae9-1e07bf47dcfd | note | Armoured sheathed cables = 12 times the cable diameter
| checkpoint | Cable follows the correct route
| checkpoint | Cable is clear of heat sources
| checkpoint | Cable is segregated from telecommunications cables by either a continuous barrier or separated by at least 50mm - AS/NZS 3000 Clause 3.9.8.4 (c).
| checkpoint | Cable is secured and mechanically protected (where required).
| checkpoint | Cable is marked with cable or circuit number