## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist-flat | QA_TEM_014_Cable Terminations |  | QA_TEM_014_Cable Terminations |  | cdfebefc-d5cf-49e7-ac53-f81381fc6752
| checkpoint | Correct type and size gland
| checkpoint | Gland properly and securely fitted
| checkpoint | Correct cable identification
| checkpoint | Correct core identification
| checkpoint | Cores loomed properly
| checkpoint | Cores on correct terminals
| checkpoint | Terminals properly tensioned
| checkpoint | Cores correctly lugged
| checkpoint | Lugs correctly insulated
| checkpoint | Adequate clearances
| checklist-flat | QA_TEM_011_Mains & Submains Installation |  | QA_TEM_011_Mains & Submains Installation |  | 420a7781-2bee-4e7a-a428-d602d98810bd
| checkpoint | Cable is in good condition and free from damage and defects
| checkpoint | Cable has correct origin and destination
9a8aaf33-46d7-541b-bdcb-5bcb4edad69e | textbox | Origin
9bc36e79-bef2-593f-9b6c-3384bc4105a2 | textbox | Destination
| checkpoint | Cable Type, Number of Cores, Size and Configuration is as specified
4996ef1e-b9ae-5cc2-b0b0-3ae093277bf1 | textbox | Size (mm2)
4f31905a-7588-59a4-bfe6-2a6c2d7271b1 | textbox | Cores
701a1ac8-8624-5478-b3e9-f169078a878a | textbox | Cable Type
4eda15aa-24c5-5ff2-9e0e-bd87bfc73c55 | textbox | Earth Size (mm2)
4959e65c-a0da-52f2-962e-d210690ab21b | textbox | Cores
4b638f83-56a7-5852-8f51-d728479526d1 | textbox | Cable Type
| checkpoint | Bending radius recommended by the cable manufacturer has been observed
4b6e3652-602f-5018-b26f-123fe372d80e | textbox | Bending Radius (mm)
2317db07-bfde-5fb4-a3bc-8f27e881d7e8 | note | Where manufacturer’s information is not available, the following minimum internal radii may be considered suitable
3a4c3dbd-c304-54d1-91b1-334dcdae11dd | note | Unarmoured sheathed cables = 6 times the cable diameter
38ceaebc-48e3-5b70-be41-64595e44b5e6 | note | Armoured sheathed cables = 12 times the cable diameter
| checkpoint | Cable follows the correct route
| checkpoint | Cable is clear of heat sources
| checkpoint | Cable is segregated from telecommunications cables by either a continuous barrier or separated by at least 50mm - AS/NZS 3000 Clause 3.9.8.4 (c).
| checkpoint | Cable is secured and mechanically protected (where required).
| checkpoint | Cable is marked with cable or circuit number