## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | QA_TEM_014_Cable Terminations |  | QA_TEM_014_Cable Terminations |  | cdfebefc-d5cf-49e7-ac53-f81381fc6752
| section | Cable Terminations
| checkpoint | Correct type and size gland
| checkpoint | Gland properly and securely fitted
| checkpoint | Correct cable identification (Cable Size/Cable Type) (Photo required)
| checkpoint | Correct core identification (Photo required)
| checkpoint | Cores loomed properly
| checkpoint | Cores on correct terminals (Photo required)
| checkpoint | Terminals properly tensioned as per manufactures specification:
| textbox | Torque Setting (NM):
| textbox | Torque Wrench Serial #
| checkpoint | Calibration Exp. Date:
| checkpoint | Cores correctly lugged
| checkpoint | Lugs correctly insulated
| checklist | QA_TEM_011_Mains & Submains Installation |  | QA_TEM_011_Mains & Submains Installation |  | 420a7781-2bee-4e7a-a428-d602d98810bd
| section | Confirm following items comply with requirements:
| checkpoint | Ensure when using a winch to install cables that the correct breakaway pin/fuse and swivel is utilised to ensure the maximum pulling tension is not exceeded.
| textbox | Maximum pulling tension: (kN)
| textbox | Breakaway pin/Fuse size: (kN) (Attach data sheets)
| checkpoint | Cable is in good condition and free from damage and defects
| checkpoint | Cable has correct origin and destination
| textbox | Origin
| textbox | Destination
| textbox | Reference Document/s:
| checkpoint | Cable Type, Number of Cores, Size and Configuration is as specified
| textbox | Size (mm2)
| textbox | Cores
| textbox | Cable Type
| textbox | Earth Size (mm2)
| textbox | Cores
| textbox | Cable Type
| textbox | Reference Document/s:
| checkpoint | Bending radius recommended by the cable manufacturer has been observed
| textbox | Bending Radius (mm)
| label | Where manufacturer’s information is not available, the following minimum internal radii may be considered suitable
| label | Unarmoured sheathed cables = 6 times the cable diameter
| label | Armoured sheathed cables = 12 times the cable diameter
| checkpoint | Cable follows the correct route
| checkpoint | Cable is clear of heat sources
| checkpoint | Cable is segregated from telecommunications cables by either a continuous barrier or separated by at least 50mm - AS/NZS 3000 Clause 3.9.8.4 (c).
| checkpoint | Cable is secured and mechanically protected (where required).
| checkpoint | Cable is marked with cable or circuit number