## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | Fans |  |  |  |  | Yes | Fans | 085bd549-5eee-458d-afa9-48d55f90c830
checkpoint-group |  |  | section | Fans
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
checkpoint-status |  |  | checkpoint | Mountings / springs installed
checkpoint-status |  |  | checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint-status |  |  | checkpoint | U/S of Fan heights correct as per Workshop Drawings.
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-flat |  |  | checklist | E4M - Mechanical Board ( MSSB ) |  |  |  |  | Yes | E4M - Mechanical Board ( MSSB ) | 089815f2-7b7f-4451-801a-ad4b23502099
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
checkpoint-status |  |  | checkpoint | Switch Board Mounted in correct position and level
checkpoint-status |  |  | checkpoint | Switch Board terminations complete
checkpoint-status |  |  | checkpoint | Board Tested
checkpoint-status |  |  | checkpoint | COC's Complete
checklist-flat |  |  | checklist | Cleaning Agent Removal |  |  |  |  | Yes | Flushing - Cleaning Agent Removal | 14fefff5-95f0-4118-8689-a47ee051ef78
checkpoint-status |  |  | checkpoint | All flushing valves are open.
checkpoint-status |  |  | checkpoint | Make-up valve is open.
text | 58b8b881-e3bc-57ac-bdb2-482be2a0c485 |  | textbox | Date
checkpoint-status |  |  | checkpoint | Main drain valve at the pump is open.
label | eaeb98d2-a495-5b9e-afc2-fc76d1d262ad |  | note | Drain waterflow has been calculated by filling up 20 L drum and timing the duration.
text | 28009fde-c71d-5ef4-9233-00a196f5913a |  | textbox | Calculated Drain waterflow (l/s)
text | 56bf711b-2ded-5a3e-855c-ac4379b884a3 |  | textbox | Drain location
text | 2941cc68-d739-5e64-9641-23710cb7ec34 |  | textbox | Drain duration (seconds)
text | 0bfc94cc-3468-5663-8e49-e24d0c495e22 |  | textbox | Calculated drain water volume (L)
text | da37f4d3-1abc-5e87-8d19-654ddf6994d9 |  | textbox | Special trade waste water permit obtained. Do not upload if uploaded in the preparation checklist.
checkpoint-status |  |  | checkpoint | Adequate make-up water available. System's static pressure is not decreasing.
checkpoint-status |  |  | checkpoint | Clean strainers as required. Upload dirty and clean strainer photos here.
checkpoint-status |  |  | checkpoint | Circulate and replace water until the water runs clear.
checkpoint-status |  |  | checkpoint | Water sample is taken, and labeled as "End of Cleaning" and dated.
text | 9893fcca-82fb-5177-9a16-da2436b57fdc |  | textbox | Date
checkpoint-status |  |  | checkpoint | Sulphate
label | 1d8bedaf-97e5-5e39-8bee-963ee942e6f5 |  | note | The level of Sulphate should be same as make up water. Refer previous results. Recommended: <250 mg/L
text | 5a83960f-8830-5876-95ef-1c8abcd6a616 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
label | de3f4caf-15ed-5407-bce4-b3eae26bfa1d |  | note | Recommended: <250 mg/L
text | 4072e792-9e1a-5dc0-bc4b-e2bc046a14ee |  | textbox | Site measurement
text | 1ca8f9ff-ab9f-53e0-bd8c-3a4184a79d2e |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
label | 572250f5-6436-563d-8a55-e0cfc1948ebb |  | note | Recommended: 6.0 < x < 8.5
text | e2ed3bee-6438-5c94-be67-3acb2e93f586 |  | textbox | Site measurement
text | 48c7ecd4-1e7f-530b-b1d5-3012543f38cf |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 5738558e-9fe7-5eb8-a15c-d34ace9716cf |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | fe2bcaa1-e6dd-5794-ba69-c77960a653d0 |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
label | 31db4738-e27c-5d64-86db-1d3c75ae6c19 |  | note | Recommended: <10000 per ml
text | 22980dbd-864e-5773-825a-e8df98600b84 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
label | ffffab82-d024-550a-ba2b-e251fb898f23 |  | note | Recommended: <10 per ml
text | 25fc4296-0d2b-5ec2-8c03-0d6b5d68fd96 |  | textbox | Lab test results
checklist-flat |  |  | checklist | External Duct Work Insulation |  |  |  |  | Yes | External Duct Work Insulation | 150a7f1b-5ea7-4afe-a8d5-0be60e9a56a3
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Ductwrap materials - Multitel 18kg Density foiled 1-side 25mm thick
checkpoint-status |  |  | checkpoint | Cover entire surface with insulation including all flanges, stiffeners and support angles.
checkpoint-status |  |  | checkpoint | Provide 50mm over lapping at all joints.
checkpoint-status |  |  | checkpoint | Tape all joints with 75mm width (72mm on the Market) Aluminium foiled tape.
checkpoint-status |  |  | checkpoint | Fixing for all Duct size 375mm to 750mm steel weld pins on centreline at 400mm spacing bottom surface only.
checkpoint-status |  |  | checkpoint | Fixing for all Duct size 750mm and greater steel weld pins at 400mm spacing maximum.
checkpoint-status |  |  | checkpoint | Fixing for all Duct riser steel weld pins at 400mm spacing maximum.
checkpoint-status |  |  | checkpoint | Using additional polypropylene fixing Bands 600mm centres.
checkpoint-status |  |  | checkpoint | Provide an overlap of atleast 300mm where insulation changes from the inside of the duct to the outside.
checklist-sectioned |  |  | checklist | Mechanical Duct |  |  |  |  | Yes | Mechanical Duct | 172bf90c-5c33-4a50-be36-a700fdce0ffa
checkpoint-group |  |  | section | First Fix QA
checkpoint-status |  |  | checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint-status |  |  | checkpoint | Ducting / equipment connections including flexibles, nuts, bolts and washers correct and tight.
checkpoint-status |  |  | checkpoint | U/S of duct heights correct as per Workshop Drawings.
checkpoint-status |  |  | checkpoint | Ducts to be removed relocated / relocated as per drawings
checkpoint-status |  |  | checkpoint | Duct Hangers (is spacing correct, installed level etc)
checkpoint-status |  |  | checkpoint | Duct jointing (Joints sealed, cleats fitted etc)
checkpoint-status |  |  | checkpoint | Fire Dampers installed in open position c/w access panel.
checkpoint-status |  |  | checkpoint | Sound attenuators installed
checkpoint-status |  |  | checkpoint | Filter box installed
checkpoint-status |  |  | checkpoint | Transfer ducts installed
checkpoint-group |  |  | section | Second Fix QA
checkpoint-status |  |  | checkpoint | Motorized dampers orientation to be installed correct way for sealing purpose
checkpoint-status |  |  | checkpoint | Access Panels to be installed as per drawing
checkpoint-status |  |  | checkpoint | All volume control dampers set fully open.
checkpoint-status |  |  | checkpoint | Butterfly and outlet dampers installed as per drawing and in open position.
checkpoint-status |  |  | checkpoint | Seismic bracing installed as per Drawing
checkpoint-group |  |  | section | Fit Off QA
checkpoint-status |  |  | checkpoint | Flexible ducting installed c/w supports.
checkpoint-status |  |  | checkpoint | Correct Equipment / Correct Grills / Diffuser Installed
checklist-flat |  |  | checklist | Fire Rated Duct Insulation |  |  |  |  | Yes | Fire Rated Duct Insulation | 177bad2e-0519-427f-a22b-70a38684ffdc
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Fire rated Ductwrap materials - 38mm thick Fyrewrap Elite 1.5 (FRL 120/120/120)
checkpoint-status |  |  | checkpoint | Install as per Manufacturer's Standards: (Trafalgar-Fyrewrap)
checkpoint-status |  |  | checkpoint | Fyrewrap duct wrap must completely covered the duct and there must not be any exposed sections or gaps.
checkpoint-status |  |  | checkpoint | A 100mm minimum overlap must be used on all joints. Only the Three specified methods (telescope, checkerboard and butt splice methods.) of overlap may be used when adjoining Fyrewrap duct wraps.
checkpoint-status |  |  | checkpoint | Cut edges must be completely sealed with the specified pressure-sensitive aluminium foiled tape.
checkpoint-status |  |  | checkpoint | ≤600 x600 duct size Steel banding only spacing 40mm from edges over the overlap and one additional between overlaps.
checkpoint-status |  |  | checkpoint | ≤1200 x1200 duct size Steel banding and pins bottoms only spacing 40mm from edges over the overlap and one additional between overlaps. Pre-welded Pins grid 200mm centres.
checkpoint-status |  |  | checkpoint | ≥1200 x1200 duct size pins only all sides of duct pre-welded Pins grid 200mm centres.
checkpoint-status |  |  | checkpoint | Wall penetrations up to 1600mm duct size 75mm x 75mm x1.6mm steel angle 100mm width x 60mm thick maxilite board.
checkpoint-status |  |  | checkpoint | Length of second layer from the fire barrier FRL 60/60/60
checkpoint-status |  |  | checkpoint | Duct size 600mm x 600mm or less -second layer 1350mm
checkpoint-status |  |  | checkpoint | Duct size 600mm x 1200mm or less -second layer 1600mm
checkpoint-status |  |  | checkpoint | Duct size 600mm x 600mm -second layer 1900mm
checkpoint-status |  |  | checkpoint | Duct size 200mm x 2400mm -second layer 2500mm
checkpoint-status |  |  | checkpoint | Duct size 2400mm x 3600mm -second layer 2700mm
checkpoint-status |  |  | checkpoint | Used only Trafalgar Access Panels -must be fitting directly over the existing duct access panels fixed with rivets and fyreflex fire rated sealant, with a second local layer of Fyrewrap.
checklist-sectioned |  |  | checklist | Heater banks |  |  |  |  | Yes | Heater banks | 1d080c57-c3c6-4474-af28-c6c0a5b18c4a
checkpoint-group |  |  | section | Heater banks
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
checkpoint-status |  |  | checkpoint | Mountings / springs installed
checkpoint-status |  |  | checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint-status |  |  | checkpoint | U/S of Equipment heights correct as per Workshop Drawings.
checkpoint-group |  |  | section | Second Fix QA
checkpoint-status |  |  | checkpoint | Fire rated insulation installed as per spec
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-flat |  |  | checklist | External Acoustic Insulation (FCU's) |  |  |  |  | Yes | External Acoustic Insulation (FCU's) | 220b4bda-8011-48c5-a3ab-9318745eabea
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Acoustic wrap materials - 50mm Polyester sheet cover with 5kg wave bar
checkpoint-status |  |  | checkpoint | Cover all surface of the FCU units with insulation excluding the Vents and pipe outlet area.
checkpoint-status |  |  | checkpoint | fixing using self adhesive pins and polypropylene Bands with with buckles .
checkpoint-status |  |  | checkpoint | Tape all joints with 50mm width reinforced Aluminium foiled tape.
checklist-flat |  |  | checklist | Document: |  |  |  |  | Yes | Project Documentation Upload | 26315648-6c7b-4efb-97aa-56d6e755b3ab
checkpoint-status |  |  | checkpoint | Document Attached
checklist-flat |  |  | checklist | Labeling of Equipment |  |  |  |  | Yes | Labeling of Equipment | 29ad1a0c-1765-4538-990b-38a5dc7766b2
checkpoint-status |  |  | checkpoint | Corect label installed as per referance on Equipment / Drawing
checkpoint-status |  |  | checkpoint | Label visable
checkpoint-status |  |  | checkpoint | Correct directional arrows / colour coding installed on system
checklist-sectioned |  |  | checklist | DX Units |  |  |  |  | Yes | DX Units | 37d773f8-f223-48e4-bedb-1f41419bacdd
checkpoint-group |  |  | section | DX Units
checkpoint-status |  |  | checkpoint | Correct Unit Installed
checkpoint-status |  |  | checkpoint | Out door Unit Installed
checkpoint-status |  |  | checkpoint | u/s of Unit at correct height
checkpoint-status |  |  | checkpoint | Mounting and Springs Installed
checkpoint-status |  |  | checkpoint | Pipe Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Correct Hanger Spacing
checkpoint-status |  |  | checkpoint | Unit Plenum Boxes to be installed
checkpoint-status |  |  | checkpoint | Refrigeration Pipework installed as per drawings
text | 035e54ac-1c9e-57b4-acbd-04075647470c |  | textbox | Installation done by
checkpoint-status |  |  | checkpoint | Pipework Installed from DX unit box to Outdoor unit
checkpoint-status |  |  | checkpoint | Condensate Piping installed
checkpoint-status |  |  | checkpoint | Tundish installed by others and connected up
checkpoint-status |  |  | checkpoint | Pressure Tested
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
text | fce0e107-f986-5492-85c6-6fe9e549637c |  | textbox | Sign Off by
checkpoint-status |  |  | checkpoint | Vacuum system down below 500 Microns
checkpoint-status |  |  | checkpoint | Triple Evacuation procedure to be done
checkpoint-status |  |  | checkpoint | Refrigeration ( Scale ) charge unit completed - According to Calculation for Pipe Size & Length
checkpoint-status |  |  | checkpoint | Insulation Complete for Piping and Condensate lines
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
checkpoint-group |  |  | section | Unit Second Fix QA
checkpoint-status |  |  | checkpoint | Filters Installed
checkpoint-status |  |  | checkpoint | Grilles Installed
checkpoint-status |  |  | checkpoint | Commissioning Complete
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checkpoint-status |  |  | checkpoint | Do not energize DX unit until commissioning , otherwise all solenoid will close resulting in no evacuation of Moisture from Indoor units
checklist-flat |  |  | checklist | CHW & HHW Piping ( WELDING ) |  |  |  |  | Yes | CHW & HHW Piping ( WELDING ) | 40c59aa4-04b3-4419-a0e4-c09311753f47
checkpoint-status |  |  | checkpoint | Pipework installed as per Drawing
text | f50032ea-70b7-5010-a5d6-37b698e9decf |  | textbox | Installation done by
checkpoint-status |  |  | checkpoint | All fabricators/welders are qualified and have current tickets
checkpoint-status |  |  | checkpoint | Pipe sizing is correct and valving in correct location
checkpoint-status |  |  | checkpoint | Valve arrangement installed as per Detail specified drawing i.e. Chiller/ AHU / Pump / FCU / VAV / Buffer tank /Expansion tank / Dosing Pod
checkpoint-status |  |  | checkpoint | Insulation blocks installed where required
checkpoint-status |  |  | checkpoint | Correct hanger spacing
checkpoint-status |  |  | checkpoint | Isolating and Control valve installed correctly
checkpoint-status |  |  | checkpoint | Hose piping installed
checkpoint-status |  |  | checkpoint | Air vents installed at all high points
checkpoint-status |  |  | checkpoint | All materials are in accordance with applicable AS/NZ standard
checkpoint-status |  |  | checkpoint | Welding procedure specification to be applied as per attached
checkpoint-status |  |  | checkpoint | Steel is primed and weld painted after works are completed (PA10)
checkpoint-status |  |  | checkpoint | Welding of pipework
checkpoint-status |  |  | checkpoint | Pipework Seismic to be installed ( Expansion joints , loops etc. )
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
text | 362ced87-41a9-57d0-b044-84f7be1680f2 |  | textbox | Drawing Reference Number
checklist-flat |  |  | checklist | Cowls |  |  |  |  | Yes | Cowls | 41d79ad4-e2f6-4e42-a013-11b9c8484bf2
checkpoint-status |  |  | checkpoint | Outside Air Roof Cowl Installed
checkpoint-status |  |  | checkpoint | Builder - Waterproof and Seal to be installed
checklist-sectioned |  |  | checklist | Fire Dampers |  |  |  |  | Yes | Fire Dampers | 43d4b6b7-78a8-41c5-94ce-bf5de3ccf078
checkpoint-group |  |  | section | First Fix QA
checkpoint-status |  |  | checkpoint | Correct FD Installed
checkpoint-status |  |  | checkpoint | Access Panel installed
checkpoint-group |  |  | section | Second Fix QA
checkpoint-status |  |  | checkpoint | Drop Tested ( Sudeshan please use previous job sheet that is in your library)
checkpoint-status |  |  | checkpoint | Track is Clear
checkpoint-status |  |  | checkpoint | Builder to Fire Sealed
checklist-flat |  |  | checklist | CHW & HHW Insulation |  |  |  |  | Yes | CHW & HHW Insulation | 4bf96cc9-5fc5-4e97-8497-9484cf400071
checkpoint-status |  |  | checkpoint | Approved material thickness has been used (Thermobreak®).
checkpoint-status |  |  | checkpoint | Insulation is installed as per the manufacturers recommendations, as well as per any additional requirements set out in the project specification
checkpoint-status |  |  | checkpoint | Pipe sections firmly abutted to Insulation Blocks within the pipe supports, and Blocks have been glued
checkpoint-status |  |  | checkpoint | Insulation is glued to the pipe with a 50mm wide band of adhesive (Ados F2®) at both ends of section to form the vapour barrier
checkpoint-status |  |  | checkpoint | Adhesive is applied along all longitudinal and circumferential joints
checkpoint-status |  |  | checkpoint | A 50mm wide strip of pressure sensitive tape reinforced aluminium tape is applied to the insulation facing, along and around all joints
checkpoint-status |  |  | checkpoint | Mitre cut elbows have been used on all bends.
checklist-flat |  |  | checklist | E4M QA |  |  |  |  | Yes | E4M QA | 4c4577e4-9c08-4af3-994f-d22f47f1cb95
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-flat |  |  | checklist | Duct / Equipment Cleaning |  |  |  |  | Yes | Duct / Equipment Cleaning | 4f27dc4d-d8ac-4bee-900f-ac4245904d17
checkpoint-status |  |  | checkpoint | Specialized Cleaning contractor to clean Outdoor / Supply and Return air Ducting and equipment in accordance with HVCA Guide TR/19 or NADCA Standard 1992-01
checkpoint-status |  |  | checkpoint | Verification of ductwork cleanliness shall be by vacuum test ( gravimetric analysis ) in accordance with HVCA Guide TR/19 or NADCA Standard 1992-01
checkpoint-status |  |  | checkpoint | Undertake a second vacuum test immediately prior to handover.
checklist-sectioned |  |  | checklist | Radiant Heaters |  |  |  |  | Yes | Radiant Heaters | 5a1127a2-1bb8-4a7e-bc0a-eec9ac2605a5
checkpoint-group |  |  | section | Radiant Heaters
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
checkpoint-status |  |  | checkpoint | Mountings / springs installed
checkpoint-status |  |  | checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint-status |  |  | checkpoint | U/S of Equipment heights correct as per Workshop Drawings.
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-flat |  |  | checklist | Braze Bench Test |  |  |  |  | Yes | Braze Bench Test | 686005e7-9255-42eb-848a-379810aedfd4
checkpoint-status |  |  | checkpoint | Test Sheet Completed
text | 6a236dd3-cec7-564b-91f8-94aff49e5095 |  | textbox | BUILDING:
text | 60d79efb-b1ee-5fb5-a1f0-98300064a0dd |  | textbox | AREA / SYSTEM:
text | 3cd5deb0-b9af-5798-8003-f3d9e19d8c2a |  | textbox | DRAWING No.
text | a870987f-c259-51d8-9a5b-0d67b912f1d5 |  | textbox | NAME OF WORKER:
text | fb7c885a-2bac-5b7a-96c7-b7073a120232 |  | textbox | ASSIGNED BRAZE ID.
text | fd544bb3-4bb7-5833-970c-42237eb47634 |  | textbox | JOINT TYPE INSPECTED:
text | 94d953d8-c0c0-5286-8ca8-ce3944bdfdcc |  | textbox | INSPECTING SUPERVISOR
checkpoint-status |  |  | checkpoint | Tube is cut by suitable means, ends are deburred & cleaned of any filings, and surfaces prepared with light grade emery paper.
checkpoint-status |  |  | checkpoint | Joint fit has correct clearance and expanded end of tube (if applicable) is to correct length for pipe size - as per NDY specified requirements
checkpoint-status |  |  | checkpoint | Heat from Oxy Acetylene torch is being applied uniformly to the fitting, and torch flame is slightly reducing/carburising.
checkpoint-status |  |  | checkpoint | Silfos used is 15% and is being applied so that through capillary action is achieved around the entire joint.
checkpoint-status |  |  | checkpoint | Shoulder build-up of Sipfos is just present around the entire circumference of the brazed joint, and completed joint is left to air cool.
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | 56d45f9e-28df-5b1d-aebf-c6535c47b93d |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | 5cd61648-7eba-5444-9198-c604f15b6666 |  | textbox | Consultant Name
checklist-flat |  |  | checklist | Passivisation |  |  |  |  | Yes | Flushing - Passivisation | 6a622c33-212a-462e-9173-b6b805c144e9
checkpoint-status |  |  | checkpoint | Confirmed all terminals backward & forward flushed
checkpoint-status |  |  | checkpoint | Confirmed the system water quality is as close to the make-up water quality as possible.
checkpoint-status |  |  | checkpoint | Test make-up and system water to compare
checkpoint-status |  |  | checkpoint | pH
text | e1cb8ed0-f83c-5c8e-ad3d-f524c3c9984a |  | textbox | Make-up Water
text | 2d33799c-c226-5a49-b684-244d4c410be4 |  | textbox | System Water
checkpoint-status |  |  | checkpoint | Conductivity
text | 90cd3dde-3acc-5438-9d79-c0b1644a2b60 |  | textbox | Make-up Water
text | 6484466a-5106-5539-ba2b-9ed8e0ac06c0 |  | textbox | System Water
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | aef4bd6c-ae04-5e42-8cc8-f2c51467544d |  | textbox | Make-up Water
text | 91e7a0b7-842c-512a-827f-21fee11f8410 |  | textbox | System Water
checkpoint-status |  |  | checkpoint | Inhibitor chemical(s) added.
text | e107d9c1-dca6-5933-9b4f-65d7924d0430 |  | textbox | Enter Date & Time
text | 84aff0da-ca15-5b01-93a9-b5ac9fde86d9 |  | textbox | Name of chemical and SDS
text | 37ba7057-3e91-5a4b-8927-577d02ec8f7a |  | textbox | Name of chemical and SDS
checkpoint-status |  |  | checkpoint | Biocide chemical(s) added.
text | fc1aa27e-1b4c-594b-acb6-bfeaa3ae504f |  | textbox | Enter Date & Time
text | 2ba42a91-0931-5d93-87a2-21fa70e4edab |  | textbox | Name of chemical and SDS
text | 0ed2edbb-7231-5f50-9ac0-864a2bac53b1 |  | textbox | Name of chemical and SDS
checkpoint-status |  |  | checkpoint | Circulate water 2 - 4 hours
select | 8eaf3cf0-8bb6-5580-ad70-56f8977aab80 |  | dropdown | Is there any neutralisation chemical added as per chemical specialist advise? | Yes,No
text | abc2e27e-7ef4-55f4-b2ee-845ee4ea3e47 |  | textbox | If Yes, enter name and quantiy
checkpoint-status |  |  | checkpoint | Test the water conditions at the completion of the circulation.
checkpoint-status |  |  | checkpoint | Water sample is taken, and labeled as "End of Flushing" and dates.
text | fde53494-5c81-57d0-b930-34776acf4c84 |  | textbox | Date
checkpoint-status |  |  | checkpoint | Sulphate
label | cce9c8c5-316c-57ed-9450-401f5d589508 |  | note | The level of Sulphate should be same as make up water. Refer previous results. Recommended: <250 mg/L
text | 4708334d-af26-5fef-aa8c-2fd0bccd982c |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
label | bd56dc4f-d953-504a-88a4-00717f5bbc51 |  | note | Recommended: <250 mg/L
text | b2e03093-e27a-5de2-9a38-a3beb8911154 |  | textbox | Site measurement
text | 3db2dcac-2976-5797-90d3-c3932a97b9b4 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
label | 018ed425-a756-5f4d-8ca5-634616e21519 |  | note | Recommended: 6.0 < x < 8.5
text | d2e50afa-aba7-566e-b821-9cf176c35762 |  | textbox | Site measurement
text | 80ea38ef-a1a4-519c-8584-41c11a4d633d |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 186d24cb-8838-5df8-a533-7eb9662ada24 |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | cead956d-741f-53f2-9cf4-75aa4477f022 |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
label | c0acf4f2-b335-57dc-8d79-de1675e25c79 |  | note | Recommended: <10000 per ml
text | 4caf028f-c47d-5137-863b-a6271ce1c0cc |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
label | 7672eb86-7a48-5a6d-8ac8-477bee9244a4 |  | note | Recommended: <10 per ml
text | 2f994d26-7135-5859-8fc0-57879ceee65c |  | textbox | Lab test results
checklist-sectioned |  |  | checklist | VAV's Boxes Ducted |  |  |  |  | Yes | VAV's Boxes Ducted | 7108e00d-3f40-41f0-86d5-1ec1258415e9
checkpoint-group |  |  | section | Unit First Fix QA
checkpoint-status |  |  | checkpoint | Correct Unit Installed
checkpoint-status |  |  | checkpoint | u/s of Unit at correct height
checkpoint-status |  |  | checkpoint | Correct Hanger Spacing
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
text | ad32ee18-f48b-5de6-bf57-732f1a762bd9 |  | textbox | Drawing Reference Number
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-flat |  |  | checklist | Chemical Flushing Checklist |  |  |  |  | Yes | Flushing - Chemical Flushing Checklist | 75398361-c914-42f3-b576-6a94e01c32f0
checkpoint-status |  |  | checkpoint | Following zones / terminals / branches has been (chemical) flushed during this stage.
text | 16dd69a0-55aa-55a9-9667-026a9851c01f |  | textbox | remove
checkpoint-status |  |  | checkpoint | Confirm all other terminals isolated
checkpoint-status |  |  | checkpoint | Test the water conditions prior adding chemical
text | 98e0fea5-0ac6-58fe-8ff9-67021aac8a40 |  | textbox | pH (Site Measurement)
text | 9b3f42a3-7e3c-5d71-b31d-18708ff6cf84 |  | textbox | Conductivity (Site Measurement)
text | 7a906472-d6b8-5410-ada4-ba808dc4508d |  | textbox | TDS (Total dissolved solids) - (Site Measurement)
text | 8a5cc198-61ac-5dd6-b5d1-a7f9a8b1910b |  | textbox | Chloride (Site Measurement)
checkpoint-status |  |  | checkpoint | Pump is operating at 50 Hz.
checkpoint-status |  |  | checkpoint | Required cleaning added as per flushing plan.
text | b48df8e4-b9b0-5733-9943-1d7ad300e6a4 |  | textbox | Name of cleaning chemical and its SDS
text | d346718d-1b80-57c9-918f-695683faee09 |  | textbox | Required amount: (L)
text | 9a7632da-c530-5ef7-b2cb-119bbb3727dc |  | textbox | Name of additional chemical and its SDS
text | 1e912488-df6b-59fb-935f-1396a23ff26b |  | textbox | Required amount: (L)
text | 009883df-33a3-5eea-9b5a-081ddcd2776e |  | textbox | Name of additional chemical and its SDS
text | 67b5781b-4392-5ba6-a44c-84ad19a8fb22 |  | textbox | Required amount: (L)
text | 694d3dee-39b3-5ec4-9e02-e978e440287f |  | textbox | Name of additional chemical and its SDS
text | 16561a1e-8357-5596-8b76-d5fa0cc0c3c8 |  | textbox | Required amount: (L)
checkpoint-status |  |  | checkpoint | Circulate water 2 - 4 hours
checkpoint-status |  |  | checkpoint | Test the water conditions prior adding chemical
text | 69565291-b4b0-51c0-8c84-4cd8abb08bf4 |  | textbox | pH (Site Measurement)
text | 722123d9-b889-5dcc-a22d-dfc7486e8b2c |  | textbox | Conductivity (Site Measurement)
text | 9d08380f-5a18-5d4e-8bdf-0fadd058ef40 |  | textbox | TDS (Total dissolved solids) - (Site Measurement)
text | 047c0c91-8cfd-505a-8afe-6ab8b1d1214a |  | textbox | Chloride (Site Measurement)
checkpoint-status |  |  | checkpoint | Photo of water sample at the end of the circulation before draining water.
checkpoint-status |  |  | checkpoint | Is there any neutralisation chemical added as per chemical specialist advise? If yes enter name and quantity
checkpoint-status |  |  | checkpoint | Record total and terminal waterflows on the "Flushing Water Flows" test sheet and upload here.
checkpoint-status |  |  | checkpoint | Clean strainers as required. Upload dirt and clean strainer photos here.
checkpoint-status |  |  | checkpoint | If this is last section to be flushed, then continue draining process.
checklist-flat |  |  | checklist | Back-Flush |  |  |  |  | Yes | Flushing - Back-Flush | 7eb5a2b0-cb1b-4008-b588-9fa6aed00d71
checkpoint-status |  |  | checkpoint | Chemical cleaning is completed and clear water is visible at the main drain valve.
checkpoint-status |  |  | checkpoint | Terminals backward and forward flushed and water drained at the terminals until clear water is visible.
text | 912a1a88-7d6e-5081-a6b2-c3a06af049f2 |  | textbox | List the terminals backward & forward flushed.
checkpoint-status |  |  | checkpoint | Water sample is taken from the furthest terminal, and labeled as "Back-flushed terminal" and dates.
text | 1fb3baeb-0270-598a-ac6b-ca7df54b3dbd |  | textbox | Date
checkpoint-status |  |  | checkpoint | Sulphate
label | 93096e62-dc7d-55a6-be18-a8c2a57a11f0 |  | note | The level of Sulphate should be same as make up water. Refer previous results. Recommended: <250 mg/L
text | 839fdfec-7aff-5785-9e85-0fc65e73866a |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
label | b702e3cf-ecc9-525b-b178-fe8e0b6dffbe |  | note | Recommended: <250 mg/L
text | 244a2395-bee7-5720-89d5-7c437902059d |  | textbox | Site measurement
text | 660e4788-4ef6-582c-b139-b14acc36e366 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
label | 9a9c1773-001f-5d2b-94d6-d07a1c380372 |  | note | Recommended: 6.0 < x < 8.5
text | 8aad34e8-3857-583f-8e3b-b5dd7d133ae0 |  | textbox | Site measurement
text | b4e7eabe-9f07-52a7-8ece-77eaa20ad38c |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | cffe0ee3-0337-5535-8a6b-736870ac8415 |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | f6677d6b-8767-53d3-878d-e2dc472c9277 |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
label | b6bfe99f-e2b3-5141-8cef-30030cababc8 |  | note | Recommended: <10000 per ml
text | ce334e5c-ca28-5c26-8859-6f3373c4a32e |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
label | 0fd96093-720c-5ee6-a69a-ce22de5c97f2 |  | note | Recommended: <10 per ml
text | 670218bf-0d6f-5835-8ccb-c9bfa0debb32 |  | textbox | Lab test results
checklist-flat |  |  | checklist | Internal Duct Work Insulation |  |  |  |  | Yes | Internal Duct Work Insulation | 8820f4f2-7931-45d5-aa1a-7246a85f1b68
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Duct materials - Fibreglass
checkpoint-status |  |  | checkpoint | Fixed with Adhesive weld pins and speed clips located not more than 75mm from the edges of the ducts and spaced not more than 300mm centres.
checkpoint-status |  |  | checkpoint | Longitudinal corner joints fixed with:
checkpoint-status |  |  | checkpoint | duct dimensions less than 300mm -25mmx25mm angles
checkpoint-status |  |  | checkpoint | duct dimensions 300mm and greater -50mmx50mm angles
checkpoint-status |  |  | checkpoint | Joints taped between adjacent of insulation with a 75mm wide strip of reinforced aluminium foil laminate tape.
checkpoint-status |  |  | checkpoint | Tape joints protected with 75mm wide sheet metal cover strip, pop riveted to the corner angles.
checklist-flat |  |  | checklist | Metal Cladding |  |  |  |  | Yes | Metal Cladding | 9f083132-69ef-4619-8cf2-35eed954ae14
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Approved materials have been used - 0.6mm galvanised sheet metal, or 0.8mm stucco embossed aluminium
checkpoint-status |  |  | checkpoint | Min. 40mm overlap has been provided on longitudinal and circumferential joints
checkpoint-status |  |  | checkpoint | Coned down ends of sheathing have been provided where insulation has been specified as being coned down
checkpoint-status |  |  | checkpoint | All bends have been neatly cut and formed into lobster-back segments
checkpoint-status |  |  | checkpoint | In applications not involving a vapour barrier, pop rivets are provided through pre-drilled holes
checkpoint-status |  |  | checkpoint | In applications involving vapour barrier, 12mm wide straps of 0.4mm sheet metal are used to secure cladding
checkpoint-status |  |  | checkpoint | Straps on straight lengths are no fewer than 3 on each section, c/w locking buckles
checkpoint-status |  |  | checkpoint | Suitcase Clips' are used for all readily removable items such as evaporator heads, strainers, etc which require access for routine maintenance
checkpoint-status |  |  | checkpoint | Penetrations are sealed for gauges, instruments, and drain vents (silicone)
checklist-flat |  |  | checklist | Condensate Insulation |  |  |  |  | Yes | Condensate Insulation | a48d6783-cd73-4f23-a49c-3bf509bb6edb
checkpoint-status |  |  | checkpoint | Approved materials have been used (e.g. Elastomeric closed cell insulation), min 9m thick
checkpoint-status |  |  | checkpoint | Entire surface of pipe is covered from the indoor units' condensate trap, for a distance of 2m down the line
checkpoint-status |  |  | checkpoint | Adhesive is applied to any longitudinal and circumferential joints, as well as to the ends of the insulation to the pipe
checkpoint-status |  |  | checkpoint | Finish circumferential joints by wrapping with 50mm wide pressure-sensitive pre-adhered PVC tape.
checklist-flat |  |  | checklist | CHW & HHW Piping ( VICTAULIC ) |  |  |  |  | Yes | CHW & HHW Piping ( VICTAULIC ) | b966a686-b0e6-48db-91f6-e322429f4925
checkpoint-status |  |  | checkpoint | Pipework installed as per Drawing
text | c7093cc7-e853-5cc6-9550-9038f2042446 |  | textbox | Installation done by
checkpoint-status |  |  | checkpoint | All fabricators/welders are qualified and have current tickets
checkpoint-status |  |  | checkpoint | Pipe sizing is correct and valving in correct location
checkpoint-status |  |  | checkpoint | Valve arrangement installed as per Detail specified drawing i.e. Chiller/ AHU / Pump / FCU / VAV / Buffer tank /Expansion tank / Dosing Pod
checkpoint-status |  |  | checkpoint | Insulation blocks installed where required
checkpoint-status |  |  | checkpoint | Correct hanger spacing
checkpoint-status |  |  | checkpoint | Isolating and Control valve installed correctly
checkpoint-status |  |  | checkpoint | Hose piping installed
checkpoint-status |  |  | checkpoint | Air vents installed at all high points
checkpoint-status |  |  | checkpoint | All materials are in accordance with applicable AS/NZ standard
checkpoint-status |  |  | checkpoint | The pipe OD and groove dimensions are within tolerance range as per victaulic specification
checkpoint-status |  |  | checkpoint | The correct coupling has been used for the correct joint i.e. flexible or rigid
checkpoint-status |  |  | checkpoint | All fitting are vicataulic approved
checkpoint-status |  |  | checkpoint | Victaulic grease has been applied to the gasket and OD of pipe
checkpoint-status |  |  | checkpoint | Couplings are tightened by alternating sides equally
checkpoint-status |  |  | checkpoint | Bolt pads have firm metal to metal contact
checkpoint-status |  |  | checkpoint | Steel is primed and weld painted after works are completed (PA10)
checkpoint-status |  |  | checkpoint | Pipework Seismic to be installed ( Expansion joints , loops etc. )
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
text | 403ea329-330d-5303-aaf6-811ba581dec2 |  | textbox | Drawing Reference Number
checklist-flat |  |  | checklist | Labelling of Equipment |  |  |  |  | Yes | Labelling of Equipment | c4c59ecf-8815-4734-b38e-605ef80edf74
checkpoint-status |  |  | checkpoint | Correct label installed as per reference on Equipment / Drawing
checkpoint-status |  |  | checkpoint | Label visible
checkpoint-status |  |  | checkpoint | Correct directional arrows / colour coding installed on system
checklist-flat |  |  | checklist | Flushing Preparation Checklist |  |  |  |  | Yes | Flushing - Flushing Preparation Checklist | db1466b5-9943-4384-874f-261c60bfa13a
checkpoint-status |  |  | checkpoint | Differential pressure manometer
text | b71189ff-ab8a-5ed7-aa00-f413e1f22e8b |  | textbox | Model Number
text | b27f00a2-4212-57a7-ac57-3f528a667259 |  | textbox | Serial Number
checkpoint-status |  |  | checkpoint | Ultrasonic Flow Meter
text | bf7953b3-5ccc-5065-a1c0-e4eb2fd5bfec |  | textbox | Model Number
text | 9f4f6f37-a575-5ff7-b0f7-dcd756270d2c |  | textbox | Serial Number
checkpoint-status |  |  | checkpoint | HydROtwist Portable Digital PH Test Meter
checkpoint-status |  |  | checkpoint | HM Digital Hand Held TDS Temperature Water Test Meter TDS-3
checkpoint-status |  |  | checkpoint | Hm Digital Hand Held Conductivity & Temperature Meter EC-3
checkpoint-status |  |  | checkpoint | 0-14 pH test strips
checkpoint-status |  |  | checkpoint | High level 200 ppm chlorine test strips
checkpoint-status |  |  | checkpoint | Low level chlorine test strips
checkpoint-status |  |  | checkpoint | Select the pump to be used for flushing and upload it's Pump Curve here.
select | 20745caf-4422-5088-a921-7c7e2b9ce9e1 |  | dropdown | Flushing pump | Temporary pump,system pump
checkpoint-status |  |  | checkpoint | Pump is under VSD control, wired and ready to be turned on.
checkpoint-status |  |  | checkpoint | Strainer basket(s) is installed with commissioning mesh.
checkpoint-status |  |  | checkpoint | Skimmers sock is installed on the strainers.
checkpoint-status |  |  | checkpoint | Schematic and layout drawings are available and studied.
checkpoint-status |  |  | checkpoint | Isolation valves are installed at each terminal.
checkpoint-status |  |  | checkpoint | Balancing valve is installed at each terminal.
checkpoint-status |  |  | checkpoint | Balancing valves are used to measure waterflows
select | 096d2fe1-5442-5e0f-8ec1-c68dd771d335 |  | dropdown | Any additional method to measure /confirm flushing waterflows. (flushing velocities) | Pump curve,Ultrasonic flow meter,Main Branch valve
checkpoint-status |  |  | checkpoint | Chemicals available on site as detailed in the flushing plan.
checkpoint-status |  |  | checkpoint | Piping system has been pressure tested and passed.
checkpoint-status |  |  | checkpoint | Signed pressure test certificates for every pipe section is uploaded here
checkpoint-status |  |  | checkpoint | System has been installed as per drawing and schematic. If not mark-up the drawing and upload here.
checkpoint-status |  |  | checkpoint | All high points have air vents installed
checkpoint-status |  |  | checkpoint | All low points have drain cocks installed.
checkpoint-status |  |  | checkpoint | Mains water / make-up water supply pipe is connected at the suction side of the pump downstream of the drain port.
checkpoint-status |  |  | checkpoint | Mains water pipe connection size is 40 mm or bigger.
checkpoint-status |  |  | checkpoint | Mains water pressure is minimum 1.3 Bar at flow.
checkpoint-status |  |  | checkpoint | A backflow prevention valve (check valve) is installed at the mains water supply valve and it is certified.
checkpoint-status |  |  | checkpoint | A local drain is available in the vicinity of the flushing pump.
checkpoint-status |  |  | checkpoint | The drain pipe minimum 40 mm size is connected upstream of the strainer.
checkpoint-status |  |  | checkpoint | A high volume of contaminated water is to be discharged to the sewer drain. A discharge consent is not required and the discharge limits are recorded below in the note sections.
checkpoint-status |  |  | checkpoint | A special council discharge (trade waste water) consent is required and obtained. A copy of permit is attached. The discharge limits are recorded below in the note section.
checkpoint-status |  |  | checkpoint | Sensitive equipment as listed below are isolated (by-passes), and not included in the dynamic and chemical flushing processes.
checkpoint-status |  |  | checkpoint | Coils
checkpoint-status |  |  | checkpoint | Control valves
checkpoint-status |  |  | checkpoint | Heat exchangers
checkpoint-status |  |  | checkpoint | Condensers
checkpoint-status |  |  | checkpoint | Evaporators
checkpoint-status |  |  | checkpoint | Cartridges from any auto-flow control valves
checkpoint-status |  |  | checkpoint | 15 L dosing pot is installed and connected
checkpoint-status |  |  | checkpoint | Sulphate
label | 20fe6c5d-1eda-57cb-a385-131bcac82226 |  | note | BSRIA BG 29/2012 recommends make up water quality standards. Sample taken from the make-up water to be tested. Sample bottle labeled as "Make-up water sample" and dated. Recommended: <250 mg/L
text | 173628f3-1e0a-5cca-80e9-3ccc8449030c |  | textbox | Laboratory test results
checkpoint-status |  |  | checkpoint | Chloride
label | 2e9abbbc-c2bf-534e-9e10-c3e3b10257e2 |  | note | Recommended: <250 mg/L
text | 849e77fe-103c-5431-a7a1-afb249a272e0 |  | textbox | Site measurement
text | 62a01a8d-f77b-5f0c-848c-480f904c1437 |  | textbox | laboratory test results
checkpoint-status |  |  | checkpoint | pH
label | b7ccf040-9e07-55be-8362-d874cbb7740e |  | note | Recommended: 6.0 < x < 8.5
text | dc2d3d68-67f1-5e84-9aee-e773c4e43ef8 |  | textbox | Site measurement
text | 988257b2-fe33-5017-9bdf-36c7672a1148 |  | textbox | Laboratory test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 65ef69f4-3d50-5642-8a3a-853cdc90e5fa |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | a1884ef3-9f37-5a47-93f0-ba25daddc99b |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
label | 07a7958b-f701-5414-b86f-c88cd979aa4e |  | note | Recommended: <10000 per ml
text | 9a0abedb-e186-5868-ab9f-38e01a299abf |  | textbox | Laboratory test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
label | f86580c6-52a1-5f3c-96b4-475d877336f1 |  | note | Recommended: <10 per ml
text | d14cfe85-e039-58ec-9042-054c2c47a237 |  | textbox | Laboratory test results
checkpoint-status |  |  | checkpoint | System filled with make-up water
checkpoint-status |  |  | checkpoint | Date and time of initial fill with make-up water.
checkpoint-status |  |  | checkpoint | Make-up water connection location
checkpoint-status |  |  | checkpoint | Mains water pressure (kPa)
checkpoint-status |  |  | checkpoint | Water drained from furthest terminal until clear water is visible.
label | 2e47b84a-8070-59b9-a99f-178fcc8a0b1f |  | note | Drain waterflow has been calculated by filling up 20 L drum and timing the duration.
text | d834cb26-13d0-50d3-a9e8-4f245dc23861 |  | textbox | Calculated Drain waterflow (l/s)
text | 508774b8-ac26-5ec0-9bd9-5d0d232743f2 |  | textbox | Drain location
text | d5686218-8494-5d12-a694-162accdc5bcd |  | textbox | Drain duration (seconds)
text | 9306bf6a-89d5-534f-aad1-4297e5907440 |  | textbox | Calculated drain water volume (L)
checkpoint-status |  |  | checkpoint | Water drained from all other location same as above
checkpoint-status |  |  | checkpoint | Air vent from all high points.
checklist-sectioned |  |  | checklist | Chillers / Buffer Tank / Dosing Pod / Pumps |  |  |  |  | Yes | Chillers / Buffer Tank / Dosing Pod / Pumps | ece1c63f-0e73-4614-84f6-03c3ee38fb86
checkpoint-group |  |  | section | Equipment QA
checkpoint-status |  |  | checkpoint | Check if plinth site is correct
checkpoint-status |  |  | checkpoint | Correct Unit Installed
checkpoint-status |  |  | checkpoint | Setting out point correct
checkpoint-status |  |  | checkpoint | Anti Vibration pads to be installed if required
checkpoint-status |  |  | checkpoint | Correct Springs installed ( If required )
checkpoint-group |  |  | section | Unit Second Fix QA
checkpoint-status |  |  | checkpoint | Condensate Piping installed ( If required )
checkpoint-status |  |  | checkpoint | Tundish installed by others and connected up ( If required )
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
text | 2e27da9c-655d-5bf9-83ef-b9acd80192d2 |  | textbox | Drawing Reference Number
checklist-sectioned |  |  | checklist | Fan Coil Units |  |  |  |  | Yes | Fan Coil Units | ef96d2c8-68eb-4106-afc8-eec2d8c22466
checkpoint-group |  |  | section | Unit First Fix QA
checkpoint-status |  |  | checkpoint | Correct Unit Installed
checkpoint-status |  |  | checkpoint | u/s of Unit at correct height
checkpoint-status |  |  | checkpoint | Mounting and Springs Installed
checkpoint-status |  |  | checkpoint | Correct Hanger Spacing
checkpoint-group |  |  | section | Unit Second Fix QA
checkpoint-status |  |  | checkpoint | Unit Plenum Boxes to be installed
checkpoint-status |  |  | checkpoint | Filters installed
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
text | d4ef442a-da54-526c-85bb-310f91ba882f |  | textbox | Drawing Reference Number
checkpoint-status |  |  | checkpoint | P - trap installed
checkpoint-status |  |  | checkpoint | Driptray installed
checkpoint-status |  |  | checkpoint | Condensate Drains installed
checkpoint-status |  |  | checkpoint | Tundish provided by others
checkpoint-status |  |  | checkpoint | Correct Fall to tundish , and water flow tested
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-sectioned |  |  | checklist | AHU's |  |  |  |  | Yes | AHU's | f259b032-0094-4a0f-ae6a-b7c0e7076920
checkpoint-group |  |  | section | AHU's
checkpoint-status |  |  | checkpoint | Check if plinth site is correct
checkpoint-status |  |  | checkpoint | Correct Unit Installed
checkpoint-status |  |  | checkpoint | Setting out point correct
checkpoint-status |  |  | checkpoint | Anti Vibration pads to be installed
checkpoint-status |  |  | checkpoint | Condensate Piping installed
checkpoint-status |  |  | checkpoint | Tundish installed by others and connected up
checkpoint-status |  |  | checkpoint | Insulation Complete for Piping and Condensate lines
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
text | a5ef81d0-a0d2-570d-bc06-799af0a56096 |  | textbox | Drawing Reference Number
checkpoint-group |  |  | section | Unit Second Fix QA
checkpoint-status |  |  | checkpoint | Filters Installed
checkpoint-status |  |  | checkpoint | Commissioning Complete
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-flat |  |  | checklist | Lab Gas Piping |  |  |  |  | Yes | Lab Gas Piping | f98f7854-e9dd-4803-93d7-302ee962bf7b
checkpoint-status |  |  | checkpoint | Pipework Installed as per drawing ( CO2 , O2 , N2 , HE , ZA )
text | cacaad19-ef0e-543d-abfe-2aad517bc756 |  | textbox | Installation done by
checkpoint-status |  |  | checkpoint | Pipe Brackets installed
checkpoint-status |  |  | checkpoint | Pipe sizing is correct as per drawing / schematic
checkpoint-status |  |  | checkpoint | Valve arrangement installed as per Detail specified drawing
checkpoint-status |  |  | checkpoint | Seismic Installation
text | b86f6d85-9f1f-56b0-9c91-fc96f9cef4da |  | textbox | Drawing Reference number
checkpoint-status |  |  | checkpoint | Gas cylinders installed as per drawing i.e. ( CO2 , O2 , N2 , HE , ZA )
checklist-flat |  |  | checklist | Dynamic Flushing Checklist |  |  |  |  | Yes | Flushing - Dynamic Flushing Checklist | fcbe23ed-9679-4293-9e9d-3c4ed9d607d9
checkpoint-status |  |  | checkpoint | Following zones / terminals / branches has been (dynamic) flushed during this stage.
checkpoint-status |  |  | checkpoint | Uploaded highlighted drawing.
checkpoint-status |  |  | checkpoint | Confirm all other terminals isolated
checkpoint-status |  |  | checkpoint | Turn the pump on and run it at 20 Hz (or at minimum speed)
checkpoint-status |  |  | checkpoint | Increase the pump speed to 50 Hz and measure the total waterflow
text | ac9c4bb4-5625-53c8-a141-c3d55a70a1cf |  | textbox | Record total and terminal waterflows on the "Flushing Water Flows" test sheet and upload here.
checkpoint-status |  |  | checkpoint | Circulate water for 2-4 hours by sampling the drain water quality. Record the duration.
label | 407be494-81dc-58cf-bdb7-11e352fcd596 |  | note | The duration of this process depends on the size of the system and may required to be extended.
text | 592877e3-0072-5723-abc2-66491841689c |  | textbox | Duration
checkpoint-status |  |  | checkpoint | Clean strainers as required. Upload dirt and clean strainer photos here.
checkpoint-status |  |  | checkpoint | Photo of water sample at the end of the dynamic flushing
checklist-flat |  |  | checklist | PVC Condensate Drain Pipe |  |  |  |  | Yes | PVC Condensate Drain Pipe | fd343aef-d40c-451a-9020-10f1c0c4426d
checkpoint-status |  |  | checkpoint | PVC Pipework installed as per Drawing
text | b2cc7707-5c16-5a50-8a57-ddc319c43569 |  | textbox | Installation done by:
checkpoint-status |  |  | checkpoint | Correct PVC Glue used on pipe work
checkpoint-status |  |  | checkpoint | Correct hanger spacing
checkpoint-status |  |  | checkpoint | All materials are in accordance with applicable AS/NZ standard
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed