## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | GFPS-AU - Electrofusion Installation Checklist | [5 empty] | GFPS-AU - Electrofusion Installation Checklist
section | Details
checkpoint | Details:
textbox | Project Name
date | Installation Date
textbox | Welder’s Name
textbox | Welder’s ID
textbox | Company Name
textbox | Pipe Brand
date | Pipe Date
textbox | Welding Machine Model
textbox | Welding Machine S/N
textbox | Fitting Brand
textbox | Fitting Batch No.
radio | Is the machine calibrated? (please select) | Yes,No
section | 1. Clean pipe surface
checkpoint | Weather Concerns:
button | Rainy? | Yes,No
button | Windy? | Yes,No
checkpoint | Environmental Concerns:
button | Clay, dirt, bentonite etc. present? | Yes,No
checkpoint | Wash pipe with clean water and clean rag.
section | 2. Pipe inspection
checkpoint | 2.1 Dimensions
label | Tooling: use Diameter / Pi tape to measure.
textbox | ○ Pipe OD: |  |  | mm
textbox | ○ Pipe SDR:
textbox | ○ Min OD: |  |  | mm
textbox | ○ Max OD: |  |  | mm
label | Reject under-size pipe.
checkpoint | 2.2 Pipe Surface
button | ○ Check for flat spots, using an ovality gauge: | Yes,No
label | If Yes, reject all pipes with flat spots.
label | ○ Pipe gouges or damaged: reject or cut pipe
checkpoint | 2.3 Pipe Ovality
label | Must use re-rounding tools, if ovality exceeds:
label | ○ 3mm or 1.5%xDN for pipe ≤ 315mm OD
label | ○ 5mm or 1%x DN for pipe ≥ 355 -800mm OD
checkpoint | 2.4 Pipe Reversion
label | Check pipe end reversion using a steel ruler or sprit level (straight edge).
label | Pipe ends with toe-in (tapered edge) must be cut off.
section | 3. Square pipe end
checkpoint | 3.1 Cut pipe square at 90° angle, checked using a builders square.
checkpoint | 3.2 Use deburring tool to remove swarf and sharp edges from the pipe end.
section | 4. PE Fitting inspection
checkpoint | PE Fitting inspection
textbox | Fitting’s SDR:
button | Check SDR Range / Pipe Compatibility: | Yes,No
textbox | Fitting Resistance (Ohms):
section | 5. Pipe peeling length
checkpoint | Measure half the length of the fitting, plus an additional 20 mm and mark on the pipe.
checkpoint | Pipe peeling length
textbox | (half length of the fitting) + 20mm (pipe peeling length) = |  |  | mm ¦ mm
section | 6. Peel pipe: minimum 2 peels CRITICAL FACTOR Use GF Rotary Peeler to ensure the peeling quality.
checkpoint | 6.1 Check: The peeling tool blade is sharp. Replace the blade if necessary.
label | Measure 1st peel thickness.
checkpoint | 6.2 Measure peel strip thickness with Micrometre or Vernier Callipers (+0.01 mm tolerance)
label | ○ d63-d315 Pipe: 0.3 - 0.5mm
label | ○ >d315 Pipe: 0.4-0.6mm
label | Measure 2nd peel thickness.
checkpoint | 6.3 Never peel more than the minimum peeled pipe OD, as mea- sured using Diameter tape.
checkpoint | 6.4 Peeling records:
label | ○ 1st peel: |  |  | mm
label | ○ 2nd peel: |  |  | mm
label | ○ 3rd peel: |  |  | mm (if necessary)
label | ○ 4th peel: |  |  | mm (if necessary)
section | 7. Clean peeled area only, using manufacturer approved > 90% Alcohol wipes
checkpoint | 7.1 Only wipe inside the peeled zone to prevent introducing contamination, outside the unpeeled area.
label | CRITICAL FACTOR
checkpoint | 7.2 Wipe away from the pipe end in one direction - not back and forth.
checkpoint | 7.3 Alcohol solution must ful- ly evaporate / flash off prior to joint assembly.
section | 8. Mark pipe insertion depth
checkpoint | 8.1 Using a marking pen, measure half the length of the fitting.
checkpoint | 8.2 Measure and mark the pipe end, at 4 points around the pipe circumference.
checkpoint | If necessary, pipe reround- ing clamps can be installed at the pipe insertion depth mark.
section | 9. Insert pipe into fitting and check annular gap, with align- ment clamps fitted
checkpoint | 9.1 Note gaps?
textbox | If Yes, how big is the gap? |  |  | mm
checkpoint | 9.2 Check: annular gap should be evenly distributed around the socket mouth.
checkpoint | Straightening clamps can be used when pipe curvature (i.e. coiled pipe) prevents smooth insertion into the fitting, including prevention of pipe misalignment.
section | 10. Electrofusion Welding
checkpoint | Electrofusion Welding
button | ○ Is manufacturer’s welding time completed? | Yes,No
button | ○ Are there any Welding Machine Error Message? | Yes,No
textbox | If Yes, what are the error messages?
checkpoint | DO NOT remove alignment clamps until cooling time elapses:
checkpoint | Is manufacturer’s cooling time completed?
section | 11. Post Weld Inspection
checkpoint | 11.1 Inspect the fitting to ensure molten polymer has not extruded from the socket mouth, or visible heating wires displaced between the joint annular gap.
checkpoint | 11.2 Check that the melt fusion indicator pins have fully risen.
checkpoint | 11.3 Check the pipe has not moved during welding by ensuring the insertion depth mark is in the same position as marked on the pipe surface during joint assembly.