## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | FHC-ITP-023 - Conduit, Pit & OCS Installation | itp |  |  |  |  | FHC-ITP-023 - Conduit, Pit & OCS Installation Rev2
section | Preliminary Works
checkpoint | 1.1 Check for correct documentation
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: Ensure that all employees and subcontractors are:
label | — using the correct and complete set of drawings
label | — all drawings are the latest revision
label | REFERENCE DOCUMENTS: Drawings and drawing registers
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed off
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 1.2 Implementation of all measures and controls
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: All necessary measures and controls are being implemented, that is: OHSCP, PHSCP, PCMP, EMP, ECP, CEMP, ERA, QMP, CHMP, SWMS
label | REFERENCE DOCUMENTS: OHSCP, PHSCP, PCMP, EMP, ECP, CEMP, ERA, QMP, CHMP, SWMS
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: This ITP signed off
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 1.3 Materials
label | FREQUENCY: Per Batch
label | ACCEPTANCE CRITERIA: Carpark Lighting A pit is to be installed adjacent to each lighting pole with 1 x 80mm HD conduit installed between pit and the pole mounting base.
label | ○ Electrical supply conduit all conduits for underground mains shall be heavy duty 'Orange' underground category PVC pipe complying with the most recent issue of AS/NZS 3000 Australia/New Zealand Wiring Rules.
label | ○ Communications conduit to be white 50 HD PVC conduits and 100 HD PVC conduits
label | ○ Camera mounting poles and structures shall meet AS47806.2 (2006) Section 5.4.1 (k)
label | ○ Cable pit lids shall be VicRoads type approved, impressed with 'VicRoads' and 'Electrical', 'Communication', 'Traffic signals" as appropriate as per VicRoads Standard Drawing TC-1220
label | ○ All equipment labelling to comply with requirements of NIST-013.4
label | ○ Cable pits shall be 435mm dia x 550mm deep, Type 43 plastic HDPE – Aco Cablemate cable pit with concrete lid or equivalent
label | REFERENCE DOCUMENTS: IFC Drawings
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer, Electrical Subcontractor
textbox | Date Completed:
section | Construction Works
checkpoint | 2.1 Survey set-out
label | FREQUENCY: As required
label | ACCEPTANCE CRITERIA: Work is set out in accordance with drawings.
label | REFERENCE DOCUMENTS: Work procedure, Drawings
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 2.2 Excavation/Boring & Trenching
label | FREQUENCY: Prior to Backfill
label | ACCEPTANCE CRITERIA: Trenches shall be excavated to a depth required to achieve the specified depth of cover and drainage slope, plus an over-excavation of approximately 50 mm to allow for bedding sand. The width of trenches shall be as required to fit all the conduits and pipes for services sharing the trench with specified separations, plus a further 50 mm minimum clearance from the outermost pipes or conduits.
label | ○ Where trenches are excavated across roadways, car parks or paved areas, the trench shall be backfilled with Class 2 crushed rock. The crushed rock shall be placed in layers not exceeding 150mm finished depth and compacted to a minimum of 98% of modified density.
label | REFERENCE DOCUMENTS: L1-CHE-STD-077 Sect 6.10.6
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | HP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.3 Installation of Pit and Conduits
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Underground conduits shall have a minimum of 750mm cover for single and dual-conduit trenches, and 650mm for tri or quad-conduit trenches.
label | ○ Multiple conduit entry penetration holes on a pit wall shall be spaced at least 50 mm apart in horizontal and vertical planes
label | REFERENCE DOCUMENTS: L1-CHE-STD-077 Sect 6.9 IFC Drawings
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed WP
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 2.4 Back Fill of Trenches (Trafficable)
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Bedding: 5mm dust as per MA-FLH-MA-000374
label | ○ Backfill: VicRoads 20mm class two crushed concrete base compacted to 98% of modified density in 150mm thick layers
label | REFERENCE DOCUMENTS: L1-CHE-SPE-313 IFC Drawings
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | WP/ IP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 2.5 Back Fill of Trenches (Non Trafficable)
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Bedding: 5mm dust as per MA-FLH-MA-000374
label | ○ Back Filling: Site or imported material containing no more than 20% mass of rock fragments with size between 75-150mm with no rock or clay fragments greater than 150mm.
label | REFERENCE DOCUMENTS: L1-CHE-SPE-313 IFC Drawings
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | WP/IP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 2.6 Installation of Draw Cords
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: A draw wire of 6mm polypropylene blue/yellow rope shall be placed in each pipe and suitably anchored at each end. Pipe ends shall be sealed using pipe end caps or an approved equivalent to prevent the ingress of dirt or sludge into the pipes.
label | REFERENCE DOCUMENTS: NIST-012 Sect 7.12(d)
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 2.7 Installation of Marker Tape
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: A 75 mm wide orange coloured PVC marker tape with the words “WARNING BURIED ELECTRICAL CABLES” shall be installed in all trenches at 200-250 mm above conduits.
label | REFERENCE DOCUMENTS: IFC Drawings
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 2.8 Cable Pits & Pit Lids
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Cable pits constructed and installed as per drawings
label | ○ Pits shall be placed at each horizontal change in direction or at spacing no greater than 100m
label | ○ Seperate pits shall be used for power conduits (orange) and communications (white).
label | REFERENCE DOCUMENTS: Lighting and OCS Pit Schedules
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
section | Completion
checkpoint | 3.1 Cleaning of Site
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: All obselete cabling to be removed during installation and disposed of appropriately.
label | ○ Upon removal of all redundant signalling equipment; the site shall be cleared of all project scrap and associated rubbish.
label | REFERENCE DOCUMENTS:
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 3.2 Recording/As Built
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: As-built drawings will be completed by the Contractor based upon the installed system by a process of editing the approved ‘for construction’ drawings, as well as survey records.
label | REFERENCE DOCUMENTS:
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed, As Built Drawing, Red Pen Markup
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | Final Inspection
note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
textbox | Date: