## Master List Templates
Id | Type | Name | Values | Prompting Name
fdca44a3-a610-4a4a-a0ea-7da07a734c72 | checklist | Communications - Cabinet |  | Cabinet
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
a6b5c039-9104-4d59-ab1d-6bfb5762edd5 | checkpoint | Confirm rack has been earthed
83c98af0-89bb-42b3-871e-fe93cc9cd729 | checkpoint | Confirm cabinet has seismic fixings and bayed together.
0a237f42-78de-4a32-b6a8-8d1d0024fc3d | checkpoint | Confirm cable management installed
c1084f6e-3980-4a5c-8269-2e82fcc13c33 | checkpoint | Confirm cabinet has asset managed label on front and rear
cc59b323-0b74-425c-8606-50e8f1820b7c | checkpoint | Confirm Cabinet is correct orientation
7ea45823-f0f0-4797-a3d6-e4ef97ffaa13 | checkpoint | Confirm PDU-A and PDU-B are on correct side and plugged into correct power supply
2ff22c34-eb26-4df6-afa8-2ad76c2cc4a7 | signoff | Checked By (Heyday/MDE):
b1832b7a-a98e-4f92-936f-06626789fef8 | checklist | Communications - Copper |  | Copper
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
76c3fe8f-3ddc-4a5e-a05c-ba977ab9a969 | checkpoint | Cabling is not susceptible to mechanical damage.
e18f9918-2b47-40e2-91f9-5482c3f7b9ec | checkpoint | Cable is dressed on the cable pathways with velcro.
eee317b7-8f5b-4eb2-883e-61d2e1a00f59 | checkpoint | Apply a plastic wrap printed label to each end of the cable.
2f3a1f84-388b-47df-90de-dde96ff660f7 | checkpoint | Cable is terminated into a faceplate or surface mount block.
78caadc4-7dd4-4b82-a55a-b5670488ad92 | checkpoint | Cable is terminated into the correct patch panel reflected in the communication cabinet elevations.
fe7c9542-22b6-49bb-8910-c5e9721757f7 | checkpoint | The patch panel, faceplate/surface mount block are labelled correctly with a traffolyte.
dfbecaf3-200a-4be9-8412-b04a17a436d1 | signoff | Checked By (Heyday/MDE):
d80c0715-f329-4661-9a44-68e4b5a51855 | checklist | Communications - Fibre |  | Fibre
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
e2737053-d94a-48c5-b40d-ea6cb9f0e5d8 | checkpoint | Cabling is not susceptible to mechanical damage.
c283b042-76d5-463a-8cca-eae28e34775a | checkpoint | Cable is dressed on the cable pathways with velcro.
0f151bed-084f-43d3-bbb6-d3158693983c | checkpoint | Apply a plastic traffolyte label to each end of the cable.
434d0ada-b213-43de-a343-48e2bdb3bafb | checkpoint | Fibre optic reticulates into cabinet correctly and is terminated into fobot.
361e5676-c9be-450d-b966-9efe3d620a60 | checkpoint | Fobots is labelled correctly with traffolyte.
716f9a14-a9e5-4c50-ad9f-89cc55535c35 | signoff | Checked By (Heyday/MDE):
df71fccc-889f-4250-bc86-4df129d6a8ae | checklist | LOT BREAK UP |  | LOT BREAK UP
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
dcdf5328-e886-4cde-95f0-59dde8dc5444 | checkpoint | Attached Mark up of Lot Breakup
3ca3689f-77c0-48c2-ab24-e1d735cf09e7 | checklist | Testing & Commissioning - 3 Phase Subcircuit |  | 3 Phase Subcircuit
861fd99c-dca8-43d2-8e4b-f8409081293a | section | Pre-requisite Works
6da69891-19bb-46f6-a2d4-9b9cf3d8e4bc | checkpoint | Insulation Damage
7225f360-ac04-4778-95db-9dbcc07e76ac | checkpoint | Correct Type of Termination
3971722c-baa9-43a9-aa06-c86c6056edfb | checkpoint | Correct Colour Code
9708cbf1-ec02-4027-9710-1f71e383629d | checkpoint | Correct Outlet Rating and Size
e327169b-3ebd-4006-adbb-d344cb7384ca | checkpoint | Earth Continuity
d1fad654-d6b7-5aaa-ad18-5ced852d1212 | textbox | Resistance (Ω)
21706f16-3e14-4132-869a-39878965623e | checkpoint | Polarity Check
a878f000-c1ad-5c8c-917d-0e62e1a0e5c2 | button | No Transposition | YES,NO
b8ec0463-70f4-5599-97fb-21e80b4abc49 | button | Switch in Active | YES,NO
e3cc3ac1-4360-4fb6-a0db-9fd6969e809e | signoff | Checked By (Heyday):
9cac9730-f4a3-4380-b5fb-b44eee12d42e | section | Insulation Resistance
96dd6692-f9e5-4dbd-8b51-64a37deb1e6e | checkpoint | R-W
2b39491a-1d6a-511a-82f4-71cfabd13a8c | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
d348ccc8-6968-5dae-a021-9c9ceffa5e6f | textbox | Actual Reading if <200MΩ/<500MΩ
f206d7ac-521d-4be4-8f41-eea8e2e1e3bf | checkpoint | R-B
52a2c584-84aa-5609-880b-8300f96e8f5e | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
f9cb7812-44c5-52af-a9b2-3ffb8d4e72a6 | textbox | Actual Reading if <200MΩ/<500MΩ
882b4c0f-8dcb-4d8c-8881-b4c7b13c157a | checkpoint | W-B
c6af3168-67a5-5e0e-935f-deba5b39563d | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
92fa960a-d385-55d2-a305-6489a079a3f0 | textbox | Actual Reading if <200MΩ/<500MΩ
8ed72945-9322-49ab-879b-2450c3ad8f68 | checkpoint | R-N
f3510836-c94f-5348-bc00-0fe3bd323739 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
8f7cadda-8d23-53d8-af25-7ee29ed9e6e2 | textbox | Actual Reading if <200MΩ/<500MΩ
3ce7661c-5fca-41d4-a5a5-790a3a4b01c6 | checkpoint | W-N
4037876f-d6e5-5dbc-9a61-0e8ea3923279 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
d477f3c7-aa58-5755-aa05-0b066a1b7cef | textbox | Actual Reading if <200MΩ/<500MΩ
9651f12e-c9a4-442d-bc8c-f11c854fa56e | checkpoint | B-N
4605fcfd-7b25-5173-a9e7-a07339fd902c | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
a0128354-5305-5bf4-8282-5f7a8295fc7f | textbox | Actual Reading if <200MΩ/<500MΩ
6e4631a7-7c3b-405e-ab1b-9f82b89f9fd9 | checkpoint | R-E
c64a6297-5d59-5b92-87a9-d2b62a3fbf04 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
144b208d-ae23-5be7-9e51-128cf9d3dcc2 | textbox | Actual Reading if <200MΩ/<500MΩ
0fccc83f-b50d-4cc0-a288-d4c98f56d0fd | checkpoint | W-E
a0b931b0-76eb-54d1-bfa0-459efcda5dcf | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
84054121-9153-5416-93f7-c6d93908d8d6 | textbox | Actual Reading if <200MΩ/<500MΩ
fc799b05-5f47-4321-a8db-0c227ad69d10 | checkpoint | B-E
729c09c8-067e-5ce3-8113-46aaef757ae0 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
f51bf965-727e-5964-8a37-3fb5928b1a41 | textbox | Actual Reading if <200MΩ/<500MΩ
827f6e60-be17-4eca-9c30-2c54ef6f95c4 | checkpoint | N-E
977a6a16-6d9e-51d3-9adc-0d181d6c3fed | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
22efc18d-777c-5ae2-9787-29ab2333ca6e | textbox | Actual Reading if <200MΩ/<500MΩ
b89d6cb3-d1ef-4cc8-a496-2c4d55ed41be | signoff | Checked By (Heyday):
e60f69f2-5a59-44f0-8566-b462615f9a6b | section | Voltage
cac5f44a-a6bc-43b1-bc53-f27a0da64f14 | checkpoint | Red - White
d4f6e39a-cf4b-52ba-bdcb-be3fcffe2da4 | textbox | Voltage (V)
04166c8d-957b-4eff-8864-5075cad5d374 | checkpoint | Red - Blue
c2419cc4-d59c-522d-bc84-c1b9e086ff6d | textbox | Voltage (V)
8d39a288-efcc-46a4-94b9-e7db2c44ff87 | checkpoint | White - Blue
b6a6b526-117f-5e79-8caf-03a2f65b3c2c | textbox | Voltage (V)
37f3f198-3fa3-4e3c-8adc-2d6c6cbb04a1 | checkpoint | Red - Neutral
84e20906-51b7-5586-ba8a-2d4a0116eb57 | textbox | Voltage (V)
ba9cca36-b89a-4d4e-91ec-08c54b9d4d4d | checkpoint | White - Neutral
5b8dd4b2-2a55-5141-8932-7780c4377448 | textbox | Voltage (V)
105d0dae-3ddb-45ad-8b9a-83a2318b7f89 | checkpoint | Blue - Neutral
d043e074-431b-5586-a349-5e7e8b33c605 | textbox | Voltage (V)
f2f49762-0dc4-40de-95b0-61b04776d6e4 | checkpoint | Red - Earth
d88e464b-bed5-5f0c-af21-50d796bb2403 | textbox | Voltage (V)
2d1255f8-a0dd-4086-9488-3b81ccfe8362 | checkpoint | White - Earth
525be556-c6cd-5964-97e9-9b8c22e9604b | textbox | Voltage (V)
f436332f-ea9d-4c26-baaf-6498f0980e05 | checkpoint | Blue - Earth
a12e795b-46a0-5ee2-be31-e824ee9c758c | textbox | Voltage (V)
1b183ac1-3850-4d0e-9f9b-fbd8162a88e1 | signoff | Checked By (Heyday):
4bb0e1c9-4368-4df3-bb6e-c9fb61376ee0 | section | Earth Fault Loop Impedance Test / RCD-RCBO Tripping Test
b0df5f2e-1ff1-49a7-8eba-c133f962acfe | checkpoint | Impedance - (N/A if the circuit is RCD Protected)
b044fe0b-852f-5b44-844f-169a2ebc699d | textbox | Record Inpedance (Ω)
b93650ce-1006-567a-bce0-c07128c7e1cf | textbox | Target Impedance (Ω)
79eb7072-a04e-4b6a-85e5-30b4b5f2109d | checkpoint | RCD-RCBO Tripping Test
abf38619-a914-59e4-97ed-521a8167c7c6 | textbox | Trip Current (mA)
273439a4-eb3c-5eaa-b343-12c237a4b61d | textbox | Trip Time (ms)
6aa7fba7-6aac-4dd5-a301-11e58a52dfb3 | signoff | Checked By (Heyday):
c4fab001-6d7f-4e61-9514-e45467024253 | checklist | Testing & Commissioning - Communications Cabling |  | Communications Cabling
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
55d94b5c-3689-4cb2-8f73-9160690a51be | checkpoint | Cable installed to Manufacturers requirements
f4a63d89-7085-4de9-a646-9ff3b5e2c2b7 | checkpoint | Cable Labelled
57b1b891-a26a-4284-b199-006ddec485d7 | checkpoint | Cable Terminated
0b118d6f-2240-4905-9767-72c4a3c64569 | checkpoint | Cable Tested
61d91b88-697a-4bdc-a7a3-1d7e495d395f | checkpoint | As-Builts reflects installed Cable Number and Location
86dbe344-1f18-4c57-9799-284e4f4985ac | signoff | Checked By (Heyday):
075cbb8f-7395-4215-990a-36ee8f123766 | checklist | Testing & Commissioning - Distribution Boards (Energised) |  | Distribution Boards (Energised)
ac8d2b3a-1062-4805-9ee2-f6ed983b5857 | section | Phase Voltage Reading
a53ff1c6-2797-40a2-a2f8-f7d38489ecdc | checkpoint | Red - White
41085b71-2ea6-5b63-a473-f908e40c84db | textbox | Voltage (V)
16a098d4-cc95-4d40-b7f2-5a6f971a8dae | checkpoint | Red - Blue
196e18ef-44d6-5e0c-a2a1-3e123df518ec | textbox | Voltage (V)
5f5f3b6a-f863-41d2-b2f2-ae73ae753490 | checkpoint | White - Blue
dd4fb89a-49d2-5cb5-81f7-9353800034b4 | textbox | Voltage (V)
2c7982e1-caca-49f5-b608-0d810e12fc87 | checkpoint | Red - Neutral
84ea402e-0a70-5ef7-875a-b3d7242e3e72 | textbox | Voltage (V)
23082f5e-1a0c-4b41-87eb-0d83fd061e60 | checkpoint | White - Neutral
3559dc80-e4b9-529a-b961-94b338fdf2a5 | textbox | Voltage (V)
d20cf236-03c4-48ec-bb3d-a76d4c0a7931 | checkpoint | Blue - Neutral
b5c0d298-c429-55a3-b066-19c0ef1adec4 | textbox | Voltage (V)
828bffa7-26e3-4c1a-9bae-5901fdb6fa71 | checkpoint | Red - Earth
5e97d0e2-e2ab-5fd5-b47a-2336dfd51118 | textbox | Voltage (V)
1258b1f5-490b-4bed-a1f2-aa12c5f28b2c | checkpoint | White - Earth
ac623e8d-cf6b-505d-bb88-361d6a1997e1 | textbox | Voltage (V)
5b1ac89f-0558-43f0-863a-940529d8515e | checkpoint | Blue - Earth
3970221d-9189-52b1-8a60-1654c34deea7 | textbox | Voltage (V)
ea11a561-9fd9-4f60-b0f1-50cf897b2eaf | signoff | Checked By (Heyday):
2817d947-17af-4959-86d2-ad261376d5c6 | section | Phase Rotation
b88f8ba0-5ca0-416a-833c-5540c7146713 | checkpoint | Direction
ae1d7739-bc6e-5e73-89bd-a6284a3ee7fb | button | Direction | Clockwise,Anti-Clockwise
60203d98-7d92-49d7-941d-68aecd92f89d | signoff | Checked By (Heyday):
ab447333-a299-4292-8db0-7bf6f22c0c5a | checklist | Testing & Commissioning - Distribution Boards (Pre-Energisation) |  | Distribution Boards (Pre-Energisation)
8977fb2d-d688-4cf3-ba87-cb3b8fa58f11 | section | Physical Checks
53931865-a78a-45ab-97ba-c708723ce19b | checkpoint | Confirm board's dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section)
406cc207-1337-4249-b626-ad3c99a32f08 | checkpoint | Confirm correct circuit identification and labelling
9fe77cb5-17a2-4cbd-986f-6b77e11a3212 | checkpoint | Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in the Comment section
803faee4-c37d-40fe-9c85-2e74fc369c5b | checkpoint | Confirm correct phase identification of busbars and cables inside the board
47ec17c8-ae92-4b4d-866c-ff0d9ea6aee2 | checkpoint | Confirm correct size of earthing conductors
63b54de8-ad3b-41d3-a0f3-fc5241186aa9 | checkpoint | Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
a2e1e634-debc-4435-a180-231056e71a2d | signoff | Checked By (Heyday):
64c1c2c8-43ed-4fd4-bb5b-5d012ed1db54 | section | Mechanical Checks
cf8b9aa7-08fd-4c0e-91c8-cbb9f004a809 | checkpoint | Repeat manual closing and opening of moulded case circuit breakers for 3 times
49cfc303-218e-487c-81da-99c451f007b0 | checkpoint | Repeat manual closing and opening of miniature circuit breakers for 3 times
bcb84516-3183-41b4-96f5-4fce85c25419 | checkpoint | Repeat mounting and dismounting of power fuses for 1 time
aa08c339-65f9-48dd-bb4c-bcb7bb3ecc17 | checkpoint | Repeat mounting and dismounting of control fuses 1 time
bc551d4c-f188-4b41-92fa-cc1e5bb9ac39 | checkpoint | Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards.
48adfc55-5257-4635-a37d-8aaa1cdb361a | checkpoint | Conduct pull test for all cables connected to MCBs and Termination blocks
9d255614-8493-4ed6-8960-67d13c4bee8c | signoff | Checked By (Heyday):
21404c63-9e24-472c-9e6b-fcff18e7f796 | section | Preliminary Checks
28c77213-b2ae-49b2-8713-4e8526be9db4 | checkpoint | 1. Confirm all fuses Removed in board’s Control Sections
8dfbd3cf-e1f3-4186-92f7-84d6786be3cd | checkpoint | 2. Confirm Main Breaker Closed
19f52456-4a04-4556-af92-67733c2ddd7c | checkpoint | 3. Confirm Outgoing Breakers Closed
becadeaf-a4c6-4c17-9c3d-18902626e1eb | signoff | Checked By (Heyday):
bdf6c1bc-a00d-4ab5-9aff-1bbba6598c13 | section | Insulation Resistance (500V)
95780f93-e76b-4d2f-9976-285f8da63ae6 | checkpoint | 1. Between L1 Phase and Neutral
d13d1e56-7dcb-5e3a-9b5c-a0177a9b705e | button | >10MΩ | YES,NO
acb50fa4-ec67-553a-ac17-a3c84289aef3 | textbox | Actual Reading if <10MΩ
97429c4d-a75b-43ac-b3d6-8e93dea59342 | checkpoint | 2. Between L2 Phase and Neutral
b536bc25-10c9-5f2b-b54e-2d017764b346 | button | >10MΩ | YES,NO
fbc00ebb-87e0-5b6b-b6ea-a7b87cda5dde | textbox | Actual Reading if <10MΩ
56504dc8-adab-47d4-b32b-f0ef6bf26930 | checkpoint | 3. Between L3 Phase and Neutral
bf84e43c-e7a0-5de6-8d9d-eaaa028eb099 | button | >10MΩ | YES,NO
21adcd4d-6cbf-5f5e-b8a8-b96d7ba516f5 | textbox | Actual Reading if <10MΩ
59e61667-dcdb-4fdf-a339-2e207b35bcbb | checkpoint | 4. Between Neutral and Earth
a7c183bc-5dac-5983-b295-3010e75cbb96 | button | >10MΩ | YES,NO
a7e77f7f-29c5-518c-9001-05d65d66e0fa | textbox | Actual Reading if <10MΩ
555ad5dc-50ed-4de6-bb8e-e1c1569a6e90 | checkpoint | 5. Between L1 Phase and Earth
baf66c08-1e2a-5e9b-92bf-4c4497f8506c | button | >10MΩ | YES,NO
a613c700-5f1c-5268-b5ff-dd5877585430 | textbox | Actual Reading if <10MΩ
758028f6-f6fa-43eb-906b-ad9ba25d281f | checkpoint | 6. Between L2 Phase and Earth
1429255c-7841-56ad-8697-2c6d159d4785 | button | >10MΩ | YES,NO
3cb29882-53f7-571c-a986-60f07c038d4a | textbox | Actual Reading if <10MΩ
7d0031ee-ffd7-418b-8ad9-32353aca2e22 | checkpoint | 7. Between L3 Phase and Earth
6b34d913-698f-543f-acbd-b15ce2393323 | button | >10MΩ | YES,NO
eca5e2f2-4f96-54a4-bd9c-d773ef32d661 | textbox | Actual Reading if <10MΩ
95d05598-ce63-4609-bc1e-50944d2c5aac | checkpoint | 8. Between L1 Phase and L2 Phase
f2d0ded0-11dc-5ed7-b174-7ae1e1f2de7f | button | >10MΩ | YES,NO
409049d8-bf8e-5277-b9d3-092b1ed58bf4 | textbox | Actual Reading if <10MΩ
f5ff6e4a-a62f-4e95-aea1-04b18472b68c | checkpoint | 9. Between L1 Phase and L3 Phase
062ccca4-0713-55fd-a25e-95a99c06db87 | button | >10MΩ | YES,NO
94d30298-de90-5b38-bbbd-e6d83151d789 | textbox | Actual Reading if <10MΩ
bb98cdd5-869c-44eb-8f53-98f3bc74dcc8 | checkpoint | 10. Between L2 Phase and L3 Phase
bb2650ae-08aa-536f-bfd8-7ae3895db90c | button | >10MΩ | YES,NO
eabaa815-6458-54b1-aa8c-0d477e6c4d97 | textbox | Actual Reading if <10MΩ
6b866b55-c275-4004-8a3f-20fffb08a5f8 | signoff | Checked By (Heyday):
7ce3d526-d0f2-46a6-919a-831e9e8f6dd5 | section | Earth Continuity Test
f3e1e57e-5bd1-4798-b4c6-f29e27628b90 | checkpoint | Earth Continuity
2a6ea1f6-c5ff-500e-9214-32679eb3c7c6 | textbox | Resistance (Ω) - [Target: <0.5Ω]
504d9245-321d-489c-a665-632a21902d0d | signoff | Checked By (Heyday):
36c84e5b-0495-4dfc-b941-3b128d44482c | checklist | Testing & Commissioning - Earthing Systems - Construction Tests (Earth System Reticulation) |  | Earthing Systems - Construction Tests (Earth System Reticulation)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
5d791298-49e3-4116-b523-c359d010f8b6 | checkpoint | Correct Cable Size and Labelling
3124bc43-3fc7-4493-9eea-108a575e2ae1 | checkpoint | Earth Continuity
c5ad7585-699d-581b-8267-c3d24da56d0e | textbox | Resistance (Ω)
e8f761bb-2760-541e-b5ec-9156d4f317ce | textbox | Target Resistance (Ω)
5c7272eb-5012-417d-9440-1e7547cbd7b6 | signoff | Checked By (Heyday):
cae18be9-29d2-43c5-a730-ba3a912fa0c5 | checklist | Testing & Commissioning - Earthing Systems - Construction Tests (Main Earth System) |  | Earthing Systems - Construction Tests (Main Earth System)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d269a52a-29a7-45f0-ade5-97796ceae758 | checkpoint | RWV Industries – Earthing Test Report. Steel Reinforcement Continuity
aa286d59-6b01-4cdd-895a-a4bae9404a65 | checkpoint | RWV Industries – Earthing Test Report. Footing Earthing
8d60bbbe-1ea3-4ffc-acc6-cc9659a95a68 | checklist | Testing & Commissioning - Emergency Lighting |  | Emergency Lighting
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
c2dfcdbf-2955-419d-b108-ffede429bf4f | checkpoint | Pre-requisite Works
22880dd4-2579-4d39-b8c9-957b8934c66f | checkpoint | Correct Location & Labelling
919b553b-f5f3-4c09-8f17-9d5c2b61169a | checkpoint | Correct Software Mapping
bc6f4cea-40bb-4efd-b470-b4392c182cc9 | checkpoint | Discharge Autonomy Test
e7af81ef-61e0-4cde-9f0b-c1aae177aa04 | signoff | Checked By (Heyday):
4f516721-9264-4603-a113-5d0c70e71377 | checklist | Testing & Commissioning - Lighting Control |  | Lighting Control
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
8c82fdbe-8112-4b24-8d84-0462942894a2 | checkpoint | Pre-requisite Works
f6adb625-199d-424f-91ee-be65f1df8ba3 | checkpoint | Correct Location & Labelling
857c855a-81e6-4de5-a16a-74858e79f3c5 | checkpoint | Manual Control
e0ecd3a3-ac7c-4d58-81db-b765f2d3fefa | checkpoint | Occupancy Sensor or PE Cell Control
420e3ac5-6120-45c2-9561-ce56de03204b | signoff | Checked By (Heyday):
0ab4814e-ddcd-49f8-8d06-d7ee539439a5 | checklist | Testing & Commissioning - Low Voltage Busduct (Energised) |  | Low Voltage Busduct (Energised)
56b517ed-d914-41f2-96a7-965ae9efdff1 | section | Phase Rotation
4c6ab7d8-e371-4454-b5bd-85d1fc9e87e2 | checkpoint | Direction
a30d2ede-1096-5c42-975d-8a1be371ca17 | button | Direction | Clockwise,Anti-Clockwise
fa9a7ff6-7c7a-431a-983e-756bb25dea55 | signoff | Checked By (Heyday):
8e265440-c473-440d-a516-0359dd4e6393 | section | Voltage
94d46092-4876-4725-b9f8-5d7434200652 | checkpoint | Red - White
4acfc2d5-d4cd-5a9e-a48e-4556de77b138 | textbox | Voltage (V)
cea9d429-b75d-431a-85a7-aa3358f67df3 | checkpoint | Red - Blue
33b3e158-b999-558b-8219-4378cabaf116 | textbox | Voltage (V)
f78d8e9d-64fb-4a16-9fee-f2eae06c45c3 | checkpoint | White - Blue
3aa40e1d-b21a-5f71-8fac-e8968bdbf5e1 | textbox | Voltage (V)
1898309a-844d-4694-b4ce-867734163b9e | checkpoint | Red - Neutral
f5241f11-686a-59f5-9ff4-cfdbe0b920e4 | textbox | Voltage (V)
9fe0a72a-67fd-4f6d-b4bc-657002c5487f | checkpoint | White - Neutral
1e87b879-5ba3-5d4b-825b-a059e4ff959c | textbox | Voltage (V)
d5eb50a9-bf63-4c23-82f2-2807888f24dd | checkpoint | Blue - Neutral
bf6b7655-9c2e-5ff2-9973-938cf3c6aaf6 | textbox | Voltage (V)
5659b85a-684e-49c6-9618-92a793aea502 | checkpoint | Red - Earth
2b3b47e3-65cb-5550-b872-92b0c10c686f | textbox | Voltage (V)
747676ca-124e-403e-9c65-c5ba6e57922d | checkpoint | White - Earth
1f5ad7ba-1296-50a3-8a73-943d46b0379a | textbox | Voltage (V)
a24327c9-3e70-4ccc-bb76-6fd489037fda | checkpoint | Blue - Earth
b045f50e-7da0-5ed0-af29-d3fad1980b0c | textbox | Voltage (V)
4d8d5f35-7891-47d0-8ebd-e1cb5724390f | signoff | Checked By (Heyday):
13cf0cf9-c3da-4e9c-bb52-18cc0215eece | checklist | Testing & Commissioning - Low Voltage Busduct (Pre-Energisation) |  | Low Voltage Busduct (Pre-Energisation)
2683ac7d-d83d-434f-86db-4bc68ec544c8 | section | Pre-requisite Works
6f6e2026-e685-47f6-96eb-26aab5f17835 | checkpoint | Insulation Damage
fbb93c2b-c852-4a57-b3e1-c9ab11a568fc | checkpoint | Correct Type of Termination
cfc0e5d9-f976-494b-9421-9032e5ad627c | checkpoint | Correct Colour Code
4478576e-9436-47da-943e-dbc0c0770867 | checkpoint | Correct Size and Labelling
0af3d548-923b-45c1-9792-4072fb23bf3a | checkpoint | Correct Routing
51ab7f2d-c49f-4573-a2cf-c0918afaaefe | signoff | Checked By (Heyday):
52688ba0-c53b-4ecf-9ceb-ed2c6bea4ef1 | section | Continuity Testing
2bbbeb81-d76f-4ab7-9b37-4af81c15d03e | checkpoint | Red Phase
bccf9913-d1d2-56f3-a607-88c92ed9ccab | textbox | Resistance (Ω)
f6644a85-f277-584c-b823-e4aabc9fe3fa | textbox | Target Resistance (Ω)
fb88138b-a601-468d-a400-b241f2a7d8f1 | checkpoint | White Phase
0b7948c2-7d82-5100-8f1b-4cea01b30f18 | textbox | Resistance (Ω)
66424b14-26aa-5233-a73e-8fa6cc8050f6 | textbox | Target Resistance (Ω)
9c311428-b330-40eb-b40c-1dd67b1725aa | checkpoint | Blue Phase
52743c86-7a1e-5846-9ed4-16d922e5a47a | textbox | Resistance (Ω)
5f38758d-f8b6-51ab-a26e-c74dd36d841b | textbox | Target Resistance (Ω)
b34c5bdc-1be4-4637-b9d2-444cd99281de | checkpoint | Neutral
f370275e-68f7-5955-8861-2dcb1588eb3e | textbox | Resistance (Ω)
585a13f3-7590-5d8a-bbc8-95d5275da47a | textbox | Target Resistance (Ω)
30c50d31-0f05-4055-a918-1ca7a5211171 | checkpoint | Earth
3b368092-9571-5aa2-a2a7-e0730ef000fd | textbox | Resistance (Ω)
b7961f1e-bd19-544e-968b-da79a8efb990 | textbox | Target Resistance (Ω)
16af6e5f-e4ca-481c-a82b-99a40a4ce1fc | signoff | Checked By (Heyday):
fb07be62-3a2f-4f9c-b77d-500cab4e5db9 | section | Insulation Resistance
4b1c9924-2f9e-4a2f-9e95-666cf0fe70da | checkpoint | R-W
71e52e0f-a926-568d-a8cd-a92f6c639b94 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
236615dc-9f7f-5d83-b480-8f4a2ee5b083 | textbox | Actual Reading if <500MΩ/<1000MΩ
40e123b4-db69-43d8-9785-4b395c22ffc5 | checkpoint | R-B
970d468e-6b01-5be9-b3b6-05d5078c0aab | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
33641d8f-e337-533a-a805-87211cbf3a91 | textbox | Actual Reading if <500MΩ/<1000MΩ
8d09ae7e-c911-4b43-af36-414ea08fcce7 | checkpoint | W-B
b3b8d3a8-65a5-5c5d-aeec-ccbf4ea127a9 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
ee127d77-1bf2-5c44-b48e-7269a34edaeb | textbox | Actual Reading if <500MΩ/<1000MΩ
160b2c93-6069-4671-95ba-e72256df6f8b | checkpoint | R-N
bd4e072d-3fcf-52ff-82b9-294e57745273 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
7ec26620-539d-538d-ba0d-db4f4d700f79 | textbox | Actual Reading if <500MΩ/<1000MΩ
2218ed7b-c321-493c-b1f1-41861b0b0a42 | checkpoint | W-N
f2522ff5-f858-50ac-afa5-d36327eba8b7 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
a8e1d7e2-1f9d-5fae-a962-5a9ff4b7e50e | textbox | Actual Reading if <500MΩ/<1000MΩ
a13a077c-4e34-4816-acfd-d56ca034e416 | checkpoint | B-N
e6c30564-7894-53de-84e1-27f305aa7aee | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
53ed9870-e3ff-5a45-9d16-70ec0141be7e | textbox | Actual Reading if <500MΩ/<1000MΩ
55c6628d-118f-484b-8659-a501d45e9040 | checkpoint | R-E
b0dfed67-2b0a-5d94-afbf-b0695936573b | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
1dd8bfc4-1c23-5ce6-8bd8-e776a7524c53 | textbox | Actual Reading if <500MΩ/<1000MΩ
b868133f-b4b3-4beb-a629-a4b3ae5e6ccf | checkpoint | W-E
8f12b33d-2867-5720-809f-451dd09a8a35 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
11d0aeb0-8c74-5805-8a27-3c9ffc096d80 | textbox | Actual Reading if <500MΩ/<1000MΩ
2f1e5474-67ca-4290-a4c0-d0c00ab0fa5f | checkpoint | B-E
91374eda-c96c-52e7-8d39-0ea32572ab8c | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
14a493d0-eeb2-5290-9728-f1b86a8b0eba | textbox | Actual Reading if <500MΩ/<1000MΩ
c9a0cae2-b286-4106-845c-1cc0f3a2c670 | checkpoint | N-E
5c0881ea-f11e-5a26-9ea2-899b372ad1a0 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
9ec664f6-3127-5687-85f9-817771475f51 | textbox | Actual Reading if <500MΩ/<1000MΩ
475fb419-ba6d-4392-acf5-3dc809c6e54a | signoff | Checked By (Heyday):
adf41567-33c7-4edd-a2e3-b2eb8e5ca8a8 | checklist | Testing & Commissioning - Low Voltage Cables - Mains/Submains (Energised) |  | Low Voltage Cables - Mains/Submains (Energised)
2b0dd3a0-2840-4fd7-838c-e64206f9de3f | section | Phase Rotation
a6e4ad7e-ec83-4416-8528-d65f1ab998b5 | checkpoint | Direction
28ea72d6-4a91-5a15-94c5-2854db45b57b | button | Direction | Clockwise,Anti-Clockwise
c26a325e-78ba-45d6-91e6-5860806890c3 | signoff | Checked By (Heyday):
e88e7031-561f-46cd-bbb9-0199c3ac78cb | section | Voltage
86f8e276-da9e-4b97-ba69-9d5b6f4dd122 | checkpoint | Red - White
93653f00-3b32-5550-844e-7b7cf8710501 | textbox | Voltage (V)
6ed9be45-6b56-4b49-87da-ea502410a2e4 | checkpoint | Red - Blue
b368877c-44f2-56ed-8d65-302019e35b3e | textbox | Voltage (V)
db14faf0-0b83-49f8-b05e-3ed90cd33602 | checkpoint | White - Blue
71305fd4-cd21-5a08-90d9-04d103c384bf | textbox | Voltage (V)
b2cb4bf8-69b4-4225-a2f7-6c2d237fc507 | checkpoint | Red - Neutral
50f8d9fd-9169-58b7-8c5c-2ad5568d5af6 | textbox | Voltage (V)
0eb3a0b2-9ab2-43bb-98b4-86a8a5174f99 | checkpoint | White - Neutral
15d9f414-9e57-5b37-8804-20266311e4d0 | textbox | Voltage (V)
b70d7c3e-3add-4007-ad5d-b1ca733190b5 | checkpoint | Blue - Neutral
69e62051-5aa3-5258-8375-5880247be8a5 | textbox | Voltage (V)
8d2bbccf-f4e9-4131-99ab-030da4b330d2 | checkpoint | Red - Earth
85db411d-c77e-5ae5-9482-8871a3b373c5 | textbox | Voltage (V)
0725d234-197f-4880-b767-b9be6da1b33c | checkpoint | White - Earth
58452f28-615b-5268-8df2-6aa3d6bad2f7 | textbox | Voltage (V)
1cfb0202-de30-4657-b8ff-6952e850a957 | checkpoint | Blue - Earth
45e1a898-8aef-5fe6-a258-43e9f2f26db6 | textbox | Voltage (V)
8982ac97-a732-4e66-a639-4970c71168cf | signoff | Checked By (Heyday):
f5b959a8-9496-4502-9f36-3c5ce66f64bc | checklist | Testing & Commissioning - Low Voltage Cables - Mains/Submains (Pre-Energisation) |  | Low Voltage Cables - Mains/Submains (Pre-Energisation)
018edeaf-369d-4f29-b1bf-c91bde4328eb | section | Pre-requisite Works
23f86157-f72b-4ffa-a768-98665b79837f | checkpoint | Insulation Damage
57bacc0d-557a-45ca-93e7-ece22f64ffd4 | checkpoint | Correct Type of Termination
9684c7b9-19a0-48c9-b01a-cccbab0659ff | checkpoint | Correct Cable Size and Labelling
8d721160-3276-4051-aca5-78c3ced57d54 | checkpoint | Earth Nesting
57d6eede-c12c-4a00-be4c-750031f4f70e | section | Insulation Resistance
0cf19de5-79a4-4ab0-8d41-dc57fd701299 | checkpoint | R-W
9a8a942c-c760-54ab-8156-7f923929fb81 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
ce678e18-59f2-501b-974a-b76616a2e263 | textbox | Actual Reading if <500MΩ/<1000MΩ
d4ef7fc9-293d-4bb1-a821-0d89ceace40b | checkpoint | R-B
1c60b3a6-1e7b-5679-9483-48e4dd4f3da1 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
dd511f61-20d5-518f-81f4-fc71cc02430e | textbox | Actual Reading if <500MΩ/<1000MΩ
88eebd9e-2491-41ab-8bc2-7495c59d63f0 | checkpoint | W-B
00092a90-1d66-57c2-9ac1-af0166a8fdba | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
ccd93f11-247b-50bb-8940-faffeea99973 | textbox | Actual Reading if <500MΩ/<1000MΩ
0dbda30a-d146-4689-8032-1a754f027c24 | checkpoint | R-N
c2567637-4493-5346-b1b1-6608d53e6dbe | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
f42ca530-cdd3-5eec-9abc-41f8a9593ad3 | textbox | Actual Reading if <500MΩ/<1000MΩ
30776b3e-d58f-4dc9-bb62-41c38d10f98d | checkpoint | W-N
9e43d7f4-0af4-5ba6-96d7-5ca6707f7408 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
d3ac676d-4354-5beb-9005-912a85b0d966 | textbox | Actual Reading if <500MΩ/<1000MΩ
2970f94b-cb79-43a9-9ea1-b18274f0ac88 | checkpoint | B-N
591d006c-3ed7-56f8-8464-c575b772c723 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
4cc71dfc-b209-54b8-bc83-e89b7f48d10d | textbox | Actual Reading if <500MΩ/<1000MΩ
3d6923be-a1f5-449f-a6e0-8f4ed98390f2 | checkpoint | R-E
c2fab04d-bf8f-581c-b555-5ed80cce206e | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
55cce7c7-7810-582e-8a6b-369795d3b0c6 | textbox | Actual Reading if <500MΩ/<1000MΩ
c9c38127-6fdd-48a2-9520-4253554c02e0 | checkpoint | W-E
06e4a05b-ae5f-5741-8393-5b16751588c6 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
2282f52b-da13-536e-ac5b-4cba786a817b | textbox | Actual Reading if <500MΩ/<1000MΩ
256e178d-ee3e-4d6a-b835-ea77f714c7d4 | checkpoint | B-E
4e9f2bd5-abdc-5f0e-87ca-b8c4ecf750c6 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
75306665-e77b-5cf6-8ce6-a29309f9b014 | textbox | Actual Reading if <500MΩ/<1000MΩ
90b33d64-3d90-45ba-8441-9a370fc4ba0d | checkpoint | N-E
7d47d5a8-e5e5-54b1-bf15-f8deabff2b62 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
71eef9c5-5789-5d90-89ea-0b68c00ea9b5 | textbox | Actual Reading if <500MΩ/<1000MΩ
52006caf-6350-4285-8d32-6a0561fdbfed | section | Continuity Testing
904dd9ec-4232-4529-a23d-9924bf54ff18 | checkpoint | Red Phase
cf4db43d-bd8a-5d5d-8efe-a99fe73bd4d0 | textbox | Resistance (Ω)
bbc273bf-6757-59b2-b065-7b79be06a427 | textbox | Target Resistance (Ω)
8a010c34-ad3f-44f6-b612-187c1b52df72 | checkpoint | White Phase
c53816fc-336b-5f0c-82dc-5a69b57952ab | textbox | Resistance (Ω)
96675194-8fbd-56aa-93d5-0408c0aa5faf | textbox | Target Resistance (Ω)
b3d56b96-05a0-4893-95d7-00bf5811b4fe | checkpoint | Blue Phase
c1062c2d-c386-55f0-99cd-12016163d1ee | textbox | Resistance (Ω)
88f65101-39fd-5748-b7cf-2b25ec17919b | textbox | Target Resistance (Ω)
b5e9a7d4-309f-452f-b5fb-5b1bdeb93dae | checkpoint | Neutral
736f3782-a7c4-588c-acd2-268a4a03e69f | textbox | Resistance (Ω)
615464c5-2962-5723-9c3e-de0d1a961057 | textbox | Target Resistance (Ω)
fbe6cce2-e362-42d8-ac3c-ed5f1e81b0a9 | checkpoint | Earth
2ee539aa-933f-56c0-9220-1db1e740fc7b | textbox | Resistance (Ω)
17f9b7f0-2c20-5abe-a210-21c0556a83fd | textbox | Target Resistance (Ω)
0963f175-9fe2-4d9e-a431-045b23711916 | signoff | Checked By (Heyday):
3e42762d-bf31-4d36-829b-e5be308b1a59 | checklist | Testing & Commissioning - Main Switchboards (Energised) |  | Main Switchboards (Energised)
f9aa158d-c33c-45ef-8941-ff151efe3e40 | section | Phase Voltage Reading
f96731dc-15c4-4ade-b71a-c95e9777c215 | checkpoint | Red - White
f4a3c1c8-4e6c-58fe-92a1-38c60f07d84d | textbox | Voltage (V)
46972991-0c7b-473b-9eaf-8a516c8c437a | checkpoint | Red - Blue
9012a56a-eb3f-549c-a99e-4ab59a18706f | textbox | Voltage (V)
eb36847c-ed6d-4567-9d58-f3b164fd3df1 | checkpoint | White - Blue
7730bb55-8399-5410-a6d8-9e321f2c3b55 | textbox | Voltage (V)
a1f0e0e5-888d-439a-b021-188f1611623e | checkpoint | Red - Neutral
1b9de252-2bcb-50f7-a8a4-21296a1917d1 | textbox | Voltage (V)
5982f28f-419b-436a-a8c8-e8c3a795f156 | checkpoint | White - Neutral
fd5ad721-6b4d-581b-98cd-16572b17c288 | textbox | Voltage (V)
c968da2a-b6d4-4aef-b161-053f68e23df1 | checkpoint | Blue - Neutral
5e1fa804-47a1-5108-b5c5-98b30ca5c998 | textbox | Voltage (V)
3be6019e-bce6-494d-9680-40f2b59f2946 | checkpoint | Red - Earth
27a4ef16-3301-50ce-998e-8dc1a2448f00 | textbox | Voltage (V)
264f3f81-f0b1-451c-98da-05ef1aedaaff | checkpoint | White - Earth
1dee7dae-4540-58c6-980a-81266bf5e66f | textbox | Voltage (V)
eb645a35-eaac-4c73-a941-28e7662351d0 | checkpoint | Blue - Earth
fef4a341-e45a-5d94-b3d8-5d6cc06e2ce8 | textbox | Voltage (V)
9fb37f2e-d1cf-4563-b290-de3d9ef95ec0 | signoff | Checked By (Heyday):
03d24af3-4139-436a-b530-ee2eb31b26b6 | section | Phase Rotation
0983e440-0629-44a5-acde-f06ac1b4807b | checkpoint-no-value | Direction
53223924-832f-5e8b-9414-bec236d33ab5 | button | Direction: | Clockwise,Anti-Clockwise
06501d42-3386-43fb-b9da-0d8237b6d947 | signoff | Checked By (Heyday):
50866f89-092f-4410-b11b-5e2c0f371df3 | checklist | Testing & Commissioning - Main Switchboards (Pre-Energisation) |  | Main Switchboards (Pre-Energisation)
8fae24b8-93ff-44e4-9f3e-3d4d4fd11b95 | section | Physical Checks
e709c7be-8e7d-4169-9abe-3cb7607e04ab | checkpoint | 1. Confirm boards dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section)
f12a6ef1-c025-4c3f-8e3c-aabbcbac8a65 | checkpoint | 2. Confirm correct MSB Form of Separation, Provide actual Form of Separation in Comments section
4bacf871-43d7-44b1-9ca7-931eb3d5c73e | checkpoint | 3. Confirm the Layout of fitted components (ACBs, MCCBs, MEN, ATS) is in accordance with approved shop drawings (provide drawings reference in the Comments section)
5acd8e26-1e16-488f-bf1f-2688b05a237b | checkpoint | 4. Confirm that Brand of fitted components is in accordance with approved shop drawings (provide drawings reference in the Comments section)
c3e92977-4409-4e3c-b8a0-114bf210be9f | checkpoint | 5. Confirm meters location, types and labels are in accordance with approved shop drawings
134840f7-5341-470d-a375-90551e836a99 | checkpoint | 6. Confirm the circuit breakers rating is in accordance with discrimination study (provide discrimination study reference in the Comments section)
0763de31-405b-4e72-857d-2ced3f82e9c9 | checkpoint | 7. Confirm Trip units and protection relay settings are set in accordance with discrimination study
109d65e8-a0df-42f4-8a18-a6457d59aadf | checkpoint | 8. Confirm correct circuit identification and labelling
f10e2dcb-9875-47f0-b4d8-958e1fd394ee | checkpoint | 9. Confirm easy access to controls termination
9a611db2-39d4-4660-b50b-1fcb1452706a | checkpoint | 10. Confirm correct location, access and sufficient support for incoming cables
8083287d-4ea4-4e47-8888-070a7be1c4f8 | checkpoint | 11. Confirm correct location, access and sufficient support for outgoing cables
dd201025-c906-4ded-af65-32c021351bff | checkpoint | 12. Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in a Comment section
a596d58c-b005-485b-9c07-51013801b5a8 | checkpoint | 13. Confirm correct phase identification of busbars and cables inside the board
bc2f44c9-0e12-4027-9ac0-857eef3646d5 | checkpoint | 14. Confirm correct size of incoming power cables as per approved cable schedule
5db9f0ed-1af7-439a-be14-ef8d2771c4d1 | checkpoint | 15. Confirm correct size of earthing conductors
3039bea8-eb57-44dd-beda-50bce13c367b | checkpoint | 16. Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
e2a9d985-c8f5-41c3-9d63-7c730d1b8185 | signoff | Checked By (Heyday):
1e94d923-98c2-4cf3-83f4-8e81fb3f9ed2 | section | Mechanical Checks
ed460c2b-4e25-45f6-a336-77a8cc25c8ae | checkpoint | 1. Repeat closing and opening of air circuit breakers for 3 times using the front panel operating buttons and charging handle
0e70d6de-0d05-46e6-a482-c5df4089c862 | checkpoint | 2. Repeat racking of air circuit breaker in and out of chassis for 2 times to verify correct functionality of sliding mechanism
33e985fc-0800-4089-ac92-b78eaf79d6fb | checkpoint | 3. Repeat closing and opening of air circuit breakers for 3 times using the front panel operating buttons and charging handle
7606501e-6b84-4d59-bf66-647360d4245e | checkpoint | 4. Repeat manual closing and opening of moulded case circuit breakers for 3 times
8365c25d-b9eb-4b26-a107-e3ec28f0ca3f | checkpoint | 5. Repeat manual closing and opening of miniature circuit breakers for 3 times
cfa73a8c-32bd-498f-92f4-6645a8c83db8 | checkpoint | 6. Repeat mounting and dismounting of control fuses 1 time
1bbac3cf-816d-429e-8593-6f95117b09fa | checkpoint | 7. Repeat mounting and dismounting of control fuses 1 time
4df04b50-8603-4e17-a06d-09346cb9d6c6 | checkpoint | 8. Verify integrity of mechanical interlocking system between ASBs (MCCBs) by closing Source 1 Breaker and confirm that Source 2 Breaker is mechanically interlocked
ba24e470-4526-445c-8da5-7f158e4f0fa9 | checkpoint | 9. Verify integrity of mechanical interlocking system between ASBs (MCCBs) by closing Source 2 Breaker and confirm that Source 1 Breaker is mechanically interlocked
a9a85573-39a3-48ad-acb5-79c2bccd745e | checkpoint | 10. Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards
7379659a-2fa1-4c98-a287-5b383874bf0e | signoff | Checked By (Heyday):
722dc086-3965-41eb-8544-d40f6e036103 | section | Switch Gear Busbar - Preliminary Checks
7f37c3cd-7b41-49b4-8dd7-d0952e802c69 | checkpoint | 1. Confirm all fuses Removed in board’s Control Sections
420447a3-a867-4e5e-b379-dad0ffae8c6d | checkpoint | 2. Confirm Main Incomers ACBs/MCCBs are Closed
0cad5f1a-3ffc-4c5c-b91f-9a473d0f7771 | checkpoint | 3. Confirm Bus-coupler is Closed (if exist)
216adc9a-95a4-48a8-822a-97fe489b05c1 | checkpoint | 4. Confirm Outgoing Feeders is Closed
31e36a40-14f8-4cbe-9a16-a63c06e2e646 | checkpoint | 5. Confirm Main Panel Neutral to Earth Link(s) was Removed
3521c02c-fa2e-4164-9e0a-e2a75858c4bd | checkpoint | 6. Confirm Neutral link on Transient Voltage Surge Suppressor is Opened
f4d3a76f-555b-4d08-b1d6-4d5b74b52e15 | checkpoint | 7. Confirm All Long Time rating Plugs From ACB's are Removed (if applicable)
2449c516-6d70-4564-a68a-81fc28786ec1 | signoff | Checked By (Heyday):
b93d32c8-fa8d-49b1-9124-61c88bd8b5a1 | section | Switch Gear Busbar - Insulation Resistance (1000V)
fce186ff-8fe9-420b-baa6-25a24b2687eb | checkpoint | 1. Between L1 Phase and Neutral
5d0fa9d4-3057-5f7b-95f7-ee58f147495d | button | >10MΩ | YES,NO
80a0e736-fd6c-580a-9dfe-e4566efffaa5 | textbox | Actual Reading if <10MΩ
f51eb97c-857c-41ad-8a95-47625b23dfba | checkpoint | 2. Between L2 Phase and Neutral
67010062-53c3-58b0-aaf0-1fce18f8b9f5 | button | >10MΩ | YES,NO
ce4e99d7-d9b1-56ef-8de3-f1adc0c6dea7 | textbox | Actual Reading if <10MΩ
90fd0fcf-c627-4718-8cc7-77d1c29a1fed | checkpoint | 3. Between L3 Phase and Neutral
4411ae80-a470-52a3-8e98-2e78a4fd4846 | button | >10MΩ | YES,NO
bd565b3f-87dd-59b9-8dbb-46149c449d56 | textbox | Actual Reading if <10MΩ
13d3855a-a1b4-46e7-8ccc-b27564e8a236 | checkpoint | 4. Between Neutral and Earth
91779843-aadc-5e9e-8df5-c8484ba1da16 | button | >10MΩ | YES,NO
0d181df8-1b98-5f4c-ba7b-187a701c47b8 | textbox | Actual Reading if <10MΩ
f95ee146-bbb8-4e2f-a4df-c8e5d3f26450 | checkpoint | 5. Between L1 Phase and Earth
4c632dfa-483b-5787-adb5-28360c6c913f | button | >10MΩ | YES,NO
39b1bc1e-1c12-50dd-8316-88afe5fca0cf | textbox | Actual Reading if <10MΩ
d30595f0-a3f8-4402-b31c-336b98e222bb | checkpoint | 6. Between L2 Phase and Earth
46836438-d796-5460-aa13-7cae26b1fd97 | button | >10MΩ | YES,NO
9e6f285d-66fd-56cf-b709-4c5083cc1e73 | textbox | Actual Reading if <10MΩ
fe251e3b-f2e0-47da-a196-2c7bede637f4 | checkpoint | 7. Between L3 Phase and Earth
6120150e-b479-5ebb-b823-3d0597e4012d | button | >10MΩ | YES,NO
371fa103-6b1b-5a1d-a8ff-22b0a9a90fe0 | textbox | Actual Reading if <10MΩ
6b83d718-c6ab-4eae-9a93-cbf60e348f7f | checkpoint | 8. Between L1 Phase and L2 Phase
6c31f4b8-d3b5-5a40-aec8-1cace3e40112 | button | >10MΩ | YES,NO
e6e64b91-a4fa-503d-a906-c38b723cab43 | textbox | Actual Reading if <10MΩ
322c5bc1-a6a4-468a-90e9-2fbb787585a4 | checkpoint | 9. Between L1 Phase and L3 Phase
acae8a88-5a0b-5a84-932f-bd9473732356 | button | >10MΩ | YES,NO
c3ac8128-d9c4-5287-a16f-68a7a4233fc7 | textbox | Actual Reading if <10MΩ
5467d427-0bfe-4a76-93c0-dafb6762aab2 | checkpoint | 10. Between L2 Phase and L3 Phase
c32f53a4-5b47-5025-8e58-dd468a5b1ae8 | button | >10MΩ | YES,NO
c60a138e-3cbd-5d99-a5d7-e1830a41f33d | textbox | Actual Reading if <10MΩ
9ab74075-6424-47ab-93b3-86223af607cd | signoff | Checked By (Heyday):
1101a10d-756f-4e13-8fda-4961a22ab017 | section | Current Transformer Checks
6e28df17-fe33-4990-b850-65e3962369b9 | checkpoint | Current Transformer Checks
2ca59f02-67a2-5beb-b332-0c51245ac3ca | textbox | CT ID | YES,NO
a0a82070-b7f4-5def-a4e8-ed1406108b82 | button | CT Polarity is Correct | YES,NO
a6f07223-c23c-528e-8fc1-033de1f54bd3 | button | No crossed phase CT connections | YES,NO
ef0bddc3-f045-565f-8180-9f59cbbe3652 | button | No phase sequence CT connection errors | YES,NO
63bf9fa9-ae18-4cdd-93aa-59a4170eb7de | signoff | Checked By (Heyday):
10d56c3d-cdad-465f-b948-220f28af9777 | checklist | Testing & Commissioning - Single Phase Subcircuit |  | Single Phase Subcircuit
99fcf775-d9d9-45aa-bc40-72ea8e95beac | section | Pre-requisite Works
b6245e80-1e48-4375-9cfc-b3295cba6b21 | checkpoint | Insulation Damage
c960e5b7-636f-44eb-8b9e-1acc1f6c3372 | checkpoint | Correct Type of Termination
830d7519-7adc-4fe4-990f-97619c9fa743 | checkpoint | Correct Colour Code
6623d9a4-6615-4c48-a1c0-4c32931da7b4 | checkpoint | Correct Outlet Rating and Size
6af80b46-6884-4add-b7f2-b4eb130de2b9 | checkpoint | Earth Continuity
060aa90b-811f-5ad5-a5da-76c27b44531f | textbox | Resistance (Ω)
7eec440f-bc3f-455d-bf19-55fc824a350a | checkpoint | Polarity Check
440b6016-299e-5394-867f-385fa07202af | button | No Transposition | YES,NO
053b0de7-0eb6-5547-9d2d-46e1f3bf95e9 | button | Switch in Active | YES,NO
cac33f21-9bd0-4d32-9e91-4a0bf4bb1986 | signoff | Checked By (Heyday):
f4a80d27-97cd-4a26-b498-168f68df6e9a | section | Insulation Resistance
8ba76168-4007-4b84-a280-12de7c138cd0 | checkpoint | R-N
537274d1-6646-5c85-9b27-ebf56328087c | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
6dafc51c-6de6-5824-870b-a7a7a90a7265 | textbox | Actual Reading if <200MΩ/<500MΩ
db4bc454-6f5c-491f-a3a3-dfaca4127ad2 | checkpoint | R-E
8982dd66-b9fb-5b80-853e-77054ede7db5 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
ae800fe7-c015-5255-b809-77f63aec3189 | textbox | Actual Reading if <200MΩ/<500MΩ
40c2ab33-5545-4ccd-9b21-54406f15e189 | checkpoint | N-E
b6de9cfe-c2d0-5ae3-97a9-4ecc322b1504 | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
7eaa26a2-e6bf-5dbe-bc66-803628eeb184 | textbox | Actual Reading if <200MΩ/<500MΩ
f4af799e-be17-416a-ab51-2d2359803069 | signoff | Checked By (Heyday):
28c42bf5-375b-4323-800e-8f7333eb5598 | section | Voltage
c4eb594f-a5e8-4bda-ad37-025dc2ed4b10 | checkpoint | Red - Neutral
40d5203f-80a5-5632-8e29-135176de772d | textbox | Voltage (V)
23234cdd-c1ec-4a2d-a172-b8a9451f300a | checkpoint | Red - Earth
fb73a258-9d7e-5f99-b38f-64a76c6df601 | textbox | Voltage (V)
1b5a065d-b5e8-436f-87a0-86d74770114d | signoff | Checked By (Heyday):
b0eba347-4d78-4768-a547-43d5a8d27339 | section | Earth Fault Loop Impedance Test / RCD-RCBO Tripping Test
9af5b6e3-ad80-4327-acd6-fd1c0042d1b4 | checkpoint | Impedance - (N/A if the circuit is RCD Protected)
ca658463-6c9b-535c-9f84-e77a01da0d98 | textbox | Record Inpedance (Ω)
35a29d49-1248-5728-ad7c-5f968884a5b1 | textbox | Target Impedance (Ω)
4429efd3-4f70-4c1d-b68e-8e99ef5835f9 | checkpoint | RCD/RCBO Tripping Test
e3ba2339-b613-58ff-83a6-2095d2667dcd | textbox | Trip Current (mA)
e0ca11a2-eb7e-51dd-ad53-5839c860a2f7 | textbox | Trip Time (ms)
858b7cb6-6ac1-489a-b2ee-fa203eaa4510 | signoff | Checked By (Heyday):

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Postfix
82c06f34-8c90-46dd-9f46-676d6894970a | checklist | Installation and Rough in |  | Installation and Rough in
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
188d52b4-88d8-403a-b8fc-23d967798458 | checkpoint | Distribution Board Installation
f0f48faa-ed18-4a4a-87a4-e1b3b260f85a | checkpoint | Light and Power Rough in
b6b2e16d-c924-44be-8eec-37efa112cef0 | checkpoint | Light fitting Installation
ef7fb927-8f99-4f29-96e0-235892bf9486 | checkpoint | Electrical Equipment /Accessory installation
f28b3c7b-6efd-482f-9f10-832605550ccf | checklist | ITC-EL-E003-C-R - MAIN SWITCHBOARDS | itp | DB #
763f4822-5825-4ee0-a2da-5f297fad504a | section | ITC
9dd098c0-b658-475b-bf0f-67b28c01657a | checkpoint | Voltage Checks
f07475ef-024a-53bb-a120-e4cafea62a34 | textbox | R-W
e5438411-cda2-5ea8-9afa-1a962d67e4ac | textbox | R-B
8d6d17b1-90f0-5ed6-92b9-ca31e0bce706 | textbox | W-B
50160456-f93a-5796-a7a0-f2989cb6ea1f | textbox | R-N
ff7e5d1e-498e-58bf-828a-ba9e7365bef4 | textbox | W-N
1a5acc73-e609-52cb-a99c-d782f346b6fa | textbox | B-N
0ae9dfb6-80b1-5706-9b62-19f0871fcaff | textbox | R-E
c3bc17c0-3f90-5586-b4ff-44677b983ab8 | textbox | W-E
40769b39-ad7f-592d-9c53-0a7098d76ad8 | textbox | B-E
a3867c13-2268-478d-8524-f9b7a4afecda | checkpoint | PHASE ROTATION
f4a751eb-e189-5146-8b3b-24b16e0f5f62 | textbox | Board Nm.
f0886a2d-91fc-5fd4-b0c1-5006b81bea12 | textbox | ROTATION:
2a3366c4-fd21-4725-bde5-990ea758840c | checkpoint | Multimeter reading (V=Volts & A=Amps)
39393ad8-77c7-508a-95ff-847409a7743a | textbox | Red Phase
6860dda1-004e-5f63-aa97-85646ad4b150 | textbox | White Phase
1aa4920f-7ef5-5d0c-ae05-54478879f81e | textbox | Blue Phase
328b93eb-d9d5-4aec-9873-e5b74a804550 | checkpoint | DB Meter reading (V=Volts & A=Amps)
7b6c413b-7f75-52fe-bdfd-ebe83ada5f05 | textbox | Red Phase
574ffd69-078b-5e4f-978a-bed65d44da53 | textbox | White Phase
c6740cff-b514-5b6d-803d-3ef346459f64 | textbox | Blue Phase
47262031-16d4-4044-b270-75bde52771ec | checklist | PROJ3004 - ITC - (2) Metering Panels (R3) | itp | METER PANEL TYPE / NUMBER / AREA
c92e189a-7102-4d54-850f-90e199173af4 | section | ITC
be1bf1b7-1c16-48d8-8450-b81d5668a398 | checkpoint | MOUNTED CORRECTLY
5f3853cf-ec92-482b-aed5-f4870316f281 | checkpoint | DAMAGE
0287ef3a-d21e-42bf-9fb1-61d7d7969f08 | checkpoint | LOCATION TO DRAWING
532b0ad3-5a8e-477c-8bf5-0d9be339631a | checkpoint | EQUIPMENT TO DRAWING
926ce382-8999-4d0a-8fea-babfbd6f04cd | checkpoint | CONNECTIONS BY HEYDAY.
63420a0e-a981-4935-bcba-2ea59f869e2e | checkpoint | CORRECT EARTHING AND SOLIDLY FIXED
32f1173d-8f7f-4445-bc47-449f50991f4f | checkpoint | POLE FILLERS INSTALLED
c32f0676-942d-459f-abcc-6da5a6091050 | checkpoint | ALL CABLE ENTRIES WITH ESCUTCHEON PLATES AND SEALS FITTED
b7af6796-ff78-4cd3-8178-c48f92299253 | checkpoint | BOARD SEALED AND LOCKED FOR SAFETY INC: FRONT AND REAR PANELS
0a44f60a-4dd6-4be1-adec-9805955e6d21 | checkpoint | LABELS AND SCHEDULE LIST CORRECT AND INSTALLED
3a38b99b-25f9-41b1-a27c-602b99e8f7ed | checklist | Quality - Busduct |  | Quality - Busduct
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
db1ae93c-8268-473f-81f4-4737cab4cedb | checkpoint | Receipt of busduct/ busway & take off box's delivery to site
0114f097-b1f8-4453-94af-2f70c8afebbd | checkpoint | Set out - Ensure correct size, type and spare capacity
ffa958a9-909d-4049-aa96-1053347f0c80 | checkpoint | Accessories to be factory made items
deca732e-8625-46fd-b406-dfc8423083a9 | checkpoint | Hangers installed as per the drawings
c190a62c-7f82-4546-bb9a-89b5d1be057f | checkpoint | IR Test of Busduct - Separate - Test Result Above 1M Ω
542607b0-ce8e-4ec4-a7c0-5f6d4529cba4 | checkpoint | Busduct Piece are installed safely
cac51acd-6d78-49ed-870a-84ba62ce7f25 | checkpoint | Busduct Torqued to 95Nm
9e80dd70-5c34-41f4-a2e2-c730ddebf488 | checkpoint | IR Test of Busduct - Joined - Test Result Above 1M Ω
385aae35-6770-4aa5-8950-365609a1f68f | checkpoint | Photos attached of installed piece
40d6a1f9-123b-40c8-8b1f-0eed08384d78 | signoff | Checked By (Heyday):
4b07463c-5687-47a1-a511-607266efb7cb | checklist | Quality - Cable tray/Ladder |  | Quality - Cable tray/Ladder
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
8ec8ca09-6507-4060-8222-7311ba924b2b | checkpoint | Receipt of Cable Tray delivery to site & storage
31303573-2ccc-4457-bc82-5e799c64f00d | checkpoint | Set out to be confirmed with latest IFC Drawings
d203099e-f5a3-4d50-8ff3-dddf9500a92b | checkpoint | Accessories to be factory made items
55d26861-bfd5-4c2b-ad04-bd8717697dd6 | checkpoint | Correct Levelling & Alignment
07819f9e-eb9e-4d84-a017-c7c692890b33 | checkpoint | Correct bracket and safe fixing
166f14d0-60f9-488e-9f61-55ecd9d55dfd | checkpoint | Correct Bends used (Cable Ladder)
6ef7e067-c82a-4d3a-908a-f7faf4928576 | checkpoint | Photos attached.
e868e3f1-4691-4938-88fd-8ddc58831b6e | signoff | Checked By (Heyday):
09dcb9d9-840d-4b6d-9c48-298a8794b4f2 | checklist | Quality - Communications Cabinet |  | Communications Cabinet
74b0e18a-cdc3-4bbf-9f78-03e6f2dbd125 | section | Details
1e33c142-4673-491d-a7da-e50b60050198 | checkpoint | Receipt of Cabinet delivery to site
dc12a1ac-8e8b-46f4-b286-6b1ad5d64bd7 | checkpoint | set out to be confirmed with latest cabinet Shop drawings
49de0e10-2f34-4f03-9bca-f6590dbbea3c | checkpoint | Correct alignment to set out drawings
9f0f4020-4e09-4fba-aecd-05779627e9b6 | checkpoint | Correct bracket and safe fixing
0628b79b-13cc-4c4b-b895-a9da1cb20284 | checkpoint | Photos of cabinet attached
9ed5fb82-eed2-4eca-84c6-2d29edc0a756 | signoff | Signoff Required from Heyday/MDE
1e31b269-c3b2-4024-8612-2c5dabe38570 | checklist | Quality - Communications Cabling |  | Communications Cabling
3c585611-1308-4256-9659-26efaec52fbe | section | Details
3322955e-809c-4e07-932c-88f21520073c | checkpoint | Correct cable type.
2fe6887e-66fa-46b4-b33f-5b3eb2dead57 | checkpoint | Installed to correct cable routing arrangements & cable number.
c8902a47-3447-4734-95fe-fa4b9daf368a | checkpoint | Installed to final location.
b2d3582e-8fa5-4646-9760-45708511f5b0 | checkpoint | Photo evidence captured for cable containment install.
9e41f623-185e-4211-ad95-1259785aa28c | signoff | Signoff Required from Heyday/MDE
39a213a7-65c4-4725-b0fc-771c3fc18bd2 | checkpoint | Attach Photos
18c33c9d-d299-49a1-9961-d361dbf2afec | checklist | Quality - Distribution boards |  | Quality - Distribution boards
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
9626e9fd-9b2a-49cf-9de6-ee22be777fcb | checkpoint | Receipt of switchboard delivery to site
fb90b693-b41b-43ef-b944-7132319c721f | checkpoint | Set out to be confirmed with latest Switchboards Shop drawings
9df6fef5-1164-4651-bbbf-e01bd0c4b4ab | checkpoint | Correct alignment to set out drawings
54d650d1-fd7f-4b88-a49f-3006f70d0f60 | checkpoint | Correct bracket and safe fixing
504db0ed-5761-418d-8a49-302be645a3cd | checkpoint | Photos of boards attached
cd3edd1f-2cc1-48e7-983d-96d3ed60cb35 | signoff | Checked By (Heyday):
2909ede0-7452-44ce-86b2-6a44d6908f03 | checklist | Quality - Earthing & Lightning protection |  | Quality - Earthing & Lightning protection
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
629ff61e-e39b-4a4d-b1d6-f43fdf07dc05 | checkpoint | Receipt of Cable & test point delivery to site
7ec7598a-86b3-4d3b-89ec-862cbd2d6dca | checkpoint | Correct cable size and Cable type installed per the shop drawing
c2870e55-cccd-4917-b727-7cba11a742b9 | checkpoint | Installed and Terminated to final locations
573fdd8d-adad-4ccb-8426-592b5da40884 | checkpoint | Photos of test piont and bonds attached
e467a77b-0509-4d57-8f12-55e37e572503 | signoff | Checked By (Heyday):
3d85dfb4-516c-4896-801e-f2210445b1fc | checklist | Quality - Electrical Equipment/Accessory Installation |  | Quality - Electrical Equipment/Accessory Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
7a753de0-e640-4bb6-bbb3-ca0db84ce35a | checkpoint | Installed Correct Type/Colour of Equipment or Accessory
9fb1d46e-d60d-4f99-9ee6-9a01ba77aa99 | checkpoint | Installed to the correct location as per drawings
626bfe70-34f4-4c5c-9de7-05bb351b0784 | checkpoint | Installed with correct fixings and made safe
ca1cd3df-9c2a-445a-98b6-41f1312db821 | checkpoint | Installed to the correct Circuit & DB Destination
e07dfa47-4456-41fd-ad10-23784d8001ee | checkpoint | Installed correct labelling
126b060a-fb34-499b-92ba-97ea17688f72 | checkpoint | Final Check and No Damage to item
5fb31c15-d873-4099-aca7-2a7fbf0855bb | signoff | Checked By (Heyday):
57db5a91-e592-43c1-b1f0-76e9091fbcd7 | checklist | Quality - In Slab LV & Communication Conduits |  | In Slab LV & Communication Conduits
a6c2e159-baed-4a91-a5b9-d0a465679549 | section | Details
eb7412a6-194d-4540-b68c-2881991081cc | checkpoint | Receipt of conduit delivery to site & storage.
30996dea-4375-40e7-92da-13d4764f4382 | checkpoint | Correct location to Drawing
95a98eae-d4df-44be-834b-8812c91b5448 | checkpoint | Correct size and type
a3f18ce5-99b5-415f-b229-227005d5715e | checkpoint | Correct spacing in slab
c46f217a-383d-40f9-9cfa-9a7ef9bd3368 | checkpoint | Correct depth in slab
d5b57691-57db-430b-b5d4-927bfa255409 | checkpoint | Clear to other services
4a166627-0122-475a-9045-fe28eac53a52 | checkpoint | Conduits glued together
ef487874-491c-4db8-bfad-d0367a613695 | checkpoint | No Damage
2d6fc64b-33f9-4759-bfca-be8fcaad52e6 | signoff | Signoff Required from Heyday
63fbc1d1-c4e7-4c55-a940-4e67508a21a4 | checkpoint | Record photo evidence.
b6a3cbe3-4cac-446b-b33c-3fcc54db8db6 | checklist | Quality - Light Fitting Installation |  | Quality - Light Fitting Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
5683c98e-3d9f-4754-9e23-2904acc5ab6a | checkpoint | Installed to the correct location as per drawings
e2d68ed3-a669-4b5b-8c56-f1926720167d | checkpoint | Installed correct size and light fitting type
6e84a653-f97b-4185-bc4f-69425f37bb54 | checkpoint | Correct Operation
f3d94e81-85ae-4c49-bfb5-f5d6c947be5b | checkpoint | Installed to the correct Circuit & DB Destination
9ee4ed33-335a-4de0-8836-ce2c9eb82cf9 | signoff | Checked By (Heyday):
db604876-17f7-4d1c-b495-e067e3fce3b0 | checklist | Quality - Main Switchboard Install |  | Quality - Main Switchboard Install
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
f2685ba0-30a0-4f52-ba12-bd20eaa6029a | checkpoint | Receipt of switchboard delivery to site
638e84d1-2bca-4a96-a954-c834c5853c01 | checkpoint | set out to be confirmed with latest Switchboards Shop drawings
670d2ce2-a73d-4f0e-aac2-895deda45d15 | checkpoint | Correct alignment to set out drawings
11d9a4e5-5cb5-48e5-977d-85738333a35b | checkpoint | Correct bracket and safe fixing
6201460d-2ef2-4f7b-9e65-b9d912064d09 | checkpoint | Photos of boards attached
044a1233-9552-4dcd-b8ef-83b8230b4cf7 | signoff | Checked By (Heyday):
43f3ffa9-53ae-49eb-9827-e695febdf517 | checklist | Quality - Mains and Sub Mains |  | Quality Mains and Sub Mains
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
719c4738-6620-4170-8864-8df311d624c6 | checkpoint | Receipt of cable containment delivery to site & storage.
f9d3ea63-b3b6-4518-add2-cea6f6c506c9 | checkpoint | Cable storage & handling.
52d0456f-e890-465f-b975-f65bb2e62ee3 | checkpoint | Correct cable size & type.
de5eedc8-aac8-4c50-a3b8-b0d4e96e7c27 | checkpoint | Installed to latest drawings – schematics/single line diagram & cable containment drawings.
216c7054-a5da-4023-87fe-a1dfdc89266d | checkpoint | Correct cable tag installed.
2aa5f58c-be38-4bf2-a086-e4e5d7afd003 | signoff | Checked By (Heyday):
2d730550-810d-4cd1-a4f2-5b322d80fb28 | checklist | Quality - Power and Lighting Subcircuits |  | Quality - Power and Lighting Subcircuits
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
8bcec3de-4eb9-4dc0-b599-9d9f1a4a6de6 | checkpoint | Correct size & cable type.
ce35a56c-cfe4-47de-b98a-044c1b2134f5 | checkpoint | Installed to correct cable routing arrangements & circuit number.
e71781c0-b1e0-4d9d-950a-a0246600a7fa | checkpoint | Installed to final location.
b549a25d-0cc9-4637-b419-cc8c4ea1c54c | checkpoint | Attach Photos
89ff589b-850b-4ef5-84fb-e2dd44430aa6 | signoff | Checked By (Heyday):
345ddc44-7a22-497f-a506-97aca9cf6583 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000003 - Main Switchboards | itp | DB #
9d313561-34b4-4119-b267-f6509277311a | section | ITC
dd164818-b340-4632-8de1-5ab0eb7ffe25 | checkpoint | Confirm All Pre-requesite Work Has Been Completed
b71e0a5e-7c8e-4b20-b743-50ca422783d6 | checkpoint | Completion of "Visual Inspection of Distribution Board" Check list prior to testing
27803e77-22cb-5c9c-9a84-7ec313164d8d | button | No damage | YES,NO
99971487-4c3b-5423-87da-5bed22364fee | button | Sufficient supports | YES,NO
8243979f-2474-526a-a89d-d198d8cb1b3f | button | Correct labelling | YES,NO
2fd4fe67-dafb-4e38-9b93-c63fe1dea1b9 | checkpoint | INSULATION RESISTANCE
1898892e-2967-5b99-8f33-ccf8937c33a6 | note | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
334f2cbd-fa2c-55e4-b897-e3709fb4690d | note | The insulation resistance shall be not less than 1 MΩ.
44475211-7687-5950-b0d2-367f29ebf6f4 | textbox | R-W
1092c507-33e4-5d7e-91c8-9eeefbff7741 | textbox | R-B
89579447-63f3-573d-a92b-29b3c1fbc487 | textbox | W-B
00dd62c4-285c-52d8-ab4b-7603da2d45d9 | textbox | R-N
ec3c2f6c-c545-5eed-ba5f-27acc7a85db4 | textbox | W-N
7aee3b70-dc26-5d41-988c-085fa95e1fdc | textbox | B-N
d65ca42e-5364-58ba-b459-f0257a729188 | textbox | R-E
8a88b10b-084a-585d-ac94-957e2a013ade | textbox | W-E
2a7bd662-8c4c-53d4-a664-60bca4a4c817 | textbox | B-E
a0f09bad-3e3c-469f-8bdd-d4f8a970754b | checkpoint | CIRCUIT BREAKER OPERATION - OPEN POSITION
b132c51a-4085-5c42-9731-cc411aa25ad9 | note | Continuity Test – With breaker in open position
91411342-a92d-4ca5-bf03-1a88ea42932e | checkpoint | CIRCUIT BREAKER OPERATION - CLOSED POSITION
68eb7ed9-e801-52e4-8f46-ce3584deae49 | note | Continuity Test – With breaker in closed position
ccdf98f5-dddf-4f4c-b9bc-bdb73c2f3e23 | checkpoint | CIRCUIT BREAKER SETTING CHECKS
79bb6ee5-701b-599b-94cb-e36c914ab22a | note | Verify Breaker Settings are as per Distribution Board Shop drawings, Associated schematics & DB Schedules (Board Drawings to be attached to ITC)
05a43503-a7c0-4552-83c8-1f1fc7b8d429 | checkpoint | CURRENT TRANSFORMER POLARITY CHECKS
65c6baad-9916-50b0-921d-49984d5431e7 | note | Visual Inspection – Confirm CT Marking Indicators are as per manufacturer Install. Guidelines. Visual Inspection of all other wiring
3b8e8313-da56-4400-bb5e-c7a7cba34450 | checkpoint | CURRENT TRANSFORMER RATIO CHECK
7ccfe567-678c-51af-993c-058e63877043 | note | Visual Inspection of CT Ratio. Record CT ratio and confirm it is as per the switchboard shop drawing
fc811301-2fe6-5136-a7b1-48f05527d20b | textbox | CT Ratio
3bab56a8-941d-4c3e-b125-d1724074521a | checkpoint | Multimeter reading (V=Volts & A=Amps)
d44ddd49-a37b-5f8d-9995-b39328a42c9b | textbox | Red Phase
0770c1bf-ec22-5dff-8f08-cfeb278eaa0a | textbox | White Phase
eb7413fe-097c-5798-a78b-5a649135a3bc | textbox | Blue Phase
0eaaa295-1d37-4d38-8306-de74711ea0d1 | checkpoint | DB Meter reading (V=Volts & A=Amps)
0ffdbceb-bc79-5eb1-bd7e-9e4975947c46 | textbox | Red Phase
42389db0-d93c-575c-bdf8-2c3c753b0cdb | textbox | White Phase
6b6f239f-2ec3-5d55-9789-8e7345c323b1 | textbox | Blue Phase
67ce3c3a-7b69-4ff1-9027-19f21a04764e | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000004 - Distribution Boards | itp | DB #
aa337912-9bee-4158-b23a-f238c065921f | section | ITC
1d39949f-d87b-40f6-80b9-460816529273 | checkpoint | Confirm All Pre-requesite Work Has Been Completed
09ba8235-7874-4d19-ba46-d9cfaf26212d | checkpoint | Completion of "Visual Inspection of Distribution Board" Check list prior to testing
d72d7ff2-92ae-5a18-81b7-c73f1698ba42 | button | No damage | YES,NO
fc2139a6-d5f6-5c0a-a25e-9e5882439b78 | button | Sufficient supports | YES,NO
f167286f-864e-5521-b71b-5aef67f2aa98 | button | Correct labelling | YES,NO
aabe24e7-355b-4eeb-a249-1e8d99d0b42f | checkpoint | INSULATION RESISTANCE
6a53ddbd-54fa-5bb6-b9c9-0f4c5be53284 | note | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
687914a3-4a04-57ea-abfb-a8333de206e2 | note | The insulation resistance shall be not less than 1 MΩ.
fdfa1606-98ce-5b5a-962f-9222cb05ff75 | textbox | R-W
949ad97f-dd16-5397-bda8-c8d2f58e0e20 | textbox | R-B
cd0ad0d6-272d-53e1-a4c1-6144e59f07c2 | textbox | W-B
eb52c14f-b3ac-5707-89a2-2f6842b6030e | textbox | R-N
535d6c27-870c-5468-a64d-b8204eec6f64 | textbox | W-N
77ede247-4a32-5251-a6f3-d1611cdce46d | textbox | B-N
1c0b95bd-24dc-515a-a6b0-e7dfe7b66c53 | textbox | R-E
1eade390-e031-5bcc-9e9a-5b13929ce81a | textbox | W-E
e6bd1f8b-92f7-546e-9d97-5a117c8f5a62 | textbox | B-E
e6324c78-bfcd-4f84-b5f4-ad6a78322c7d | checkpoint | CIRCUIT BREAKER OPERATION - OPEN POSITION
0b3ff35b-e2f2-5488-8535-d3ad17e1c387 | note | Continuity Test – With breaker in open position
07bb891d-976b-4d3e-9281-32297705a555 | checkpoint | CIRCUIT BREAKER OPERATION - CLOSED POSITION
6c168106-5358-5032-81e6-cde29ae7113c | note | Continuity Test – With breaker in closed position
d55fc22c-2631-4a99-a0a5-17b5ef8a78c3 | checkpoint | CIRCUIT BREAKER SETTING CHECKS
6121d4f9-5172-5609-bea5-8a4017e62bea | note | Verify Breaker Settings are as per Distribution Board Shop drawings, Associated schematics & DB Schedules (Board Drawings to be attached to ITC)
0eb8a6ea-23ea-4ab1-86d6-508e32f53485 | checkpoint | CURRENT TRANSFORMER POLARITY CHECKS
9675f9eb-c04e-545b-9136-8f5415765520 | note | Visual Inspection – Confirm CT Marking Indicators are as per manufacturer Install. Guidelines. Visual Inspection of all other wiring
3161e808-a364-40b6-9292-917dab07fe15 | checkpoint | CURRENT TRANSFORMER RATIO CHECK
f3371668-67c8-56fa-9c64-518beafa50cc | note | Visual Inspection of CT Ratio. Record CT ratio and confirm it is as per the switchboard shop drawing
fb6164e2-4075-5e9d-8830-8a8c301995af | textbox | CT Ratio
3b843aa4-a46e-416b-8069-7f30b585737e | checkpoint | Multimeter reading (V=Volts & A=Amps)
998e3e51-d519-54de-8a72-83d5de6adbb2 | textbox | Red Phase
e5b954d9-376e-5daf-b9c5-f9531426eb9b | textbox | White Phase
2a56f45f-8af1-5383-b232-805dbe74b1a8 | textbox | Blue Phase
0aad88fb-a746-48d2-bb38-2133d36ce494 | checkpoint | DB Meter reading (V=Volts & A=Amps)
c1b254cd-a2bc-5a1c-855f-e1b613b2e9d5 | textbox | Red Phase
b2ce33fb-422d-5e8b-be78-591a8f3e3949 | textbox | White Phase
31811330-7735-5e51-9e68-172f5dfa7ab4 | textbox | Blue Phase
cd179520-3b6f-4722-941e-ae679f0f17b5 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000005 - Conduits | itp | LEVEL / AREA
52231bf5-6a17-4d52-98bb-e48f57783084 | section | CONDUITS
c62bf191-3e8b-486a-ace7-ab0aa71edd54 | checkpoint | CORRECT LOCATION TO DRAWING
90e14198-5809-58af-977b-bfaafe7476d1 | note | As per HD SHD
1cf2f7c7-417c-4b7d-98b4-85c9ebc7726d | checkpoint | CORRECT SIZE AND TYPE
45cbedc0-2b44-5475-8084-8076d0adfa35 | note | As per HD SHD
6fc63625-8eb8-409d-8d56-934d5e38bab2 | checkpoint | CORRECT SPACING IN SLAB
8ca1a473-c1c1-4454-a13d-abd10412fcaa | checkpoint | CORRECT DEPTH IN SLAB
04a711df-97e3-43c4-b4fa-56b0486c3597 | checkpoint | CLEAR TO OTHER SERVICES
00a31cef-529f-4a69-8583-616671e004c6 | checkpoint | ACCEPTABLE INSTALLATION STANDARD
ea2df58d-9593-4dc4-bb1e-fe24e982b620 | checkpoint | NO DAMAGE TO CONDUITS & CONDUITS ARE SECURELY FIXED
8cd5f8da-432b-41c5-bb49-a01d1bc5b7ff | checkpoint | MEASUREMENTS ARE TAKEN FOR ANY DEVIATION & PHOTOS RECORDED
ab6f1336-c740-4e4b-968d-3b0798a10d58 | section | ATTACHMENTS
66678d1b-279d-4b0f-af84-1f5d79f2afb8 | checkpoint | ATTACHMENTS
283371c6-42d5-4900-922f-ead291f3bba4 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000006 - Cable Tray | itp | LEVEL / AREA
7afe42d9-e161-4e9d-aa3b-51898d092f31 | section | CABLE TRAY
7c49685a-6130-4d88-8dee-a0f5033b0252 | checkpoint | AREA/LOCATION
4e66d5f4-d664-52bf-acc5-188a0e770420 | note | As per HD SHD
737df3f3-3ffe-4a4c-acb2-271dc623c393 | checkpoint | CORRECT SIZE
b6437529-e622-5dcc-8a24-cb3ea1924468 | note | As per HD SHD
ee716195-8eb6-4592-b0d6-fe42125b4c29 | checkpoint | CORRECT TYPE
5f7559a9-e3cc-5732-a413-f1c1a595ecc7 | note | Tray/Ladder/Basket
ffdc51a8-b89e-4d94-9e8c-5ffea568bfd3 | checkpoint | CORRECT RATING
b1422768-3415-58c0-a435-4ada8f0f467e | note | Fire Rated/Standard
1d20d748-02ae-424e-bee5-213d89397f3a | checkpoint | CORRECT MATERIAL
f41cc95a-2956-5f0f-96c0-805bcd21a412 | note | Zinc/Gal/HD/SS
13f00746-392e-4672-8201-bed0bbeacb52 | checkpoint | CORRECT SUPPORT
1ecc24e2-c72e-55da-8823-d7cfec7477c8 | note | As Per Manufacturer's guidelines
2691bba2-6a94-4b99-a70c-61a51925b2ba | checkpoint | CORRECT ALIGNMENT
4ce9a6f6-6d05-5cd2-93f1-3e9378df6edf | note | Visual Inspection
424e1099-0061-45ca-a5f4-a55b0471d912 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000008 - Low Voltage Submain Cables | itp | CABLE ID: FROM - TO
a6348e44-9218-4792-b90b-1e7b97323e0b | section | LOW VOLTAGE SUBMAIN CABLES
26b6bba8-6d5a-48dd-b590-a6e2b2f5d9af | checkpoint | PRE-REQUISITE WORKS
41f3b621-232a-5152-a3c7-c61146923ee3 | button | Compliance | FIRE RATED,NON-FIRE RATED
82ca6906-1591-5e9a-b5cf-806d7728166d | button | Type | XLPE90,XHF110
77d816d4-c0ff-5482-ba77-5d03939cbd81 | textbox | Size |  |  | RECORD DIAMETER
1f2dea6b-3bd8-5413-bb05-e3880f69e600 | textbox | Cores |  |  | RECORD CORES
8e03f3b8-1c0d-4ddc-9f07-0c1f63c5d09e | checkpoint | INSTALLATION CHECKS
c8aabdb4-7b03-5a61-bd11-526054e163e3 | note | VISUAL INSPECTION TO CONFIRM NO DAMAGE TO INSULATION
53bfe223-5400-481d-aa18-07a3fed76738 | checkpoint | CONTINUITY TEST
ae13ac14-d453-54e3-96ad-7c0c2e53646d | note | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device
82d4aaed-1734-59f0-8cb7-add907d71b0a | note | RESISTANCE OF EARTH SHALL NOT BE MORE THAN 0.5Ω
10851fdc-cd24-579f-ba46-5d3989cc5e77 | textbox | TARGET RESISTANCE (OHM)
44dc2c0e-7b9b-5983-b310-7387d3a14096 | textbox | RESULT
4949a773-1033-4565-92a7-9f3affb86dc6 | checkpoint | INSULATION RESISTANCE
4f56823f-1996-5ae5-a07c-bf18b8209fe7 | note | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
d42963b0-aa85-5988-825e-5dc4fce3cb36 | note | The insulation resistance shall be not less than 1 MΩ.
377c069b-1005-5a30-9bf0-8fe5cc4b796d | textbox | R-W
aa158db5-0148-55de-98f2-1f1041422096 | textbox | R-B
f62bfb67-ee4c-581b-816e-250e8a8cd207 | textbox | W-B
ef91e273-1a36-5c0d-939c-0af6160a0870 | textbox | R-N
3dff313b-56f4-565b-965f-3e954d41c36a | textbox | W-N
4178e483-3868-5c31-9105-fda795380f2a | textbox | B-N
a5d9d79b-9466-52be-9e65-f8ab5555ac6b | textbox | R-E
22a6e75e-1ace-5a9b-9251-4600d3c6a189 | textbox | W-E
b8cc9733-ad74-5316-8139-575cb96033f0 | textbox | B-E
1ae96cc2-2ecd-4197-b06a-d17fb19ba42d | checkpoint | PHASE ROTATION
e63ae067-e3cd-59ef-877d-3f73a4b0a44c | note | AS/NZS 3017:2007 3.5 Phase Sequence - Phase sequence testing is necessary to ensure that multi-phase equipment such as multi-phase motors and semiconductor controlled equipment operates in a predictable manner.
4e7f18c7-4172-59cf-8a9f-897dfa631b38 | note | Record result
931fca62-b4be-52d7-91be-54bb7265c25e | textbox | ROTATION:
d7ac1b18-874e-4b29-97f0-62c08ebb28e6 | checkpoint | VOLTAGE CHECK
7f92def7-856e-56bf-9521-049ec929af8e | note | Test Line Voltages and ensure the voltages are within acceptable range
b3435aec-b56a-512e-8c5a-32845271795e | note | Aus Grid NS238 6.1.1.1 Low Voltage Supply
44079409-a545-5334-930f-2f5f4707957f | note | 230V +10% / -6% = Range 216V to 253V
fbdccb10-eac1-5e57-ae62-603f221e587d | note | 400V +10% / -6% = Range 376V to 440V
36975791-4100-5a70-9c54-5b04a9972ab3 | textbox | RED PHASE:
3a0f0a90-d8e1-58a6-b88b-60d093ceb4b9 | textbox | WHITE PHASE:
5dbafd45-d2f6-5e76-856c-de1b23143d02 | textbox | BLUE PHASE:
0886281b-5e69-4615-b010-0dae486de53b | checkpoint | IMPEDANCE (OHM)
39b51c17-12d4-561a-958a-53045519f764 | note | AS:NZS 3017:2007 The earth fault-loop impedance of a circuit is measured to ensure that, if a fault of negligible impedance occurs between an active conductor and a protective earthing conductor or an exposed conductive part, sufficient current will flow in the earth fault-loop to cause a protective device to operate within a specified disconnection time.
7f910a58-e126-5c2b-a96d-cab1f6c8d439 | note | 20A TYPE C PROTECTION 1.53 Ω.
34c83741-b482-57ad-ac14-a9f5d0500722 | note | 32A TYPE C PROTECTION 0.96 Ω.
e36a38f7-bb84-5ffe-a955-6326b7be36ab | textbox | IMPEDANCE (OHM):
24617ed5-af78-5db3-9a32-523c7278c24b | textbox | TARGET IMPEDANCE (OHM):
8545a83e-6855-4432-9bef-baf8373d3794 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000009 - Main Earthing System | itp | CABLE ID: FROM - TO
d4e3eab0-eba8-4743-9883-c857fb86fc1f | section | MAIN EARTHING SYSTEM
4c163f6a-5490-44f1-a30a-63be3195e179 | checkpoint | PRE-REQUISITE WORKS
29c25bfa-f424-5647-9d8d-a589832b66d2 | note | Confirm All Work Has Been Completed
2e8db8b2-9fb1-4442-bafb-09a12ccc5132 | checkpoint | VISUAL CHECK
37c7e6f4-2843-58d0-9037-79513c515df4 | note | Visual Inspection – No damage, outlet installed correctly
de113cf1-8776-42d1-98cd-3a93a901fce3 | checkpoint | CONTINUITY TEST
f155e85f-b83f-56da-a969-3fda33c034de | note | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device (AS/NZS 3017:2007 Table 3.2 Max. Values of Resistance)
f823bfac-c029-526b-a19c-ac5f689ba319 | note | 2.5MM 2C+E 20A Type C – < 0.50 Ω
3883e193-b448-4731-a9b6-753ca849d80a | checkpoint | ELECTRICAL RESISTANCE TEST
8879ed39-1487-5844-9bea-5d94939c5071 | note | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device (AS/NZS 3017:2007 Table 3.2 Max. Values of Resistance)
f1c64d5f-6c5f-573d-96a6-b873cf39e318 | note | 2.5MM 2C+E 20A Type C – < 0.50 Ω
fce3d2ac-7c78-5e77-bfdc-9cf1c9cde1dd | textbox | RESISTANCE: |  |  | Ω
fc7151fe-eb12-57d7-abc0-860e65cd6ee9 | textbox | TARGET RESISTANCE (OHM) |  |  | Ω
16b8c94e-c7a6-42e4-b0ad-a88afc098ea7 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000010 - Lightning Protection - RWV | itp | LOCATION
5046a263-77aa-41b3-95af-b6835d207b50 | section | EARTHING
33402065-798b-4be3-a3e9-161e58603ff6 | checkpoint | Rods, clamps, conductors
15a102e8-d322-5759-9bd6-db7bd2ef1a46 | textbox | Location
b5d6fe4f-f137-5485-a533-839969e27c87 | textbox | Correct size
1c40f31a-5766-5141-acf7-044dc26faa5a | textbox | Correct number
fa3c1616-223c-5eef-b69d-6639b8b59dc1 | textbox | Straight and secure
4395fa5b-0c91-4ff1-a954-676aa293f848 | checkpoint | Test points
08e8b995-3e4f-5114-be49-5c3f81d20512 | textbox | Location
51c08209-af0d-579f-8dae-88138075d498 | textbox | Correct number
a0b21fdf-eeee-5f2a-b44d-563968819a8a | textbox | Straight and secure
a39912e9-a5fe-4a6e-9641-7296f0455226 | section | DOWN CONDUCTORS
03f732cc-ee2e-468c-a6ca-53a8654f2ef5 | checkpoint | Structure used
8353c3fc-59b2-5382-ba8d-e0844284f6f7 | textbox | Location
86b6afe8-6f3a-5b2c-b283-07f8e763798d | textbox | Correct number
11043cc5-b532-5934-a45e-121a3366b5b6 | textbox | Continuity testing
d3fcb88e-9f14-4d3f-9a9a-945e984b0438 | checkpoint | Separate
68ebfd3f-3fe6-57d0-88ab-f53cded33167 | textbox | Location
9b73a752-ba46-5091-aec8-4a15b3f35561 | textbox | Correct size
806abbb4-acef-57cc-be05-87cfd8717f74 | textbox | Correct number
daf63fe0-57d8-5350-8225-93612bf13e74 | textbox | Straight and secure
550a41b1-4094-4b84-a997-354bbba1977c | section | Aerial termination;
cb4a0789-e758-4ba0-b98e-41890fc5b838 | checkpoint | Terminals
fbde6469-a331-58ec-a97c-66d85378ec52 | textbox | Location
072db263-d2c8-59c9-8c14-926d4d5c406f | textbox | Correct size
dce60eee-651f-55b1-b26f-aa67590cf1ae | textbox | Correct number
087a2ede-e8a4-5aa9-94b0-2cbd6d69949b | textbox | Straight and secure
da9ab3d0-1802-49d3-abf9-48750dd49dd5 | checkpoint | Strapping
3a0ee2f6-860b-5008-867a-9d3bc80e4d3d | textbox | Location
d2f46476-d7ee-5e4f-9d26-dccc01b5158d | textbox | Correct size
e7d5cbe3-2dd9-5ece-8446-36197648bb9b | textbox | Correct number
7d41eb2b-0c89-5494-9d30-45832b223136 | textbox | Straight and secure
9eeff5e4-b142-4c6b-9133-2fc3249034af | checkpoint | Bonding
18bfe5ed-c4ca-5e56-a0d4-e6887a49b88a | textbox | Location
cb38d289-6260-5ef4-9eee-4b4b5c0aea66 | textbox | Correct size
562be44d-c76e-5f1c-9512-a9259c569761 | textbox | Correct number
189faac7-ba89-53de-8274-49dd8ba5be4e | textbox | Straight and secure
e737a957-d9f0-4e58-b2bd-66c0cce1c330 | section | TESTING
ef229f05-280c-493c-973a-a1acee26f0f0 | checkpoint | Earth resistance test
59d3a4b0-1549-50e1-90ee-bf4e4de328f9 | textbox | Report number
7dcbeb8b-4e9a-422b-b555-49340506771f | checkpoint | Column continuity test
c8c40951-aa39-5ad8-8c38-17aeac6cbfc1 | textbox | Report number
381d4822-5330-4361-8bc8-998600120eda | checkpoint | Full system test
efa2ea11-cddd-5b20-a818-86e7a680d1b5 | textbox | Report number
c9641695-f00c-498c-b235-931aac600682 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000011 - Lighting Circuits | itp | CABLE ID: FROM - TO
ef39ed41-3325-407a-880b-079923adaf84 | section | LIGHTING CIRCUITS
afa769ee-983b-4676-b140-84986b8da5cb | checkpoint | PRE-REQUISITE WORKS
7be6400a-c4a3-5ddb-afac-304e785345c1 | button | DB COMPLETE | YES,NO
36988923-f8bb-5552-a5f7-2fadcd346696 | button | DB ENERGIZED | YES,NO
4d558d6f-a191-5e20-b69c-97f28d8c4c0a | button | DB COMMISSIONED | YES,NO
7254402c-5920-4208-9368-160270b98910 | checkpoint | INSTALLATION CHECKS
1409e039-c545-52a7-835b-8a5127533da0 | note | Visual Inspection to confirm no damage to insulation, Plug bases installed correctly
4b0a66de-fae4-4523-942e-504a2de8d544 | checkpoint | CONTINUITY TEST
0f2eb3f1-dff1-5021-8005-474af5c46fd2 | note | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device
63591842-3932-5033-8524-b83c7c46dad6 | note | EXAMPLE 2.5MM 2C+E 20A Type C – ˂ 0.50 Ω
cdcd4ba7-b69f-5558-aefe-2d01eba24856 | textbox | TARGET RESISTANCE:
8d40ab7a-0c30-4607-99af-b9e6a1445b8e | checkpoint | INSULATION RESISTANCE
60468d4d-0b2c-52ab-85c0-75c50013066d | note | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
6d334083-ab7e-558e-8d57-c11fecadea54 | note | The insulation resistance shall be not less than 1 MΩ.
ad7e1bf1-9206-5ee3-8539-7552e62b5777 | textbox | R-W
92f37878-371e-57c0-9f0a-e34ed6c897a7 | textbox | R-B
3e171d0f-e6ec-57c9-9ed7-50706ed413fe | textbox | W-B
b19c4578-2a9a-54c3-af4c-6e0b5ee6edbc | textbox | R-N
ba2aa75c-2221-5c75-a13e-2cd7cae1a4eb | textbox | W-N
5cfe203c-ac79-5cbd-a303-401873fa48a9 | textbox | B-N
e3797533-5f3e-5537-975b-15e1208b245e | textbox | R-E
78c96853-f591-5676-ac8f-b125455a9757 | textbox | W-E
7b2dad4a-f694-530f-817f-4ade06b7af4c | textbox | B-E
a4f47b15-4def-44ce-a1ad-d935b66b8dd6 | checkpoint | VOLTAGE CHECK
471bfd45-92bb-53a1-aba7-c24067425a5b | note | Test Line Voltages and ensure the voltages are within acceptable range
1f822e99-c476-5e92-a04b-af440f34f659 | note | Aus Grid NS238 6.1.1.1 Low Voltage Supply
cb32cd91-853e-5e6e-9dec-e5b02d6ef129 | note | 230V +10% / -6% = Range 216V to 253V
bf86a6a2-a892-5ec3-9cb7-4f87c5a19654 | textbox | RED PHASE (RECORD VOLTAGE):
a91c0ce5-0625-4271-a5fa-77f7a3b3e220 | checkpoint | POLARITY CHECK
e4b8071e-abc1-5d2f-ae57-67f44b9b6b13 | note | AS/NZS 3017:2007 Polarity – Ensure that no shock hazard results from the incorrect connection of active, neutral and earthing conductors
88786f93-888a-5f56-b8f4-f33fca98628d | note | Verification through continuity testing of each conductor
ad967396-a36c-5afd-adf9-1f78e3cdae59 | textbox | NO TRANSPOSITION
833b55cb-43cd-56c7-9a8f-c120f67f11ef | textbox | SWITCH IN ACTIVE
482f767f-ba48-4cf9-9e97-f3fcbbefad36 | checkpoint | RCD TRIPPING TEST
daee56df-db22-5e2c-a4b6-ce3678aa4aaf | note | AS/NZS 3017:2007 Ensure the RCD operates and disconnects the designated circuit.
1507085d-09e5-5ec1-8d65-5f607e2ac9ba | note | Testing must be completed using an integral test device, the device must apply the rated tripping current and measure the tripping time.
46dac0be-2c3b-54c4-a4b6-64a46568730c | note | Type of RCD: General Tripping Current; 30Ma Max. Max. Tripping Time: 300ms
5f6f7d17-97ca-5adf-a91d-bdd853d04c79 | note | Result < 300ms
5c019eba-8f5d-5e66-83df-e32dc455d341 | textbox | TRIP CURRENT
6ffb84d8-8cc0-5ace-b1a0-154fd13a8452 | textbox | TRIPPING TIME
86548d7e-34c4-43f4-91cb-61a380c62050 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000012 - Lighting Control - Automated | itp | LEVEL / NETWORK
fbc74ca2-35df-4faf-be5e-229aa1bee19f | section | INSPECTION AND PROGRAMMING
aaca9df6-41ec-4fa5-9819-3e411fe5b34e | checkpoint | Dynalite equipment Load schedules completed with circuitry information for each output equipment by flash testing individual outputs
cc9bdc39-bd66-4227-97f9-3c7b864281f0 | checkpoint | Testing of output unit for each DALI universe operation by flash testing individual outputs
7f1a0ab1-94a4-4bd8-b31f-3d7915ea19ae | checkpoint | Field input lighting control equipment (Switches, occupancy Sensors, light Level Sensors) installed and terminated as per specification
c6f04d20-af8a-4705-9b11-f467d94f6469 | checkpoint | Input commissioning sheets complete with field device information
66c01aea-bbb3-4bbb-8ae0-682e13ec776a | checkpoint | Programming of DALI control units as per zone mark up
408fbf2b-403e-43a6-ac8c-1ce796367a56 | checkpoint | Programming of lighting control input units (Switches, occupancy Sensors, Light Level Sensors)
8795585c-487f-4f63-be3e-2ad63f5ab755 | checkpoint | Touch screen operation tested
dd28c2ac-8d75-45c8-9e37-dd92d4ca5518 | section | COMMISSIONING
f63db462-d90b-4c44-a469-d2847676272f | checkpoint | Tested power failure recovery system isolate power to control system
6565c4cb-25b4-40be-91f8-e17822b07816 | checkpoint | Addressing of Network Bridges and gateways ping test via ICN network
7d8f0990-b836-4998-b07a-920af6fa2bb9 | checkpoint | Allocated devices responding to allocated addresses via Ping test
65fa610b-10e6-4f4f-903f-4f8b47239a95 | checkpoint | Tested Head End operation and control functions
aabe3469-de2b-4817-bcc6-3281f7ccbbe7 | checkpoint | Mapping of Graphical data points (read/white), Manual controls buttons
5c4a55ab-7569-4dc7-a53d-cd7db5beec8d | checkpoint | Witness testing verifies correct control
af6196fd-657f-4094-8911-363e9f2b3097 | checkpoint | Device functionality confirmed
909b9c66-a6ee-4cd9-9335-0235e72e1d84 | checkpoint | Realtime reporting demonstrated
f60575ed-b4ec-407a-b43d-f76cd02b4e08 | section | TESTS
4e7b553f-fa27-401a-88ad-7a244b5907d0 | checkpoint | Test Required: Functional
387ba2df-8113-5610-9ed3-546937c0642e | textbox | Functional sections
7edbb32f-1fe0-4acb-87a9-b0f9721dcdac | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000013 - Emergency Lighting | itp | FITTING ID
d6355a41-5ceb-4d72-90a1-78a6458a265e | section | EMERGENCY LIGHTING
0cfc25bd-d871-4467-970c-7426c4c976d2 | checkpoint | PRE-REQUISITE WORKS
2beffc04-95d9-43e5-8e3e-3656eed8f2bd | checkpoint | CORRECT LOCATION
e5c840eb-15fe-4acd-8b80-a2e23cdb32af | checkpoint | CONSTRUCTION AND FINISH
c646c714-2c7b-401e-8f1c-a9dfb0cef50d | checkpoint | LEVEL AND ALIGNMENT
9a6d2e52-837d-4ba0-9ccb-85ef6a0da94b | checkpoint | ACCESS PROVISIONS
e7e7e8b9-986f-45fc-923b-4d05f73adf84 | checkpoint | EARTH CONNECTION
7a1ac2d4-e8bf-48cf-a143-12e653a66bf8 | checkpoint | LABELLING
5c5346d6-f8f4-428f-af98-6c910c7d25f6 | checkpoint | DISCHARGE AUTONOMY TEST
7bcea4cb-b2b7-4b92-ba1e-15729bdf5d64 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000014 - Power Outlets | itp | OUTLET #
164d7539-4448-46ec-b0d0-564e958b821d | section | POWER OUTLETS
f1dd7777-d442-4ec2-9853-3de77618408d | checkpoint | PRE-REQUISITE WORKS
f7f2a192-1ff2-5241-916c-722d2ad193f0 | note | Confirm All Work Has Been Completed
d7cc74f8-68f8-4851-9202-52091460f9e2 | checkpoint | INSTALLATION CHECKS
d37a0003-24d4-5487-ab5d-4a51e0dc52a2 | note | Visual Inspection – No damage, outlet installed correctly
726392e6-c04c-4e4b-8eea-dd509da32e11 | checkpoint | CONTINUITY TEST
78986652-edbd-5a53-a09f-1a3b3aba1aa8 | note | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device (AS/NZS 3017:2007 Table 3.2 Max. Values of Resistance)
d9b0f317-c9f4-5188-ad0c-a7b88af3b52a | note | 2.5MM 2C+E 20A Type C – < 0.50 Ω
0835b456-5f0a-5f37-90e9-0e5b9fdfe6b9 | textbox | RESISTANCE: |  |  | Ω
a70c7c61-0ecb-5d8b-9e03-51d987ee5654 | textbox | TARGET RESISTANCE: |  |  | Ω
254f5921-27e2-410c-8b8f-61a28a13aba9 | checkpoint | INSULATION RESISTANCE
df079988-f42c-577c-a7b2-c274d8726fee | note | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
e1ae0454-a5fc-5bec-bd39-5131ea28862c | note | The insulation resistance shall be not less than 1 MΩ.
4a6e013c-c3e8-51c1-991c-9bcd2bbedbb8 | textbox | R-W
3943ee30-60c8-5b57-9384-b24c06d09718 | textbox | R-B
4498a69f-85f4-53f3-8a4d-64b9169d1cd3 | textbox | W-B
e90271b5-5ae1-5db9-8265-5f480deeb1a6 | textbox | R-N
2201d0e2-269a-5db7-ac6d-25ea6f090ae2 | textbox | W-N
ecc1037b-262d-56b8-b108-1d1d6a854077 | textbox | B-N
55d8b46e-6538-5a90-a487-eb699c09e84e | textbox | R-E
f859b5e5-db7c-5173-9cdb-335241f50658 | textbox | W-E
86f52bdc-7e46-58e7-91e0-b9c58b1b8844 | textbox | B-E
6c566825-6013-4ab1-84e3-4b6c6920329b | checkpoint | POLARITY CHECK
8c7e524e-e3a5-5e23-ba3c-96c9db9435fa | note | AS/NZS 3017:2007 Polarity – Ensure that no shock hazard results from the incorrect connection of active, neutral and earthing conductors
4234bf11-6e1b-5d05-aaa4-03feb9cf925d | note | Verification through continuity testing of each conductor
167e44ff-1ccc-53bf-9315-29f0aaad053c | textbox | NO TRANSPOSITION
e25d0a89-551c-5579-8df1-b59981dd57c5 | textbox | SWITCH IN ACTIVE
a5cd86ce-cbb4-410a-9e97-e024e1918d9a | checkpoint | EARTH FAULT LOOP IMPEDANCE TEST
f9633e08-e777-544e-851c-9b59b9aec624 | note | AS:NZS 3017:2007 The earth fault-loop impedance of a circuit is measured to ensure that, if a fault of negligible impedance occurs between an active conductor and a protective earthing conductor or an exposed conductive part, sufficient current will flow in the earth fault loop to cause a protective device to operate within a specified disconnection time.
1094249c-f9a5-59c3-8115-766e73150b5b | note | 20A TYPE C PROTECTION 1.53 Ω.
4c883a34-c8fd-57a3-b11a-b30afe15f730 | note | 32A TYPE C PROTECTION 0.96 Ω.
2cbbb186-70a2-5ecc-a399-e3e2b7520d62 | textbox | IMPEDANCE: |  |  | Ω
64d83729-4d7c-585d-b8cc-20eb615b4c4d | textbox | TARGET IMPEDANCE: |  |  | Ω
edd5a9f7-4856-4594-a56a-240d38c2cfb4 | checkpoint | RCD TRIPPING TEST
b7d5a498-7b39-5824-9507-4e6bd265342e | note | AS/NZS 3017:2007 Ensure the RCD operates and disconnects the designated circuit.
50d5947e-dae6-58f4-b266-d0902f689c79 | note | Testing must be completed using an integral test device, the device must apply the rated tripping current and measure the tripping time.
b4089d1a-d2a8-5835-89f1-91694e812bc1 | note | Type of RCD: General Tripping Current; 30Ma Max. Max. Tripping Time: 300ms
94cf0e56-882e-5bf4-b7d4-062c90394000 | note | Result < 300ms
886dcb34-7df1-5b61-8949-4f4444ed5dec | textbox | TRIP CURRENT
0b655ad7-963f-5660-9596-a201f7afda05 | textbox | TRIPPING TIME
338ad1e3-e7e5-4dd4-ba01-b45c8058be3f | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000016 - PFC Equipment | itp | INSTRUMENT S/N #
12505f2f-bceb-43f9-8fd1-711b8956c83b | section | INSTALLATION INSPECTION (WARNING: SYSTEM MUST BE DE-ENERGISED)
c08157e3-060b-443c-bf21-bbd9483db32b | checkpoint | SIGNS OF EXTERNAL DAMAGE
b1fd51bd-3ea4-4836-8fbd-7930c445bf9a | checkpoint | SIGNS OF INTERNAL DAMAGE
2d245191-d703-4fba-a034-6da419018fa0 | checkpoint | ENCLOSURE SECURELY MOUNTED
a454e432-427a-429d-8c65-5206d1521533 | checkpoint | ENCLOSURE VENTILATION
e3c48ea8-307b-4325-b922-9a893f936e26 | checkpoint | SIZE OF POWER CABLE
96c1c61d-99a5-46ce-ba9b-ee85cf9aa8e5 | checkpoint | SIZE OF NEUTRAL CABLE
43dd2729-87eb-423c-85b5-a428daa5d69d | checkpoint | SIZE OF PE CABLE
36a32f36-5746-4eb7-ac00-21eb8e574888 | checkpoint | CABLE CONNECTIONS
ef56fa73-f424-4d6c-b3b4-473ff17b52ac | checkpoint | PHASE SEQUENCE
4a196620-8ff5-40f7-8e34-12954a9bd6c7 | checkpoint | POSITION OF CT'S
9e8bbf0e-5e23-47ad-9040-540b90c7ae80 | checkpoint | POWER FUSES
11dc3931-dd12-481d-8d94-48a72c48ba4b | checkpoint | CONTROL FUSES
0837c976-5de3-42ba-b1af-acc1507db2d8 | checkpoint | CT LINKS
9d428c2a-db3e-4c5d-8c1a-4bb8ec2cb165 | checkpoint | INSULATION RESISTANCE (WARNING: SYSTEM MUST BE DE-ENERGISED)
a1e42362-3d50-5405-8d3e-8e6c8d406273 | note | MEGGER VALUE: >200MΩ
90ececc3-86e2-54f0-b025-e28f4377e2a3 | tickbox | L1 - L2
49be9021-117a-5f32-90a2-65af655e296e | tickbox | L1 - L3
877bf748-3a39-58c8-9cba-6e968118a4f7 | tickbox | L2 - L3
0ede3efc-db07-5bb9-97ff-86bdc854e5b3 | tickbox | L1 - N
4bae0799-22c4-54f5-a3c7-d0dc7572ed12 | tickbox | L2 - N
65a5ab3e-1fe0-5b37-8cb5-e75cf5226c29 | tickbox | L3 - N
7cc6454c-afc7-5b49-bff4-e3e569e43e94 | tickbox | L1 - PE
13af1c60-21af-5e49-8bcf-6bb408b5b92c | tickbox | L2 - PE
eed6918d-e296-549a-a789-7982177057dd | tickbox | L3 - PE
95859d12-3798-544e-bbb0-003bb9f36111 | tickbox | N - PE
ade70c73-49a1-533a-9ee1-9aa42fb73159 | textbox | other value (specify)
a5790f70-5c24-4f75-9273-aa42edc4e08f | checkpoint | RESISTANCE OF EARTHING SYSTEM (WARNING: SYSTEM MUST BE DE-ENERGISED)
7dc0223a-4baf-5a84-b36f-055bf3590f31 | note | MEGGER VALUE: <0.5Ω
e92cad0a-3a04-5868-ab17-d58194f8ce9f | tickbox | GLAND PLATE
2e1e05ad-e1c6-59cc-b782-c3c97469f94b | tickbox | ENCLOSURE
c2fb0622-9668-5a0e-b489-0709d2180008 | tickbox | DOORS
306c480d-de25-5a8c-97de-1951a2994fc2 | textbox | other value (specify)
76258d7f-6733-4c81-bc24-66124a58cf5f | checkpoint | CIRCUIT BREAKER SETTINGS (WARNING: SYSTEM MUST BE DE-ENERGISED)
b21deeaf-578a-5c9d-b862-cb29f8bf5ce7 | tickbox | CIRCUIT BREAKER INSTALLED in switchboard
2d7bca78-271a-5bdc-892d-fd0b7090a5a1 | tickbox | CIRCUIT BREAKER INSTALLED in HAPFC system
649156f7-ea24-5fd3-b314-26afb2c75188 | note | PROTECTION FUNCTION - Long Delay Overload
2b117fe8-dc6a-5495-becc-8b1de3c09c6b | note | RECOMMENDED SETTING: 1.25 to 1.5 times In
9b429bb2-12de-56f8-9343-0595996dc24d | textbox | SETTING AT COMMISSIONING:
b6a7f65f-1972-5b17-a5d4-a0cf2512f66c | note | PROTECTION FUNCTION - Instant Short Circuit
936bf0ec-9817-5641-9384-e6d0efffadec | note | RECOMMENDED SETTING: 5 times In
7cbc05f5-f271-5ebb-b00f-74a840b762d9 | textbox | SETTING AT COMMISSIONING:
67ef96c8-958a-5a3b-81d9-fe8d19f073c3 | note | To determine In, use the following formula:
41ff1ee6-b481-51ae-973e-c4409a0fa335 | note | In (A) = ((Q kVAr/50kVAr) x 70A + IAHF)) x 1.3
a676ccbd-78c5-55e3-a78e-efe2411aac94 | note | Where:
23985855-9047-5b71-8c86-78e727db65c6 | note | In – Total Nominal Current of HAPFC unit (expressed in Amps)
40978723-a02a-5d49-856d-9f9620a2c6a8 | note | Q – Total Nominal Reactive Power of Capacitor bank (expressed in kVAr)
417f69bd-89ec-531e-a40c-e686390bd288 | note | IAHF – Total Rated Current of HPQ modules (expressed in Amps)
c72bb4b6-fd7a-559e-9fa9-2ec5e66eb4f6 | note | NOTE: IT IS ESSENTIAL TO CHECK AND MAKE ALL NECESSARY ADJUSTMENTS TO THE HAPFC CIRCUIT BREAKER(S) TO ENSURE DISCRIMINATION IS CO-ORDINATED WITH THE UPSTREAM PROTECTION.
067f7066-8e15-4eb2-9148-7a0faeba4d02 | checkpoint | THERMO CONTROLLER (WARNING: SYSTEM MUST BE DE-ENERGISED)
1d9f750b-ef36-5118-89bf-c6c9a39e4e14 | textbox | STAGE #1 Set to:
87f45838-0987-5c2c-839a-ccf5e75c86f6 | textbox | STAGE #2 Set to:
b9b27839-c16c-4199-96ce-a79a5aab8ea4 | checkpoint-no-value | CONTROLLER
3b8f0b3e-de31-5df0-9e06-930fb8680632 | textbox | Model
7a283bb5-78a0-5c63-9bfc-e4d15ff2dbd4 | textbox | Serial Number
77b5cb68-e796-5b7e-9715-bc38dfedebdb | textbox | HMI Version
76dc1ac3-a1d1-50fa-974b-234546491406 | textbox | HMI Data Version
385c40ca-bcef-4293-9aad-5a3dbc79255a | checkpoint-no-value | HPQ MODULE - MASTER
aa090661-115f-5845-9523-9ebc8e316643 | textbox | Model
9f4faa46-45dd-5250-92ac-c9e0b49770a8 | textbox | Serial Number
6664d315-e3a5-5d16-ba4f-853f642cda2d | textbox | Manufacturer
d4750e84-550f-5052-ac60-74242dbc8db3 | textbox | MCC Version
aace0179-4ac9-471a-aa99-56001a0e8c2c | checkpoint-no-value | HPQ MODULE - SLAVE
66dcc161-089a-542a-be82-43bf917495a3 | textbox | Model
c29a0f56-4366-5679-92bc-a412b4ddcb08 | textbox | Serial Number
881c950a-38af-5f94-80ea-6b9580022538 | textbox | Manufacturer
962affe8-df6c-523b-81af-67354d4bcfcf | textbox | MCC Version
539fd41d-2758-4684-8a77-05dacbfec528 | section | CAPACITOR BANK (UNIT MUST BE DE-ENERGISED)
7993dfe7-8ec8-40ca-b5bf-6f63c311c7d4 | checkpoint | CAPACITOR BANK
fb00200e-a631-5fe9-94db-2f4e71b69a00 | textbox | Stage:
2445e267-2e3e-5f51-851f-c4ade0a293ca | textbox | Size, kVAr:
8bd9ce03-d30f-5c9d-8437-497a2ff593e1 | note | Capacitance, uF
c176e530-d14a-5b36-a7b4-5400c786b7d6 | textbox | L1-L2:
f5dcbba0-7aa4-593f-ad08-73c26cdf1a35 | textbox | L1-L3:
cfa46072-ae26-53b6-ba2f-7cdfa84ef8f0 | textbox | L2-L3:
e194bdca-431d-4447-a012-35ca263208cc | section | VOLTAGE WHEN SYSTEM DE-ENERGISED
c5fd3802-7e21-4c89-a90d-b0173581c4d8 | checkpoint | LINE VOLTAGE
57452a92-40c3-55a1-85d4-21e3bea91f1b | textbox | L1-L2
3b7d4c93-5764-54e7-aa9e-2fff7d64fb03 | textbox | L1-L3
974a91a6-da70-5e69-8844-5c4626a00027 | textbox | L2-L3
bef254ec-ecb7-45e6-a3e7-4b9181095359 | section | CAPACITOR BANK - CURRENT
46da5502-315a-4866-b3c8-e845c88f25cf | checkpoint | CAPACITOR BANK - CURRENT
e911737e-b65e-5091-8f85-173521c5a583 | textbox | Stage:
c9bc4bbc-7095-5065-8d1a-bb30a04c38da | textbox | Size, kVAr:
e191ae64-d1eb-5e2e-aa8d-0fe690d562e0 | note | Current, A
502242d6-c56f-505f-8cb3-c594a0a5b876 | textbox | L1
969ed21e-86eb-5383-9b18-49cb7e9ebb71 | textbox | L2
0c3e66a2-ea70-5bd5-b46a-6d43f731ed4d | textbox | L3
61abab20-be94-423c-bb5d-0ddbe2e47034 | section | CONNECTION SETTINGS
b43ed669-1ee0-4c4b-9d9b-09e86f6f7b95 | checkpoint | Controller
2b715224-6d09-56ca-b1bd-f64f1979ab0d | textbox | Name
a100df63-b1f5-549d-8ad9-1b200b3764e4 | textbox | IP-address
7cc1ef39-57ba-5c2a-ae89-abb01d5c2ea7 | textbox | Port
56105f35-bc06-4340-97f1-4591d1a354fd | checkpoint | HPQ Master
20e5a269-ebce-5004-80a7-12b1c820ef80 | textbox | Name
a199e33c-a9aa-5025-b971-68c6e285702c | textbox | IP-address
582bbd21-eca7-5dd2-8deb-167ffb1ef81c | textbox | Port
6382016d-1905-432c-827c-58c95ffe65cb | checkpoint | HPQ Slave
30c9308b-252d-5cff-bd71-38a8a60fefd1 | textbox | Name
7a19beda-7990-50d5-81fa-39e9e636c474 | textbox | IP-address
87ae5ce3-4502-51ef-ac28-17c073f62f38 | textbox | Port
879eaf1d-28a6-4fde-9664-fbb294ed8b64 | section | HPQ SETTINGS - COMMISSIONING
130dd36c-7c37-427b-8b71-821de375cf40 | checkpoint | ENABLE IGBT OPERATION
2804fef0-99e5-520d-a966-13d2363cd68e | textbox | HPQ - Master
44b23f6e-ddae-5a16-ac48-43dea385a12c | textbox | HPQ - Slave
0cf8fd51-73c9-4723-ba93-255d06fbd55c | checkpoint | CONNECTION TYPE
3971ddd9-6700-5491-a0b8-f19fd9e7c97c | textbox | HPQ - Master
d3515166-31ff-5a80-9153-b0698221716c | textbox | HPQ - Slave
3dd0881c-745a-4040-a4e1-3752caaed872 | checkpoint | ELECTRICAL CONNECTION (3W/4W)
e8e7ae92-d882-54e6-8d56-788287bc90da | textbox | HPQ - Master
aa0e910d-a340-5e95-b324-928e65560020 | textbox | HPQ - Slave
f699d9a3-ec48-47ed-ae40-c66a8565b38c | checkpoint | CONFIRMED FREQUENCY
70d0a339-0a4b-51cd-893f-b41b7ff50074 | textbox | HPQ - Master
19b2981d-b2a2-5067-8ace-eb5236ef03de | textbox | HPQ - Slave
710d9421-587e-4ca9-b7d4-6922911db2ab | checkpoint | Confirmed voltage
e6eeb6f8-def7-5ddb-99b3-bbbc8b92a813 | textbox | HPQ - Master
fb4acc70-319b-5bc8-aeda-545262308a02 | textbox | HPQ - Slave
8a032045-752e-4647-ab6c-4da1f707e636 | checkpoint | COMPENSATION MODE
a3f85df5-90a2-5b36-9c05-ef63e5bfd8c5 | textbox | HPQ - Master
13c9c949-66e8-570c-9497-dbafc8036689 | textbox | HPQ - Slave
56ad98d2-e693-45d6-954e-fcf3072c60ab | checkpoint | BALANCING DEGREE
2d12aef0-5ac7-55bc-b066-f19427ffef39 | textbox | HPQ - Master
6f421892-85d4-5db5-a729-269c3daee532 | textbox | HPQ - Slave
3bd05f6f-5f47-47d6-9173-3867cc5c806f | checkpoint | X1 CT-RATIO (CUSTOMER CTS)
1d3de979-b734-595c-8465-bf19435776e1 | textbox | HPQ - Master
05d2a478-d5a0-50d7-b401-4537ee3a6131 | textbox | HPQ - Slave
fa1db2ac-b6da-4792-82e7-fd6494cf3e34 | checkpoint | TOTAL INSTALLED CURRENT
a11aff1f-257c-5873-90c9-e460fb7b2e28 | textbox | HPQ - Master
5f8f5e63-2faf-569e-97f7-19178d47f28e | textbox | HPQ - Slave
26a01378-b507-4db7-99a4-e407f6610556 | checkpoint | X3 CT-RATIO (AUXILIARY CTS)
e071f555-be3e-53bd-b69b-d9cef45efc73 | textbox | HPQ - Master
accb7a2c-4a99-5c2b-be5a-0bbb2f68af2e | textbox | HPQ - Slave
09c4f1d2-f25e-497b-ab50-71d8d545f2fe | checkpoint | ENABLE AUTOSTART
41cc0bf4-c7a9-57e7-80f8-5837686192de | textbox | HPQ - Master
bb0a6946-49da-5640-b868-7a33d4d091f0 | textbox | HPQ - Slave
33c54340-9c98-4621-935a-32d807cb746f | checkpoint | ENABLE AUTOACK
b9ebfd66-2a37-540a-a691-f681765732a9 | textbox | HPQ - Master
4d40f651-f58f-5861-a00c-a33510a02289 | textbox | HPQ - Slave
7577ab5e-5944-40bf-80ca-9e765eb75869 | checkpoint | ENABLE STAND-BY
56b89459-5bcc-5ae9-9a1e-bd6be758625d | textbox | HPQ - Master
836642b1-8c5c-5ee4-b7a6-a10ef67fc5cc | textbox | HPQ - Slave
401b894a-40d1-405f-b2d7-f33156b2bc32 | checkpoint | STAND BY TRIGGER LEVEL
dff94467-f7f4-59e4-9204-a53b48f4f688 | textbox | HPQ - Master
737a103a-593c-5f60-8b66-989df2b7cb79 | textbox | HPQ - Slave
69ba6814-614e-4df5-a217-00fe85991f0f | checkpoint | X1 CT-POLARITY L1
39f94ced-5bb0-57d7-bed0-3a7c2223e469 | textbox | HPQ - Master
d5fdc1b9-4e70-574b-a39c-82fc2f4c03aa | textbox | HPQ - Slave
a3fa35f4-dbd9-477c-af6b-0540f3e9e124 | checkpoint | X1 CT-POLARITY L2
024304da-c987-5b6c-a7fa-4132afcac5d8 | textbox | HPQ - Master
427e1724-0558-5e8a-bf2c-cfef9c0d609a | textbox | HPQ - Slave
6ee8a9fc-ec41-44d3-bb43-d366679b56c8 | checkpoint | X1 CT-POLARITY L3
6d7d901c-3923-5680-89e6-75466904278f | textbox | HPQ - Master
b31ac628-be7e-5f00-942f-ee6c006f1398 | textbox | HPQ - Slave
cb700ba1-e06a-4ee3-b3d8-057f21cb0e5c | checkpoint | DIGITAL OUTPUT 0
2cc53712-8a74-5b1f-ad78-a1395e570052 | textbox | HPQ - Master
2fecd719-0895-5049-aa1e-549b8580ce6c | textbox | HPQ - Slave
b37b2299-d3df-4414-b6f6-2febd0fccb89 | checkpoint | DIGITAL OUTPUT 1
850c7a94-5bfb-545f-8f28-23ca37e0959a | textbox | HPQ - Master
2da47957-259f-5bc2-8358-ec958e0dfc53 | textbox | HPQ - Slave
1e2c861d-9896-4f68-a6de-fdcc885f5b90 | checkpoint | DIGITAL OUTPUT 2
aa114f5c-1ffd-5cd4-ada8-fd2f06c44f18 | textbox | HPQ - Master
74da8d13-c717-5946-bd95-5ae5bf056e59 | textbox | HPQ - Slave
8fcb54e0-34f9-4d2a-aa56-74afdc264e09 | checkpoint | DIGITAL OUTPUT 3
012031c9-275e-51e0-a89d-1524037092e2 | textbox | HPQ - Master
28435717-7171-5edb-be2c-d26d4cc16b5c | textbox | HPQ - Slave
e9dfb7c2-2d06-49d7-9ec7-e59ce8a21347 | checkpoint | DIGITAL INPUT 1
04c1b174-e865-5787-a0b6-55a123a188b1 | textbox | HPQ - Master
008a4bc8-794b-5731-87ed-7f8c2083d58d | textbox | HPQ - Slave
fa57b953-ed5d-4ebe-a517-22f4573e7462 | checkpoint | DIGITAL INPUT 2
5c496551-d9e5-5d52-9c05-8da593748fa0 | textbox | HPQ - Master
523de987-7439-575a-ab0d-7545914c24c8 | textbox | HPQ - Slave
4f45beec-c69e-47e4-a6be-23fc862a291b | checkpoint | DIGITAL INPUT 3
ebf88969-e7c3-5381-ba6c-bcb2ca0794b7 | textbox | HPQ - Master
218011dd-9a6e-59ba-bad7-b570b4ecbb26 | textbox | HPQ - Slave
27fba68a-3978-4a07-addd-407ff407cd7a | section | HPQ SETTINGS - HPQ PARAMETERS
202f38b5-2eda-4e59-8679-327dafeeab1f | checkpoint | Enable HPQ
fceebb82-8d6f-5664-9cce-482473ff0da5 | textbox | HPQ - Master
cab293e0-07cc-5ee2-9afd-c6658fa78836 | textbox | HPQ - Slave
42ac24b3-6329-4344-9637-401001e24bfe | checkpoint | HPQ-MODE
fc3e43c8-70c9-5d78-906d-4b95583e188b | textbox | HPQ - Master
9a822b95-1374-5bb1-914f-16c34237bd02 | textbox | HPQ - Slave
5cb5a807-4a46-4ec5-b5ba-2d8e0ee04dad | checkpoint | UNIT ROLE
790c5389-c3a9-541f-9c01-7c03df63b34c | textbox | HPQ - Master
4ca94cc7-1059-5fc3-a9eb-f916e09ff06a | textbox | HPQ - Slave
854aada5-0315-4e47-a30c-2a7eeaa44626 | checkpoint | ENABLE FO
b14a9921-6a23-53a2-bec2-a20bdfb6159a | textbox | HPQ - Master
8d2be7e7-bd9d-5a3c-8632-f7272fb1b35f | textbox | HPQ - Slave
42e7a6fb-e20f-42c2-934c-14fe61470d77 | checkpoint | OVERVOLTAGE LIMIT
88675dd1-5406-5871-8cde-aa44d265bfd3 | textbox | HPQ - Master
3c483812-b234-5987-9fd6-dfa2cd7cefbb | textbox | HPQ - Slave
59faa39b-5682-4783-b06e-6949334096e1 | checkpoint | THDU TRIP LIMIT
593a508c-332c-5651-8497-12356fe77491 | textbox | HPQ - Master
d2ae3ed8-9de9-57a2-ab6b-3490631ecc42 | textbox | HPQ - Slave
45df0b92-056f-470a-8833-fc57f4b4513e | checkpoint | STEP COUNT
3f50ee12-060a-5b17-925b-0b66c931e952 | textbox | HPQ - Master
b42af45b-2d5e-5b04-8a64-2b8b9fa6d313 | textbox | HPQ - Slave
8bb751ce-57b4-466f-aeba-6605cb0ebce8 | checkpoint | STEP SIZE
655edc38-6c15-5a39-af98-1e609ade2a52 | textbox | HPQ - Master
a241db98-8b92-53eb-ab6e-33b8041ce7d6 | textbox | HPQ - Slave
4b97e645-ecf5-4516-9d70-d186b1afc876 | checkpoint | SERIES REACTOR
c28c8d09-aef5-599b-a8c4-397cff4a8c96 | textbox | HPQ - Master
08a726b4-fbdf-52a8-bea3-eb11eeafbdda | textbox | HPQ - Slave
99b439d2-dd39-4624-9098-8472d6993549 | checkpoint | RATED CAPACITOR VOLTAGE
4030a904-2531-5dac-9037-6895c6c5bf6a | textbox | HPQ - Master
8e19f234-8343-574b-899b-5b26373f1a0a | textbox | HPQ - Slave
b0b468f5-877c-40bd-99a3-3e4e2e4bcb43 | checkpoint | HYSTERESIS LIMIT
57840964-d0f9-5570-8b05-4d30ad8ccc1e | textbox | HPQ - Master
4e9a3f2f-9e82-598c-b085-4a3ecb7fad2f | textbox | HPQ - Slave
e90e600c-9ab9-43e9-b7f9-92e9e59b57b6 | checkpoint | DISCHARGE TIME
178024ab-cb97-5433-b5ec-30b3d0504f90 | textbox | HPQ - Master
4db140ce-4148-56a5-a258-2f525d39c9a5 | textbox | HPQ - Slave
8cc3e62e-0146-4ca8-85b5-9f14b7c8a07d | checkpoint | ENABLE LAST DO AS TRIP
199652fd-4501-52db-8bc8-65df40845f9b | textbox | HPQ - Master
f6ba91d7-e7c3-54f6-923b-09416410cf67 | textbox | HPQ - Slave
0c993197-985c-403c-87a8-6ef3c9480fec | checkpoint | CONNECTION ALARM COUNT
5a899517-b4e9-5079-8e18-389642507fe4 | textbox | HPQ - Master
175685f1-e6f5-5653-9682-30e1204e219e | textbox | HPQ - Slave
98a1cf7b-7ae8-4807-8743-cc5c5130bdcc | checkpoint | TARGET POWER FACTOR
1f7ac9c6-f849-5dc3-8c1e-acaf818500a4 | textbox | HPQ - Master
cd1066ff-d60f-59c7-aa91-03d871ff531a | textbox | HPQ - Slave
339c5d50-f9db-488a-9bc5-3c31986fce2c | checkpoint | CAPACITIVE POWER FACTOR
b4e74a60-47d9-5cbf-8bd8-65e6ca5f383a | textbox | HPQ - Master
dbe32c86-df53-5498-9569-de31a289fcdd | textbox | HPQ - Slave
b0b7dad1-285f-4f7c-a0ec-ebbccde82ee9 | checkpoint | SECONDARY POWER FACTOR
0ec0ce8a-2df9-547a-a717-679150756bab | textbox | HPQ - Master
ef1877f7-9b8e-5d9c-a3e0-990ffcbc83c6 | textbox | HPQ - Slave
c2f8be31-3429-4f71-ab5c-b94e23e0d05d | checkpoint | PRIORITY CURRENT LEVEL
003c067b-24aa-5b64-9467-7f6b52edac98 | textbox | HPQ - Master
63a10430-351a-57a0-b446-7a4db68a1761 | textbox | HPQ - Slave
7dd7b3de-e678-4e54-8ba8-cffe99e57d1c | section | HPQ SETTINGS - COMPENSATION DEGREE
147ff577-0ef7-48df-8280-3c8321a039f7 | checkpoint | Ih2
0c93da54-0460-51f0-9716-2bb27e3c0a69 | textbox | HPQ - Master
e3c752bd-f429-5286-954b-c1ec7402242b | textbox | HPQ - Slave
9781b4f3-da08-4039-a546-ded95d1541f4 | checkpoint | Ih3
dd0da493-57eb-52a6-a1bc-02fa098c4848 | textbox | HPQ - Master
2583cb97-0835-5bd9-9710-9ebe784547eb | textbox | HPQ - Slave
ea985fd4-8717-4797-b056-c8aa62f44d3d | checkpoint | Ih4
7b93cdde-bcba-5df2-a2a5-b9fc3343132d | textbox | HPQ - Master
8650cecc-07b5-5c05-9b45-19e3a0d7c0f6 | textbox | HPQ - Slave
15e3a6d4-f7c1-4275-adb6-5b2c4ca1ca55 | checkpoint | Ih5
fe1522e8-650a-5c87-abdc-20cdd2f7597f | textbox | HPQ - Master
071eda75-efc3-5b14-aeea-c64bd3d69db5 | textbox | HPQ - Slave
792c28bf-f37a-4018-bccf-140dd199ee12 | checkpoint | Ih6
64e3be44-73b9-5770-af62-c7a778ef87fc | textbox | HPQ - Master
b7b8c7af-a918-51dd-96ef-6ea29767b796 | textbox | HPQ - Slave
fd8b3a27-8d78-4ee0-ab58-4e67f7570faf | checkpoint | Ih7
3d556409-dbdc-56df-bc1d-1a918dc0cfa0 | textbox | HPQ - Master
858e0eb6-92ab-57c0-8ac7-a89c8c06d2d9 | textbox | HPQ - Slave
209f6d6f-e260-45b3-90d9-fac0cfcf0b86 | checkpoint | Ih8
8f23f540-5e75-5f22-ad29-1b80686ee718 | textbox | HPQ - Master
6697e502-d53c-5efb-b3fe-5d7e377aafaf | textbox | HPQ - Slave
fac7e50c-640b-4775-bcb6-18f1888407c3 | checkpoint | Ih9
74ee786b-f837-5800-aa37-b18015c726aa | textbox | HPQ - Master
5f77c28e-a881-5775-a971-d048ff589882 | textbox | HPQ - Slave
db46a7b9-947c-404d-a66f-797630185758 | checkpoint | Ih10
e098d777-335f-571d-95ef-b3a8a4c712e3 | textbox | HPQ - Master
5b316997-9d6f-5576-a4d6-b92d41fd6b9e | textbox | HPQ - Slave
53c43281-125e-476b-b9d9-fe2084bc13c5 | checkpoint | Ih11
16e7bdd4-9329-5ce9-ad81-eaa19de8e269 | textbox | HPQ - Master
f4ea953c-7b68-58cc-a088-6dd560a834c4 | textbox | HPQ - Slave
eef7c206-1c33-47d8-ae49-c7ad3cc23cdf | checkpoint | Ih12
167c1679-6128-57c6-894c-80391fbf7a6f | textbox | HPQ - Master
318df3e1-04da-5b5e-bb73-0680735c6fdf | textbox | HPQ - Slave
246dde42-4aab-4524-a767-7fb45e70d0ac | checkpoint | Ih13
38e4f721-0d13-55af-8fe2-cad068d8646e | textbox | HPQ - Master
b9906752-bdb2-510d-add2-2a0e454e424a | textbox | HPQ - Slave
180bc7ab-ca6a-4a1d-a800-ed2b52df8405 | checkpoint | Ih14
ef4b4159-24a2-5d48-8a4e-6e4d56da7f23 | textbox | HPQ - Master
5cdf1d93-2b03-5d07-94a4-a9099f076b86 | textbox | HPQ - Slave
86a1a7eb-2072-4c4a-9b2e-f20e27725d8b | checkpoint | Ih15
55909781-3aaa-5a99-9aa9-ec9e6ce396dc | textbox | HPQ - Master
4a1cdadf-4881-5109-81df-1f75fef82278 | textbox | HPQ - Slave
d6ee6c86-f92b-4b84-9858-93a62d4a1eea | checkpoint | Ih16
1101c207-f808-52cb-b785-4d751e10e19d | textbox | HPQ - Master
ce53ddf6-b45b-565c-8713-60d638c050e4 | textbox | HPQ - Slave
c42cc0d1-b2bb-436a-9c91-c38462d8cc27 | checkpoint | Ih17
12cc0387-b996-5a59-81a5-11de6028a69a | textbox | HPQ - Master
7c520715-6572-5ea5-b977-6eb905ef020e | textbox | HPQ - Slave
08d88b7b-530d-4716-a7e9-127225b8db49 | checkpoint | Ih18
6c59ffb2-f39f-5269-8591-0845078b532f | textbox | HPQ - Master
cfb2b880-9fb8-5fea-be59-63c10911d49c | textbox | HPQ - Slave
50aaecd9-b3ca-49fd-a775-1d5f1651be53 | checkpoint | Ih19
44aa7aa7-2ca6-5491-bd7c-5419a41d0ecb | textbox | HPQ - Master
69e24997-a632-50bf-826b-1c4ad2d1eae8 | textbox | HPQ - Slave
d33853a0-02aa-4d51-9214-bf4d14a28591 | checkpoint | Ih20
5e728ea7-235e-5686-9054-280f6a598c81 | textbox | HPQ - Master
af3494e6-60bd-5e41-ab49-dab510386ce9 | textbox | HPQ - Slave
42ae131c-c6d1-4c3a-8f7e-6f8783c63290 | checkpoint | Ih21
7c98b47c-2227-567d-8e4c-d520c18fcdaf | textbox | HPQ - Master
80f57129-27ca-53d8-9686-20502ca4464c | textbox | HPQ - Slave
f3e940d4-6b8a-4e8e-a171-475728bebe47 | checkpoint | Ih22
6af0bac3-0b02-55f7-abbe-0aed5e6a50ac | textbox | HPQ - Master
dcf46165-e420-537a-a624-2805fccf2d14 | textbox | HPQ - Slave
c24f0f52-89f7-43a4-9e9f-6a2904245955 | checkpoint | Ih23
f5cf8f64-8076-5503-b102-3551d4356cc3 | textbox | HPQ - Master
4535595b-06e4-59f8-9adb-24c23679650e | textbox | HPQ - Slave
e4574bfa-14d6-4218-ba05-315e10f10b76 | checkpoint | Ih24
32e5de77-6b5d-5fe7-9e45-0e38274d20ee | textbox | HPQ - Master
46601ebb-8761-5e6d-af51-d4b0ee6b946c | textbox | HPQ - Slave
bca5476d-b4a5-4f67-9f49-2e06c2a77182 | checkpoint | Ih25
3a47c6a6-9d11-500c-9b32-b0228476989a | textbox | HPQ - Master
3b24d501-8414-5fd6-827f-02eb9ce4b0c4 | textbox | HPQ - Slave
4c5e2923-7d7f-4005-ba2b-4ad0d9787524 | checkpoint | Ih1
03342ffd-ede9-52fd-b850-ccc62b6e1c5e | textbox | HPQ - Master
da5f4a06-54f4-598f-830e-e1a60a1a9003 | textbox | HPQ - Slave
060f8b4c-7666-4fef-bae4-8334fa66bfa5 | section | POWER QUALITY PARAMETERS
95f9369f-413e-4612-8f7d-c2f42b64d4d9 | checkpoint | HAPFC Mode - "STOP"
4c9e2365-fa63-5878-b0a4-93fcb3f967d1 | textbox | THD_V, L1
b4114c37-c85a-5c4b-bee9-a9ffb6bdb311 | textbox | THD_V, L2
db8eab11-492e-550b-b26d-c3cb443ba8ff | textbox | THD_V, L3
8f4ef435-bf12-58e7-90d1-441413d69ca1 | textbox | THD_I, L1
6c61c43e-3e86-5e11-8282-b1ea3a327235 | textbox | THD_I, L2
e70aee6c-a8d4-5a5b-82ac-1cc53cfd472b | textbox | THD_I, L3
829a49ca-fc8f-5143-9227-376606019fc6 | textbox | PF
56b45949-14e9-41b9-9774-92cef3f13508 | checkpoint | HAPFC Mode - "RUN"
f3fb12ec-5ce4-56df-b88f-6a1715a5a50a | textbox | THD_V, L1
548c17ba-f255-5acf-b71a-797849d7e4bf | textbox | THD_V, L2
95a90edd-fb84-5f0b-928c-100673e1b5db | textbox | THD_V, L3
26be0161-27d6-5467-af88-39f10319ed31 | textbox | THD_I, L1
d5893299-a9bc-585e-a1f4-59ad52db474f | textbox | THD_I, L2
9193d364-b47b-54ea-a2be-27af442d9431 | textbox | THD_I, L3
145caa05-d833-58c8-a520-6c3f2c5c3fa7 | textbox | PF
a532d3a2-6f9a-4d96-931a-544bdc10ff0c | section | VOLTAGE WHEN SYSTEM OPERATING
4c0ef4c2-e697-4ae2-9643-5a2c3bd73f08 | checkpoint | LINE VOLTAGE
e222d102-7817-5fbd-ac02-ca7970d8d684 | textbox | L1-L2
0e91800c-0108-50f4-9a62-8a9b23c4d67b | textbox | L1-L3
349f0dd4-381c-5e28-a058-6a94afbe7d50 | textbox | L2-L3
bb02435b-3398-47bd-b546-d45ed267cbba | checkpoint | PHASE VOLTAGE
a0e1060e-b8e7-56f3-bf52-20bd8a4e71c6 | textbox | L1-L2
c3a2e032-a5aa-5665-ae12-2139c187ec3e | textbox | L1-L3
d628c41c-dc9c-512b-bdcf-7ebe5540fecd | textbox | L2-L3
44ec4e1a-8460-4a17-af12-d6fe5f943a46 | section | FUNCTIONAL TEST
cf8c124c-5d28-41a3-9c0b-f357a701b80b | checkpoint | FUNCTIONAL TEST
a4491653-0e8d-4538-99ea-9c4f61455a02 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000017 - MATV | itp | LEVEL
c1a25960-6dd8-43b2-9e98-2b4bdd36a4c0 | section | MATV
9bcebeea-037e-4320-94d4-c11827047578 | checkpoint | QLTY
9f4e519d-35e5-5f34-bdac-dfc19368ffad | textbox | Prg
038bea77-5887-5916-a7e0-026d99007b0b | textbox | Mode
449130db-2b64-5027-be6e-b06e99d5f2a7 | textbox | Freq. [MHz]
0d577c0d-3d0f-5a08-8cd0-3040f89006a8 | textbox | Prg.Name
aae12011-8bde-5f94-af5e-4e6a890da67c | textbox | Local Osc [MHz]
96498960-1065-5cc7-a687-4d1d64a9c0c6 | textbox | S.Rate or CH.BW.
b96adde9-917b-57cf-9f1a-b968108969da | textbox | Lnb Pol SEGMENTS
6710e214-9e20-5807-8ded-3f8bcc62212d | textbox | DiSEqC LAYER
8d3a3f41-1ae1-50cb-85c2-cf1502f4e797 | textbox | Stand. or Constel
78731852-733c-50b2-b8eb-497e5f4b734e | textbox | Level or Power [dBuV]
238ef39d-a953-5c3a-b755-945cfe8bc0de | textbox | C/N MER EVM [dB]
ad9fd651-8a87-547f-88e9-456b20ea0cdb | textbox | bBER aBER PER
690f7ec4-aef1-573f-9f3c-3eae94103b18 | textbox | N.MA. [dB]
6081df97-f53f-5e0c-8780-8688a401eb47 | textbox | FEC HP/LP CODE RATE
01f92c05-ee41-47a8-9447-14c632c6c579 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000019 - Fibre Optic Cabling | itp | CABLE #
c91b0eb3-1793-4c21-8eae-c55874257b66 | section | FIBRE OPTIC CABLING
f9926649-2c23-4064-bed8-6e203478cd6d | checkpoint | PRE-REQUISITE WORKS
51b6a449-9a66-5f34-84f7-722817cc7cb6 | note | Confirm All Work Has Been Completed
f29fcbb5-291e-4615-a2be-1c51852575e7 | checkpoint | INSTALLATION CHECKS
d1b70229-037a-5e73-a9e0-08174094bef7 | note | Visual Inspection – No damage, outlet installed correctly
dbe90d71-c2d9-4725-98f3-71faf9188f59 | checkpoint | VERIFICATION & TESTING
a35a5c16-9be7-5ee1-b88c-251f79676829 | note | REFER TO SEPARATE FLUKE TEST SHEETS FOR TESTING RESULTS
93cfe0f0-59af-5252-9e5e-c937be18a956 | button | LABELLING COMPLETE | YES,NO
86bac528-52a4-5742-b3d3-af3a052bb165 | button | FLUKE TEST PASS | YES,NO
beb7026b-c4bf-429d-97a8-16ba1920d0ac | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000020 - Comms Copper Cabling | itp | CABLE #
e759e3fe-53e2-4091-98a8-f8e7885aabc3 | section | FIBRE OPTIC CABLING
364b0853-8808-4b34-9bc9-cc71b5ee824f | checkpoint | PRE-REQUISITE WORKS
da9489bf-0e58-56aa-9d6d-7e3167ce1c14 | note | Confirm All Work Has Been Completed
3e8d1c50-91c7-429a-b703-78caa9c64ec2 | checkpoint | INSTALLATION CHECKS
34d8fc00-b10e-5db4-9844-74162ef43425 | note | Visual Inspection – No damage, outlet installed correctly
a3a7c41e-ebe3-4a07-81bd-7e92d7ac8517 | checkpoint | VERIFICATION & TESTING
3a44051d-dd28-58ab-b7cd-688ee4fbdb5f | note | REFER TO SEPARATE FLUKE TEST SHEETS FOR TESTING RESULTS
5e9d8060-f437-5fd2-b0ab-bad8f23b8161 | button | LABELLING COMPLETE | YES,NO
5469449d-4449-55e4-a235-7392d12669e6 | button | FLUKE TEST PASS | YES,NO