## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
7965c37b-2539-4c7e-b425-1594f9c03dbb | checklist | Commissioning/Handover & Testing Checklist |  | Commissioning/Handover & Testing Checklist
52ea580f-a67e-4f80-ba60-95f62d6238e2 | checkpoint | Final completed for fire hydrant
193df058-7b30-48b1-b850-a9433ed50918 | checkpoint | Final sign off - Pass when happy to proceed (Any issues please comment & Add photos below)
c5b4fa60-fca7-4bb9-a703-fbf88041527f | checklist | Copper Riser Penetration |  | Copper Riser Penetration
7c22fa30-2090-4347-8b53-8a74975f156d | checkpoint | Copper Riser Penetration - Please add any photos / comments
3f3d9fed-7815-52dd-ab3f-3a24ef465062 | tickbox | MAXILTE 60 (FIRE BOARD 1525x1000x60mm)
89a515d2-9672-5a6c-81bf-940ff3aac31f | tickbox | TWRAP 300mm (TWRAP PENETRATION WRAP -25mm THICK 300 X 7620mm)
2da99a90-19ef-565e-a12e-e36a8c4e8aa6 | tickbox | TWRAP 600mm (TWRAP PENETRATION WRAP -25mm THICK 600 X 7620mm)
dcb08719-583e-57e0-93df-f8d861c558a2 | tickbox | FRYREFLEX 600W (FRYREFLEX 600mL SAUSAGE)
3b2d42b3-b234-5820-8b9e-3f7d4c73028a | tickbox | CABLE TIE SS 4.6 X 520 (STAINLESS STEEL CABLE TIES 4.6mm X 520mm)
053a367b-7582-48c1-9743-855ac341a1b6 | checklist | Copper Riser Penetration |  | Copper Riser Penetration
d7fcb3d3-6c80-4e49-ab90-106b45152bc6 | checkpoint | Copper Riser Penetration - Please add any photos / comments
5c734b6b-885b-5491-ab0e-3efc2f827250 | tickbox | MAXILTE 60 (FIRE BOARD 1525x1000x60mm)
cd2200b9-30a3-5ff4-8684-01a9f3130477 | tickbox | TWRAP 300mm (TWRAP PENETRATION WRAP -25mm THICK 300 X 7620mm)
c83e0deb-fc52-5aab-860d-cc3c6adb515b | tickbox | TWRAP 600mm (TWRAP PENETRATION WRAP -25mm THICK 600 X 7620mm)
93cea37c-0f29-56e1-bb52-6bbc0ca16d4b | tickbox | FRYREFLEX 600W (FRYREFLEX 600mL SAUSAGE)
bd904f57-d1bc-53ff-9a29-e826ad9d2fed | tickbox | CABLE TIE SS 4.6 X 520 (STAINLESS STEEL CABLE TIES 4.6mm X 520mm)
d096bf9d-ca52-4954-94af-12badb7b5504 | checklist | Fit Off Checklist |  | Fit Off Checklist
06c313af-d51a-40fc-a962-cd2e2f84851a | checkpoint | Fixtures installed at correct height/clearance
8b295813-7968-4294-a312-10329b33d64c | checkpoint | Appliances installed at correct location
5d3c5d77-ff19-4a01-851e-a8795e4f7716 | checkpoint | Dishwasher installed & tested
bc1d7c52-712c-440e-bd44-faf5ce2a8e3c | checkpoint | Correct clearance between appliance & walls, fixtures/equipment
f9c29ecc-896b-44ee-aa94-a41461f69a87 | checkpoint | Correct clearance for connections & maintenance
8b256b4e-a141-482c-b281-586321c8af90 | checkpoint | Ensure bath is installed as per specifications
b229043f-6da5-4632-abda-4ec6065b1572 | checkpoint | Final test completed & hot water tempered
c48d11a4-a2d2-40cc-bd26-2c32fcdb7ea1 | checkpoint | Valves Installed/Completed (As Per Below) - Any issues comment below
346434eb-4fe2-4757-90c6-e163a7415f33 | checklist | Internal Drainage |  | Internal Drainage
333a734b-f50d-44c3-bf8e-127bb08489b1 | checkpoint | Ensure pipes are at correct fall as per AS3500
3a60b4b5-eb5d-4680-ba7b-9831c857076c | checkpoint | Backfilling material has been backfilled & compacted as per AS3500
0c0b1414-bb8b-45a9-99fe-4fa8633e4cb0 | checkpoint | Pipes are clear of debris
2165d3d2-b660-412b-a60e-4d15b6d6ce1a | checkpoint | Jump ups at floor waste gulleys
f64a5187-9204-409d-9c34-10e8054dc98d | checkpoint | Direct rotting to WC's
84bc0bac-4e0d-469e-b5d1-d97653131815 | checkpoint | Vents installed on main lines
f383a29d-3884-4fc3-8ab2-8dbd3fc66c06 | checkpoint | Chamber vent installed
cd21211a-a5b9-4bde-a9f2-fa9c35f42c2b | checkpoint | General photos, comments & observations during internal drainage
14e73735-ea78-4ac8-be3f-aa69b4694df0 | checkpoint | Pipework fixture connections capped & secure
e93b56bf-bcc6-4aca-91a9-ab80bba2588d | checklist | Internal Stormwater |  | Internal Stormwater
1186df62-7e1e-4c4a-8c72-7ddd69651a85 | checkpoint | Ensure pipes are at correct fall as per AS3500
a92f06f4-f119-4944-b02f-7cf20f7c1abd | checkpoint | Backfilling material has been backfilled & compacted as per AS3500
4907f273-66d8-4a2c-baa7-d56c2150be15 | checkpoint | Pipes are clear of debris
2cc4f707-0aa2-45b4-b24c-4d3d01a91a7a | checkpoint | Pit invert levels & RL's are per plan
b31ed16b-9d18-4e39-95f3-a70f26e1cf99 | checkpoint | General photos, comments & observations during internal drainage
3f7149c4-df38-4a07-b499-ae51e4419626 | checkpoint | Pipework fixture connections capped & secure
534bc08e-6c06-43cc-85cc-ac5cc625d9cf | checklist | Meter Cupboard / Copper Riser |  | Meter Cupboard / Copper Riser
04567ca6-58bb-4aba-8b87-4e8c4120e62d | checkpoint | All copper piping installed & pressure tested to AS/NZS3500:2018
ff99f845-e7c5-4e00-8ff7-eec3940cea86 | checkpoint | Valves Installed/Completed (As Per Below) - Any issues comment below
49824292-84aa-5067-9e04-439e20b152d6 | button | Tempering valves installed | Yes, No, N/A
1b653194-19bf-5266-a9a3-6b8f3aa1979d | button | Air admittance valves installed & connected as specified & readily accessible | Yes, No, N/A
43286147-d8cd-5a80-806c-f708229e5973 | button | Pressure regulating valve assembles fitted, connected & pipework flushed prior to install | Yes, No, N/A
b520ac6a-4eaa-5724-b9fc-6890602c7a55 | button | Tempering valve tested ready for temperature setting | Yes, No, N/A
fc585238-13b6-48be-9c07-d271cdc8ef47 | checkpoint | General photos, comments & observations during Sewer Rough-In (Add below)
54ecee44-8f0b-40c3-9396-ff96ce622962 | checklist | Passive Fire Penetration |  | Passive Fire Penetration
2512c4bb-f14a-46be-9c13-1828d1f944e7 | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
b5f55863-338b-599b-bb2e-e6495983789a | dropdown | Material | Hilti CP 611A Firestop Intumescent Sealant, Hilti Firestop Acrylic Sealant 209633, Hilti Firestop Acrylic Sealant CP 606, Hilti Firestop Collar 100 No. 435410, Hilti Firestop collar 50 No. 455405, Hilti Firestop collar 50 No. 455406, Promaseal FC 100 No. 27253, Promaseal FC 100 No. 78269, Promaseal FC 150 No. 78254, Promaseal FC 150 No. 78270, Promaseal FC 50 No. 78272, Promaseal FCR 100 No. 78253, Promaseal FCR 100 No. 78282, Promaseal FCW 40 No. 78271, Promaseal FCW 50 No. 435906, Promaseal FCW 50 No. 78272, Promaseal FCW 50 No. 78273, Promaseal FCW 50 No. 922310, Promaseal FCW 65 No. 78273, Trafalgar Wrap, Uni Collar No. 78342, Promaseal FCW 100, Promaseal FCW 150
6451bfc2-01d0-5f70-9c7d-54bbce61ecd5 | dropdown | Description | PVC Sewer, PVC Stormwater, 20mm PEX, Copper Water, Copper Gas
895b4c7e-6c10-5d68-9aca-3081390e4504 | dropdown | Pipe size | 16mm, 20mm, 40mm, 50mm, 65mm, 80mm, 100mm, 150mm, 225mm
531e64a4-202c-40d6-be3a-eb3081cd3230 | checkpoint | Please take detail photos of penetration & labelling
95b3fa61-3367-58d0-9774-6e403b0b2ea1 | textbox | ID Number
0e01bcb7-40de-47b5-9a86-2fb1cd5865c3 | checkpoint | Please attach copy of test report / certificate
fc1a075f-af4b-4be8-9857-f753b1a511b0 | checklist | Plumbing Rough-In Water/Gas/Sewer Checklist |  | Plumbing Rough-In Water/Gas/Sewer Checklist
41a56d07-699b-445a-9d9b-59ddd8396899 | section | Sewer Stacks
328169ca-7af7-4b6e-a07e-03929370b918 | checkpoint | Pipework fastened, fixed, supported & secured (clipped) correct spacings
245f00ea-c7f5-4cd2-aefc-b3bf8aed12db | checkpoint | Pipework connection points at fixtures & fittings installed at correct height & fall
7075234a-ba85-5ddb-85fd-0f12ee5d3d04 | note | Consider ceiling height
e2a2e49c-aa71-44f8-b948-eae862fc0bfa | checkpoint | Correct invert level (As per Standards)
89024c5b-5e8f-4d7f-a42d-3956838eef59 | checkpoint | Pipework fixture connections capped & secure
15821c34-6fe9-4683-9b5c-03f970a7ff07 | checkpoint | General photos, comments & observations during Sewer Rough-In (Add below)
55ea2cfa-2c36-5fe4-8fbb-5826d1ff2eea | button | Passive Fire collars/Sealant(s) for all pipework completed (Any issues comment below) | Yes, No
8d5c3597-2ae9-4165-a4fe-298be6a2b872 | checkpoint | Drainage flood tested
c1b6ee6c-9197-55ee-8124-e98bf1a6ee72 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
dc5efb1d-4d6f-4df3-a2fe-12811e2e718e | section | Water & Gas Rough-In
317ec539-fa15-47ca-b74a-82457c1a5611 | checkpoint | Pipework run to the correct points & there are no cross connections
514193c6-9e64-4090-8aa1-3722862f8739 | checkpoint | Pipework fastened, fixed, supported & secured (clipped) correct spacings
c393504e-33be-5c55-820a-39bcae0b9e2a | note | Make sure no water hammer on Water pipes
2e6755f5-614c-4f80-9db2-1b70b86e96f2 | checkpoint | Pipework connection points at fixtures & fittings installed at correct height
17b701f0-eb63-5a0d-a4aa-0f8516711fc0 | note | Consider ceiling height
949f3a85-5b99-48c1-b45a-effd1a0f0e58 | checkpoint | Pipework fittings capped, connection loops joined & secure
f803ba4c-9439-451f-ab53-bfc0bfc26ffe | checkpoint | Leak test piping before proceeding to 1500KPA
bdb0eeac-0f61-4024-a253-704004f72b78 | checkpoint | Gas test pressure holding point 14KPA
28a841e4-069a-53ed-b675-ff358ce5733d | button | Isolation valves installed & located readily accessible for maintenance | Yes, No, N/A
c8286d57-d1b9-5de3-b8c3-7689a9686c30 | button | TMV/Tempering valve installed | Yes, No, N/A
d2245cc3-a623-4007-b165-1e1817d77a6c | checkpoint | All rough in fire rated
19588ce0-97b6-48de-b5a4-ec9d48b69308 | checkpoint | Ensure all drainage is capped
d7d46125-2074-4b65-bca0-97455d39fcae | checkpoint | General photos, comments & observations during Rough-In (Add below)
6c6a34e6-081d-4391-a029-1cc0e19d4f2c | checkpoint | Rough-In completed to specification/drawings
5fd88abe-b971-4534-8fc4-09d65f0179c4 | checkpoint | Final test completed
5489ad97-f051-4256-96ae-34c031d1e9df | checklist | Sewer Stacks / Storm water stacks |  | Sewer Stacks / Storm water stacks
55c5e892-fbbe-478d-a703-b3350d2a6c02 | checkpoint | Pipework fastened, fixed, supported & secured (clipped) correct spacings
19536ba3-748f-418b-ac86-ef463817a432 | checkpoint | Pipework connection points at fixtures & fittings installed at correct height
d639407d-2ed8-55b2-9dbf-4e4b5ee7720a | note | Consider ceiling height
139368de-f365-4c87-840b-460c6709a2f3 | checkpoint | Correct invert level (As per Standards)
9b1a0f85-6e46-45b4-9452-ae1216fb9112 | checkpoint | Pipework fixture connections capped & secure
a1ffaf2c-c20d-4a89-9778-d5913e8d62bc | checkpoint | General photos, comments & observations during Sewer Rough-In (Add below)
b912057c-5400-4c52-9f44-f8e067a765ae | checkpoint | Passive Fire collars/Sealant(s) for all pipework completed (Any issues comment below)
821634ed-3e33-44c4-a682-bd099372babd | checklist | SYS - archived - Passive Fire Penetration |  | Passive Fire Penetration
adb49741-7ff0-4798-b51c-e45c0fd8a0bf | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
9300d662-e24e-5778-bf16-cb3a964f8126 | dropdown | Material | Hilti CP 611A Firestop Intumescent Sealant, Hilti Firestop Acrylic Sealant 209633, Hilti Firestop Acrylic Sealant CP 606, Hilti Firestop Collar 100 No. 435410, Hilti Firestop collar 50 No. 455405, Hilti Firestop collar 50 No. 455406, Promaseal FC 100 No. 27253, Promaseal FC 100 No. 78269, Promaseal FC 150 No. 78254, Promaseal FC 150 No. 78270, Promaseal FC 50 No. 78272, Promaseal FCR 100 No. 78253, Promaseal FCR 100 No. 78282, Promaseal FCW 40 No. 78271, Promaseal FCW 50 No. 435906, Promaseal FCW 50 No. 78272, Promaseal FCW 50 No. 78273, Promaseal FCW 50 No. 922310, Promaseal FCW 65 No. 78273, Trafalgar Wrap, Uni Collar No. 78342
685759fb-5c35-5241-98d5-e30b4be1c2a2 | dropdown | Description | PVC Sewer, PVC Stormwater, 20mm PEX, Copper Water, Copper Gas
9c91eec6-d81d-5790-8f30-16a79b190984 | dropdown | Pipe size | 16mm, 20mm, 40mm, 50mm, 65mm, 80mm, 100mm, 150mm, 225mm
df83aa1f-657c-4caf-ade5-c08db2ea07ed | checkpoint | Please take detail photos of penetration & labelling
e804183a-ec8c-5f1c-ae0d-c3700f862e8c | textbox | ID Number
50ee48ee-8f9d-4c99-b315-918c8e979a93 | checkpoint | Please attach copy of test report / certificate