## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
e3f953ed-fd80-464e-88a7-05cd9c76c4ce | checklist | Commissioning/Handover & Testing Checklist |  | Commissioning
6e6e4ceb-be9c-4e44-a642-883250e3b9f4 | checkpoint | Final completed for fire hydrant
3b263ce9-b7e0-4271-ac18-aee6148406b7 | checkpoint | Final sign off - Pass when happy to proceed (Any issues please comment & Add photos below)
2e9a8d56-39a6-4d49-8d64-a94e62544176 | checklist | Copper Riser Penetration |  | Copper Riser Penetration
c999b648-acaa-45a8-a552-c4440769e185 | checkpoint | Copper Riser Penetration - Please add any photos / comments
76be67a6-715a-57c8-916d-467bfac0a537 | tickbox | MAXILTE 60 (FIRE BOARD 1525x1000x60mm) | Hilti CP 611A Firestop Intumescent Sealant, Hilti Firestop Acrylic Sealant 209633, Hilti Firestop Acrylic Sealant CP 606, Hilti Firestop Collar 100 No. 435410, Hilti Firestop collar 50 No. 455405, Hilti Firestop collar 50 No. 455406, Promaseal FC 100 No. 27253, Promaseal FC 100 No. 78269, Promaseal FC 150 No. 78254, Promaseal FC 150 No. 78270, Promaseal FC 50 No. 78272, Promaseal FCR 100 No. 78253, Promaseal FCR 100 No. 78282, Promaseal FCW 40 No. 78271, Promaseal FCW 50 No. 435906, Promaseal FCW 50 No. 78272, Promaseal FCW 50 No. 78273, Promaseal FCW 50 No. 922310, Promaseal FCW 65 No. 78273, Trafalgar Wrap, Uni Collar No. 78342
8335e36b-da1b-579c-80a1-1700d3760d2b | tickbox | TWRAP 300mm (TWRAP PENETRATION WRAP -25mm THICK 300 X 7620mm) | PVC Sewer, PVC Stormwater, 20mm PEX, Copper Water, Copper Gas
fcdd6d0b-920e-50a1-940e-12d6b6619a94 | tickbox | TWRAP 600mm (TWRAP PENETRATION WRAP -25mm THICK 600 X 7620mm) | 16mm, 20mm, 40mm, 50mm, 65mm, 80mm, 100mm, 150mm, 225mm
37cfb76d-e8cf-54db-aeaa-6da3c45b810b | tickbox | FRYREFLEX 600W (FRYREFLEX 600mL SAUSAGE)
8f95eaee-6502-5b6d-9eec-0762d32d6bbe | tickbox | CABLIE TIE SS 4.6 X 520 (STAINLESS STEEL CABLE TIES 4.6mm X 520mm)
20b51a8c-9dec-40ae-8e53-af33207871a9 | checklist | Fit Off Checklist |  | Fit Off Checklist
905bf8a8-640a-448d-95ff-65d820125441 | checkpoint | Fixtures installed at correct height/clearance
11d24abf-a1e4-4806-a01b-c7d4e84d185c | checkpoint | Appliances installed at correct location
fe22be54-d6a1-4cd3-a61e-8e87f341e0e1 | checkpoint | Dishwasher installed & tested
9c83ab12-3212-4d79-9a52-289ac7f745bf | checkpoint | Correct clearance between appliance & walls, fixtures/equipment
d7c8c938-fc73-4cac-bc03-3a4c25bf3dda | checkpoint | Correct clearance for connections & maintenance
444ceb30-bde5-45ff-b224-a54e7bcbedce | checkpoint | Ensure bath is installed as per specifications
73a97561-dec6-4a5a-841e-01fd94851822 | checkpoint | Final test completed & hot water tempered
bdf6498b-5553-44d5-9a16-4cb878715668 | checkpoint | Valves Installed/Completed (As Per Below) - Any issues comment below
967bf18b-69a8-4c88-918f-f79042da5d92 | checklist | Internal Drainage |  | Internal Drainage
5febedbf-3f50-49a6-addb-11761db7d0e7 | checkpoint | Ensure pipes are at correct fall as per AS3500
2f342205-88e8-48e6-85f7-c837c81168ec | checkpoint | Backfilling material has been backfilled & compacted as per AS3500
301fd694-8281-4b77-92b9-786a3d35256c | checkpoint | Pipes are clear of debris
71abda2c-cabc-4813-ae57-93867dd2211d | checkpoint | Jump ups at floor waste gulleys
38ce6102-cb51-4a6a-930b-a570363287d7 | checkpoint | Direct rotting to WC's
fd680dd7-2453-4dcd-acad-d3b1b7dfc3e2 | checkpoint | Vents installed on main lines
37edba24-d412-4de2-a5e9-27e14ed05909 | checkpoint | Chamber vent installed
feb54249-c002-4566-808e-65d451f63b46 | checkpoint | General photos, comments & observations during internal drainage
867cd297-d136-45a5-b1f4-80f6b38fb68b | checkpoint | Pipework fixture connections capped & secure
58400cba-631f-4dfb-a44e-be95e1a96a9c | checklist | Internal Stormwater |  | Internal Stormwater
3fd06599-8b62-4fb1-b3d3-57d7b49557af | checkpoint | Ensure pipes are at correct fall as per AS3500
87b5b44a-017c-4de5-a7d1-9b897ce5976c | checkpoint | Backfilling material has been backfilled & compacted as per AS3500
e015dec4-cf00-44a3-a8d3-4378ac800c1e | checkpoint | Pipes are clear of debris
2200a7e2-d477-411d-a44f-1acc60d5d3d8 | checkpoint | Pit invert levels & RL's are per plan
3abd53ea-ca45-477c-8b34-75caff958314 | checkpoint | General photos, comments & observations during internal drainage
a24c4059-1fa7-44bf-91f1-764e64b845c9 | checkpoint | Pipework fixture connections capped & secure
132e3f94-b2ec-4ece-ad8a-5b4b30d8e3eb | checklist | Meter Cupboard / Copper Riser |  | Meter Cupboard / Copper Riser
7a4c79b2-fcb0-4c09-a27a-08baec302847 | checkpoint | All copper piping installed & pressure tested to AS/NZS3500:2018
4a6e4247-f9e7-434a-a56b-391111c4ffb5 | checkpoint | Valves Installed/Completed (As Per Below) - Any issues comment below
ccf24396-6073-58b8-89d1-2d1b0d4adf53 | button | Tempering valves installed | Yes, No, N/A
fc9a9ae2-4175-5f58-9e23-192d475fa90c | button | Air admittance valves installed & connected as specified & readily accessible | Yes, No, N/A
c0b9572d-0826-5c00-85b4-0a426b577a5d | button | Pressure regulating valve assembles fitted, connected & pipework flushed prior to install | Yes, No, N/A
ab74749b-e382-53d8-b787-768cf5058080 | button | Tempering valve tested ready for temperature setting | Yes, No, N/A
76b05264-9997-4cb1-bce0-e6f064ceea05 | checkpoint | General photos, comments & observations during Sewer Rough-In (Add below)
07095b46-3547-4089-af83-b9ce7fc24df8 | checklist | Passive Fire Penetration |  | Passive Fire Penetration
3b062f64-c039-4a26-bedd-ac3d62706267 | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
6f43242a-1016-5aca-9dd2-b71b1cbdae94 | dropdown | Material | Hilti CP 611A Firestop Intumescent Sealant, Hilti Firestop Acrylic Sealant 209633, Hilti Firestop Acrylic Sealant CP 606, Hilti Firestop Collar 100 No. 435410, Hilti Firestop collar 50 No. 455405, Hilti Firestop collar 50 No. 455406, Promaseal FC 100 No. 27253, Promaseal FC 100 No. 78269, Promaseal FC 150 No. 78254, Promaseal FC 150 No. 78270, Promaseal FC 50 No. 78272, Promaseal FCR 100 No. 78253, Promaseal FCR 100 No. 78282, Promaseal FCW 40 No. 78271, Promaseal FCW 50 No. 435906, Promaseal FCW 50 No. 78272, Promaseal FCW 50 No. 78273, Promaseal FCW 50 No. 922310, Promaseal FCW 65 No. 78273, Trafalgar Wrap, Uni Collar No. 78342
ff72f1b3-79fe-524f-aa0b-ed93261ae402 | dropdown | Description | PVC Sewer, PVC Stormwater, 20mm PEX, Copper Water, Copper Gas
0b36120d-a38c-5885-9ccd-860392409472 | dropdown | Pipe size | 16mm, 20mm, 40mm, 50mm, 65mm, 80mm, 100mm, 150mm, 225mm
5440dc6a-e322-4b9a-bf46-ef459af39de4 | checkpoint | Please take detail photos of penetration & labelling
dd051cea-fbb8-51f3-81c7-ec7f856e9150 | textbox | ID Number
0a487345-8cd3-4c20-a08c-ea15364f7a1e | checkpoint | Please attach copy of test report / certificate
a6699758-3167-4c59-8444-55969a2abf20 | checklist | Plumbing Rough-In Water/Gas/Sewer Checklist V1 |  | Plumbing Rough-In Water/Gas/Sewer Checklist
1ee22170-9977-42a8-b233-32112901fde2 | section | Sewer Stacks
0c703555-87e3-4cbb-936e-3c379afbcab9 | checkpoint | Pipework fastened, fixed, supported & secured (clipped) correct spacings
07814414-6855-4776-b154-249c4c3a8c83 | checkpoint | Pipework connection points at fixtures & fittings installed at correct height & fall
5ba8326d-55c3-5b6a-99fa-7416dce906bc | note | Consider ceiling height
7ffcfb38-bc20-439f-a675-79bb1bdb2292 | checkpoint | Correct invert level (As per Standards)
4cd8a29d-4c95-44b6-b3ad-22cd4c4429d8 | checkpoint | Pipework fixture connections capped & secure
7fb2ab00-04aa-4f42-9695-a7a03ee7cb60 | checkpoint | General photos, comments & observations during Sewer Rough-In (Add below)
f3ca9eab-7e01-5c0d-9c49-b3013e6f5e18 | button | Passive Fire collars/Sealant(s) for all pipework completed (Any issues comment below) | Yes, No
e83dbf86-102c-4e42-84f8-2fb4afa4ae7b | checkpoint | Drainage flood tested
540e11d8-2fb1-5375-a919-aa232423ec47 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
1ef7930f-bff5-41de-890b-a204c6504929 | section | Water & Gas Rough-In
0938866d-0a47-4a4c-a989-5abff08aeda6 | checkpoint | Pipework run to the correct points & there are no cross connections
a6d3577d-3e1d-439f-8dd3-2e825fcdd780 | checkpoint | Pipework fastened, fixed, supported & secured (clipped) correct spacings
25f8cd43-fe04-594c-91c0-4077e6f7c87d | note | Make sure no water hammer on Water pipes
1bc8912c-6bc7-4ec2-a58c-af9cd07f2bd1 | checkpoint | Pipework connection points at fixtures & fittings installed at correct height
80e6b4ae-57d3-5df2-ac98-c08c586a03fb | note | Consider ceiling height
ff7572c7-0016-4d19-af14-e32c6fdcbe19 | checkpoint | Pipework fittings capped, connection loops joined & secure
05aa8594-1a62-46f9-9d10-d891f351c3ca | checkpoint | Leak test piping before proceeding to 1500KPA
ce5f890b-af8a-44e9-9f19-f40afed65b7f | checkpoint | Gas test pressure holding point 14KPA
c407bf9f-1520-5815-a166-ee0df2dba227 | button | Isolation valves installed & located readily accessible for maintenance | Yes, No, N/A
da9bbf81-9c2d-527a-83a8-693bd7dfb578 | button | TMV/Tempering valve installed | Yes, No, N/A
c0364950-b41c-4523-b189-b42f7889fbc5 | checkpoint | All rough in fire rated
03135eec-6879-4c8b-b523-d8f5fba8e78b | checkpoint | Ensure all drainage is capped
f925fe98-3aeb-427d-aaa8-88d5bcfaa888 | checkpoint | General photos, comments & observations during Rough-In (Add below)
a73e08da-b7d1-4a30-9dc8-925130f7a653 | checkpoint | Rough-In completed to specification/drawings
0acf0fc1-bb6d-4ec2-acb3-ad89df7941ce | checkpoint | Final test completed
9dd793ac-254a-4509-908d-65bb7ee44d70 | checklist | Sewer Stacks / Storm water stacks |  | Sewer Stacks / Storm water stacks
2a2cc132-c86d-43d1-a877-b20cc2ab41f9 | checkpoint | Pipework fastened, fixed, supported & secured (clipped) correct spacings
241cea15-d158-4241-9337-6ea78a796269 | checkpoint | Pipework connection points at fixtures & fittings installed at correct height
f815a26d-b496-5666-8f16-2c13730efae6 | note | Consider ceiling height
af999bfa-e050-4567-871f-4c57d5faf1a4 | checkpoint | Correct invert level (As per Standards)
d9cf6ce6-9fdd-4c06-b422-51fcbf41edc6 | checkpoint | Pipework fixture connections capped & secure
1868089d-0551-4462-acbc-b273c2fc42e5 | checkpoint | General photos, comments & observations during Sewer Rough-In (Add below)
f870a938-d4bb-4c4a-a70a-6c718555c204 | checkpoint | Passive Fire collars/Sealant(s) for all pipework completed (Any issues comment below)