## ITP-xxx
|  |  | Inspection and Test Plan - Installation of Conduits and Pits | [7 empty] | Document # FHC-ITP-023
[11 empty] | Revision : 1 | Date : 05/07/2022
Client: |  | MRPA |  | Construction Process: |  | Prepared by: |  | Reviewed by : |  |  | Approved by :
Project: |  |  |  | Installation of Conduits, Pits and OCS System |  | Name: Martin Syawish |  | Name: Patrick Fagan |  |  | Name: Shaun Kent
Job No: |  |  |  | Specifications: V/Line Standards, NIST-013.3, NIST-013.2 and L1-CHE-STD-077
|  |  |  | Structure / Component: OCS and Public Lighting |  | Signed : |  | Signed : |  |  | Signed :
|  |  |  | Location: |  | Date : 05/07/2022 |  | Date : 05/07/2022 |  |  | Date : 05/07/2022
Lot No: |  |  | Lot Details: | [5 empty] | Lot Size/ Quantity:
Item | Task/Activity Description |  | Inspection / Controls and Verification Detail |  |  |  |  | HP/ WP/ AP/ IP/ TP/ SCP | Responsibility | Checked by:
No. |  |  | Frequency | Acceptance Criteria | Reference Documents | Inspection / Test Method | Record of conformity |  | Project Engineer Site Engineer Superintendent Surveyor Foreman | Client | Fulton Hogan | FH's Sub-contractor | Date
1 | Preliminary Works
1.1 | Check for correct documentation |  | Prior to commencing any activity | Ensure that all employees and subcontractors are: -using the correct and complete set of drawings -all drawings are the latest revision | Drawings and drawing registers | Visual inspection | This ITP signed off | HP* | Fulton Hogan Engineer | N/A
1.2 | Implementation of all measures and controls |  | Prior to commencing any activity | All necessary measures and controls are being implemented, that is: OHSCP, PHSCP, PCMP, EMP, ECP, CEMP, ERA, QMP, CHMP, SWMS | OHSCP, PHSCP, PCMP, EMP, ECP, CEMP, ERA, QMP, CHMP, SWMS | Visual Inspection | This ITP signed off | HP* | Fulton Hogan Engineer | N/A
1.3 | Materials |  | Per Batch | • Carpark Lighting A pit is to be installed adjacent to each lighting pole with 1 x 100mm HD conduit and 1 x 63mm conduit installed between pit and the point of supply. 2 x 32mm HD conduits are to be installed between the pit and the pole mounting base. • Electrical supply conduit all conduits for underground mains shall be heavy duty 'Orange' underground category PVC pipe complying with the most recent issue of AS/NZS 3000 Australia/New Zealand Wiring Rules. • Communications conduit to be white 1C50 HD PVC conduits and 1C100 HD PVC conduits • Camera mounting poles and structures shall meet AS47806.2 (2006) Section 5.4.1 (k) • Cable pit lids shall be VicRoads type approved, impressed with 'VicRoads' and 'Electrical', 'Communication', 'Traffic signals" as appropriate as per VicRoads Standard Drawing TC-1220 •All equipment labelling to comply with requirements of NIST-013.4 • Cable pits shall be 435mm dia x 550mm deep, Type 43 plastic HDPE – Aco Cablemate cable pit with concrete lid or equivalent | NIST-5031 3.2.2.5 (f) Drawings | Verify | This ITP signed | HP* | Fulton Hogan Engineer, Electrical Subcontractor, Vline representative
2 | Construction Works
2.1 | Survey set-out |  | As required | Work is set out in accordance with drawings. | Work procedure, Drawings | Verify | This ITP signed | HP* | Fulton Hogan Engineer | N/A
2.2 | Excavation/Boring & Trenching |  | Prior to Backfill | Trenches shall be excavated to a depth required to achieve the specified depth of cover and drainage slope, plus an over-excavation of approximately 50 mm to allow for bedding sand. The width of trenches shall be as required to fit all the conduits and pipes for services sharing the trench with specified separations, plus a further 50 mm minimum clearance from the outermost pipes or conduits. Where trenches are excavated across roadways, car parks or paved areas, the Electrical Contractor shall backfill the trench with 20mm of Class 3 crushed rock. The crushed rock shall be placed in layers not exceeding 150mm finished depth and compacted to a minimum of 95% of standard density. The backfilling shall extend for a minimum of 1.0m outside all paved areas and shall be subject to the supervision of the V/Line delegated representative. | L1-CHE-STD-077 Sect 6.10.6 | Verify | This ITP signed | HP | Fulton Hogan Engineer | N/A
2.3 | Installation of Pit and Conduits |  | Each Lot | Underground conduits shall have a minimum 450mm cover if around the site but away from the track corridor, should only be in the non-trafficable areas. If exposed to traffic, the depth should be 650mm. Upon installation conduits shall be cleaned and tested using a mandrel of at least 90% of the conduit inner diameter and length three times the inner diameter. Multiple conduit entry penetration holes on a pit wall shall be spaced at least 50 mm apart in horizontal and vertical planes | NIST-013.3 Sect 4.2 L1-CHE-STD-077 Sect 6.9 | Verify | This ITP signed WP | IP | Fulton Hogan Engineer | N/A
2.4 | Back Fill of Trenches (Trafficable) |  | Each Lot | • Bedding: Graded recyclable glass in accordance with MTM standard L1-CHE-SPE-313 • Backfill: VicRoads 20mm class two crushed concrete base compacted to 95% of standard density in 150mm thick layers | NIST-5031 L1-CHE-SPE-313 MRP-708-C-AUR-DRG-20-TNT-CLT-0810 | Verify | This ITP signed | WP/ IP | Fulton Hogan Engineer | N/A
2.4 | Back Fill of Trenches (Non Trafficable) |  | Each Lot | • Bedding: Graded recyclable glass in accordance with MTM standard L1-CHE-SPE-313 or approved equivalent • Back Filling: Site or imported material containing no more than 20% mass of rock fragments with size between 75-150mm with no rock or clay fragments greater than 150mm. | MRP-708-C-AUR-DRG-20-TNT-CLT-0810 | Verify | This ITP signed | WP/ IP | Fulton Hogan Engineer | N/A
2.5 | Installation of Draw Cords |  | Each Lot | A draw wire of 6mm polypropylene blue/yellow rope shall be placed in each pipe and suitably anchored at each end. Pipe ends shall be sealed using pipe end caps or an approved equivalent to prevent the ingress of dirt or sludge into the pipes. | NIST-012 Sect 7.12(d) | Verify | This ITP signed | IP | Fulton Hogan Engineer | N/A
2.6 | Installation of Marker Tape |  | Each Lot | A 150 mm wide orange coloured PVC marker tape with the words “DANGER BURIED CABLES” shall be installed in all trenches at 300 mm below ground level except where cables are permitted in shallow trenches due to rock. In this case the depth of the marker tape shall be at the discretion of the Infrastructure Manager. | NIST-012 Sect 7.11.1 | Verify | This ITP signed | IP | Fulton Hogan Engineer | N/A
2.7 | Cable Pits & Pit Lids |  | Each Lot | • Cable pits constructed and installed as per drawings • Pits shall be placed at each horizontal change in direction or at spacing no greater than 100m • Seperate pits shall be used for power conduits (orange) and communications (white). | OCS Drawing Package | Verify | This ITP signed | IP | Fulton Hogan Engineer | N/A
3 | Completion
3.1 | Cleaning of Site |  | Each Lot | All obselete cabling to be removed during installation and disposed of appropriately. Upon removal of all redundant signalling equipment; the site shall be cleared of all project scrap and associated rubbish. | NIST-012.2 Sect 23 | Visual inspection | This ITP signed | IP | Fulton Hogan Engineer | N/A
3.2 | Recording/As Built |  | Each Lot | As-built drawings will be completed by the Contractor based upon the installed system by a process of editing the approved ‘for construction’ drawings. | NIST-013.3 Sect 5.1.3 | Verify | This ITP signed As Built Drawing | IP | Fulton Hogan Engineer | N/A
3.3 | Commisioning |  | Each Lot | Commisioning to be checked against V/Line checklist. For OCS Only | V/Line Commisioning Checklist | Verify | This ITP signed V/Line Checklist signed | WP/ TP | Fulton Hogan Engineer | N/A
Final Inspection
The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
| Print Name: |  | Position: |  | Signature: |  |  |  |  | Date: / /
Legend
HP | Hold Point | Work shall not proceed past the HP until released by the Superintendent |  |  | IP | Inspection point |  | Formal Inspection to be done and recorded
HP* | FH Hold Point | Work shall not proceed past the HP* until released by FH |  |  | TP | Test Point |  | Product compliance test to be undertaken and recorded/reported
WP | Witness Point | An inspection which must be witnessed by the Superintendent |  |  | SCP | Survey conformance point |  | A qualified surveyor to check product/section/structure and report
AP | Approval Point | Written or verbal approval given by the Superintendent
Note on K16: Rodrigo Anchico: Write "N/A" to disable the cell.