## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | EFPQF05 - Pre Action - Sprinkler Control Valve |  |  |  |  | Yes | EFPQF05 - Pre Action - Sprinkler Control Valve | 09e9855c-de7a-469f-b5da-187740cea5c8
checkpoint-group |  |  | section | Documentation
checkpoint-status |  |  | checkpoint | Confirm construction drawings approved for use.
checkpoint-group |  |  | section | Incoming Inspection
checkpoint-status |  |  | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
boolean | 6f265b20-a2e1-57e1-be54-1944dbf43285 |  | tickbox | Isolation valves.
boolean | 77b40736-da45-5fb8-a277-6567ee8f0c4d |  | tickbox | Alarm valves.
boolean | 58e2b6d5-cff1-5141-a264-db45ca59148a |  | tickbox | Pressure switches.
boolean | 30c759ff-fd23-5af7-82cd-8b39f7b48e0f |  | tickbox | Nitrogen generator/Air compressor
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Main stop valve installed
checkpoint-status |  |  | checkpoint | Alarm valve installed
checkpoint-status |  |  | checkpoint | Drain valve installed
checkpoint-status |  |  | checkpoint | Alarm pressure switches installed
checkpoint-status |  |  | checkpoint | Water motor alarm installed
checkpoint-status |  |  | checkpoint | Pressure gauges installed
checkpoint-status |  |  | checkpoint | Nitrogen generator/air compressor installed
checklist-sectioned |  |  | checklist | EFPQF03 - Wet Pipe Sprinkler Control Valve |  |  |  |  | Yes | EFPQF03 - Wet Pipe Sprinkler Control Valve | 111b8d5f-c017-40a7-b820-8b4f042e2db9
checkpoint-group |  |  | section | Documentation
checkpoint-status |  |  | checkpoint | Confirm correct construction drawings approved for use.
checkpoint-group |  |  | section | Incoming Inspection
checkpoint-status |  |  | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
boolean | 71ac039a-da39-53b5-a36b-3b506ae55690 |  | tickbox | Isolation valves.
boolean | 730811f9-a436-59db-8a92-919e3e7f142b |  | tickbox | Alarm valves.
boolean | bc90848f-34fb-5831-8093-4ce091e37ee8 |  | tickbox | Pressure switches.
boolean | b7386fea-7a3f-55c5-9cc6-4c0b76124857 |  | tickbox | Jacking pump
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Main stop valve installed
checkpoint-status |  |  | checkpoint | Alarm valve installed
checkpoint-status |  |  | checkpoint | Drain valve installed
checkpoint-status |  |  | checkpoint | Alarm pressure switches installed
checkpoint-status |  |  | checkpoint | Water motor alarm installed
checkpoint-status |  |  | checkpoint | Pressure gauges installed
checkpoint-status |  |  | checkpoint | Jacking pump installed
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned |  |  | checklist | EFPQF14 - Water Mist Install |  |  |  |  | Yes | EFPQF14 - Water Mist Install | 22a80371-f250-4f91-9034-1344ca23cf25
checkpoint-group |  |  | section | Documentation
checkpoint-status |  |  | checkpoint | Confirm construction drawings approved for use.
checkpoint-group |  |  | section | Incoming Inspection
checkpoint-status |  |  | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
boolean | 1236dcf9-0d0e-5422-8785-272772d35929 |  | tickbox | Pipe.
boolean | fe1c8281-72a6-55f3-a1cf-7913ede7dec3 |  | tickbox | Fittings.
boolean | e82de2c9-759b-5207-925f-36b87f33ffdb |  | tickbox | Hangers.
boolean | 9de35caa-4f92-56b5-a478-e3d255ebc844 |  | tickbox | Nozzles
boolean | 4559644a-036f-5946-9516-7983d112a041 |  | tickbox | Valves
checkpoint-group |  |  | section | Installation Rough In / Fit Off
checkpoint-status |  |  | checkpoint | Confirm maximum hanger spacing.
label | a2dc784a-d3bd-5704-af95-560aca0cc683 |  | note | ≤25mm - max 4m spacing.
label | 516d3ed3-f326-55bd-a1dd-0fd31fc2f9c1 |  | note | 32 – 100mm - max 5m spacing.
label | d084eea0-f926-5e59-9d4a-78e8856e1240 |  | note | Acceptance Criteria - AS:4587
checkpoint-status |  |  | checkpoint | Confirm support at change of direction at 1m max.
label | 2e92591f-5b67-5484-b737-49d94e23b376 |  | note | Acceptance Criteria - AS:4587
checkpoint-status |  |  | checkpoint | Confirm support of pipework no more than 1m from end.
label | 22f59c3d-57d4-5aea-8a4d-7c0a661a562b |  | note | Acceptance Criteria - AS:4587
checkpoint-status |  |  | checkpoint | Confirm support of armpiece exceeding 500mm.
label | c1a75051-82f7-5589-98cc-2e71dde45f2f |  | note | Acceptance Criteria - AS:4587
checkpoint-status |  |  | checkpoint | Confirm pipework installed as per drawing.
checkpoint-status |  |  | checkpoint | Confirm isolation and test valves installed
checkpoint-status |  |  | checkpoint | Cap installation and perform pressure test
label | 2003545d-042c-573b-8f1a-509e69a2b9cd |  | note | Acceptance Criteria - AS:4587
checkpoint-status |  |  | checkpoint | Confirm discharge nozzles installed.
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checkpoint-group |  |  | section | Pressure Test Report Sheet
checkpoint-status |  |  | checkpoint | Test Details & Results
text | e38d4b87-470d-51ea-81c7-035b692bc4a3 |  | textbox | Test number
select | 3ebf2613-0e2d-5c80-b364-97d6fe4de4dc |  | dropdown | Select relevant Test Criteria | WATER MIST - HYDRAULIC TEST - 3300kpa 2 HOURS - NO LOSS
text | 422182f6-dd5b-56fc-a0da-10ae0b8b4e7d |  | textbox | Start Date
text | 03e8d07a-af61-50c7-abb6-125d71aeaf23 |  | textbox | Start Time
text | d5d3c441-c342-5a5b-bb97-ea56e5e3d435 |  | textbox | Start Pressure
text | e5c10537-c27e-54ea-937e-2e0b2f6d8af2 |  | textbox | Finish Time
text | c9a78a56-798c-5f0e-8407-87a5cdcc1b4f |  | textbox | Finish Pressure
text | 01fb12a5-6b0f-53a2-88eb-60487ca4771b |  | textbox | Gauge Reference
checkpoint-status |  |  | checkpoint | Test completed to specification/drawings & Area left clean/tidy
label | b150872d-da4c-5e67-89c3-16fbc2f05c7b |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint-status |  |  | checkpoint | Entire Fire Sign-Off (attach signature)
checklist-sectioned |  |  | checklist | EFPQF15 - Fire Extinguisher & Blanket Install |  |  |  |  | Yes | EFPQF15 - Fire Extinguisher & Blanket Install | 372796d7-c0f9-49d6-a762-3b981a755c9d
checkpoint-group |  |  | section | Documentation
checkpoint-status |  |  | checkpoint | Confirm construction drawings approved for use.
checkpoint-group |  |  | section | Incoming Inspection
checkpoint-status |  |  | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
boolean | f5030450-22f7-541a-af01-4506dec9dc43 |  | tickbox | Fire Extinguisher.
boolean | a06a4182-eb22-59a5-b048-211e3a3c0e19 |  | tickbox | Fire Blanket.
boolean | 214451fc-b46c-5773-b833-dc35d040d2cf |  | tickbox | Signage.
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Confirm top of extinguisher handle ≤1200mm above floor level
label | ce6a60a0-d97c-579a-ac03-2bd6e3c6fc77 |  | note | Acceptance Criteria - AS:2444
checkpoint-status |  |  | checkpoint | Confirm extinguisher type signage located just above handle
label | 283327e0-cf61-5670-a0ec-a821baf362a5 |  | note | Acceptance Criteria - AS:4587
checkpoint-status |  |  | checkpoint | Confirm extinguisher location signage located at ≥2000mm above floor level
label | 090e087b-690e-5606-862b-c87bfef35f23 |  | note | Acceptance Criteria - AS:4587
checkpoint-status |  |  | checkpoint | Confirm fire blanket located in a readily accessible location
label | 287c758c-df06-5b85-a46c-94d80225499d |  | note | Acceptance Criteria - AS:4587
checkpoint-status |  |  | checkpoint | Confirm fire blanket signage provided adjacent to the fire blanket
label | 6d074bb8-ecf1-5220-8848-e7f6fee4f2bb |  | note | Acceptance Criteria - AS:4587
checkpoint-status |  |  | checkpoint | Confirm fire blanket location signage located at ≥2000mm above floor level
label | f9f999aa-1166-5f91-a528-ac697683c926 |  | note | Acceptance Criteria - AS:4587
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned |  |  | checklist | EFPQF04 - Pre Action - Sprinkler |  |  |  |  | Yes | EFPQF04 - Pre Action - Sprinkler | 406cb4f7-ccd4-491f-b50e-d90fbbc346d1
checkpoint-group |  |  | section | Documentation
checkpoint-status |  |  | checkpoint | Confirm correct construction drawings approved for use.
checkpoint-group |  |  | section | Incoming Inspection
checkpoint-status |  |  | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
boolean | 9aef36b3-79a3-52fd-8841-5b99c7922f38 |  | tickbox | Fabricated pipework - All pipe galvanised.
boolean | 5972d0e6-a55b-513f-be4a-45d0364eb63d |  | tickbox | Fittings - All fittings galvanised.
boolean | d08fe346-3b61-5e6d-88a1-acaf718629d6 |  | tickbox | Hangers - All hangers galvanised.
boolean | ff29940d-a758-5b00-9015-6d919fae039c |  | tickbox | Sprinklers.
boolean | 2dc5c9a0-a914-575d-858f-9d1fe95c280e |  | tickbox | Valves.
checkpoint-group |  |  | section | Installation Rough In / Fit Off
checkpoint-status |  |  | checkpoint | Confirm hanger spacing
label | 9100195f-a99d-50e4-8f89-3d6004a5d8a1 |  | note | 25mm - max 4m spacing.
label | d17d0b81-41ed-50f4-871f-62d5c40ec66a |  | note | 32 – 100mm - max 5m spacing.
label | eac96831-a6d3-5c9a-9658-d2c3a7ccc062 |  | note | ≥ 150mm - max 6m spacing.
checkpoint-status |  |  | checkpoint | Confirm support at change of direction at 1m max.
checkpoint-status |  |  | checkpoint | Confirm support of pipework no more than 1m from end.
checkpoint-status |  |  | checkpoint | Confirm support of armpiece exceeding 500mm.
checkpoint-status |  |  | checkpoint | Confirm first support of range pipe within 2m of mains.
checkpoint-status |  |  | checkpoint | Confirm pipework installed as per drawing.
checkpoint-status |  |  | checkpoint | Confirm pipework installed fall back to drain
checkpoint-status |  |  | checkpoint | Mains minimum 2mm per 1m.
checkpoint-status |  |  | checkpoint | Ranges minimum 4mm per 1m.
checkpoint-status |  |  | checkpoint | Confirm sprinklers installed.
checkpoint-status |  |  | checkpoint | Confirm sprinkler guards installed.
checkpoint-group |  |  | section | Pressure Testing
checkpoint-status |  |  | checkpoint | Confirm all open ends plugged.
checkpoint-status |  |  | checkpoint | Confirm isolation and drain valves are closed.
checkpoint-status |  |  | checkpoint | Fill pipework with air to 50kpa to confirm no open ends.
checkpoint-status |  |  | checkpoint | Fill pipework with water to 1600kpa. Hold 2 hours. No pressure loss permitted.
checkpoint-status |  |  | checkpoint | Fill pipework with air to 300kpa. Hold for 30 minutes. Pressure loss of 10% (60kpa) permitted.
checkpoint-status |  |  | checkpoint | Record pressure test results on Pressure Test Form.
checkpoint-group |  |  | section | Pressure Test Report Sheet
checkpoint-status |  |  | checkpoint | Test Details & Results
text | 6b3a6052-4fe6-58c4-bde5-8389eef7d421 |  | textbox | Test number
select | d4eb77e8-f1d0-5c5a-ae0a-ad98888cbdb7 |  | dropdown | Select relevant Test Criteria | PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa)
text | 3b04f0b7-cee4-5be4-add2-1f682b62edb7 |  | textbox | Start Date
text | 81b58a79-8a38-54df-970d-d9e1ffdff6ab |  | textbox | Start Time
text | 6c85620b-6a59-5823-858f-7aa276cb7e31 |  | textbox | Start Pressure
text | d06cd18e-74b9-5081-b514-d799ddcbebb8 |  | textbox | Finish Time
text | a6ebfcfb-1d71-5e46-af17-4122a998d42f |  | textbox | Finish Pressure
text | 76ee7cd6-0b5a-54b6-82c7-3d3ec86503f6 |  | textbox | Gauge Reference
checkpoint-status |  |  | checkpoint | Test completed to specification/drawings & Area left clean/tidy
label | efc9eca9-f5c9-55eb-b1fe-15f1211a1100 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint-status |  |  | checkpoint | Entire Fire Sign-Off (attach signature)
checklist-sectioned |  |  | checklist | EFPQF13 - Gas Suppression Install |  |  |  |  | Yes | EFPQF13 - Gas Suppression Install | 4aa5cf46-90aa-4ba1-985a-538f70510e42
checkpoint-group |  |  | section | Documentation
checkpoint-status |  |  | checkpoint | Confirm construction drawings approved for use.
checkpoint-group |  |  | section | Incoming Inspection
checkpoint-status |  |  | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
boolean | 77de4004-1465-5544-9d2b-5edbb448f53a |  | tickbox | Fabricated pipework.
boolean | 1724bf3d-724e-5523-a484-fbd0e0ff9dc2 |  | tickbox | Fittings.
boolean | ba5055e9-5d92-51c0-aea9-31e6655948d1 |  | tickbox | Hangers.
boolean | 5929cded-4900-5b2c-bdab-dc09062acc0c |  | tickbox | Nozzles
boolean | 519de37b-fe1c-5eab-af71-8a36470b6b16 |  | tickbox | Cylinders
boolean | d9fce2f0-b122-5006-a668-900e1d3063d4 |  | tickbox | Actuators
boolean | 9b60cfdd-a62a-5a7b-b42a-250f6d5c0f7f |  | tickbox | Hoses
boolean | 90c43eda-3666-5e7e-9f6e-c8ad888aaa31 |  | tickbox | Gauges
checkpoint-group |  |  | section | Installation Rough In / Fit Off
checkpoint-status |  |  | checkpoint | Confirm maximum hanger spacing.
label | 63207c3c-e441-553f-aef0-83962a830372 |  | note | 25mm - max 4m spacing.
label | 31f332c6-59ab-5561-9506-6dd4ce90b4e3 |  | note | 32 – 100mm - max 5m spacing.
label | a4d85e58-fee8-5a7f-8551-5d417fadc7b7 |  | note | ≥ 150mm - max 6m spacing.
label | dd28bb47-9a7f-5afe-a4af-56a54c46e124 |  | note | Acceptance Criteria - AS:2414
checkpoint-status |  |  | checkpoint | Confirm support at change of direction at 1m max.
label | 1fd1dac1-23e5-5b81-aee1-a40bce9518ce |  | note | Acceptance Criteria - AS:2414
checkpoint-status |  |  | checkpoint | Confirm support of pipework no more than 1m from end.
label | ff2a3dc5-d0c0-518b-9a34-007ccf8b7890 |  | note | Acceptance Criteria - AS:2414
checkpoint-status |  |  | checkpoint | Confirm support of armpiece exceeding 500mm.
label | c13af24b-59c2-5aa9-b155-3b96f6455167 |  | note | Acceptance Criteria - AS:2414
checkpoint-status |  |  | checkpoint | Confirm first support of range pipe within 2m of mains.
label | 5dbd1275-859a-56b3-a905-5b5c40829c51 |  | note | Acceptance Criteria - AS:2414
checkpoint-status |  |  | checkpoint | Confirm pipework installed as per drawing.
checkpoint-status |  |  | checkpoint | Cap installation and perform pressure test
label | cac14d95-d4a1-557f-8312-f387ad616c91 |  | note | Acceptance Criteria - AS:2414
checkpoint-status |  |  | checkpoint | Confirm discharge nozzles installed.
checkpoint-status |  |  | checkpoint | Confirm gas cylinder mounting as per manufacturer instruction
checkpoint-status |  |  | checkpoint | Confirm cylinder hoses fitted to discharge manifolds
checkpoint-status |  |  | checkpoint | Confirm cylinder pressure gauges fitted and indicating correctly
checkpoint-status |  |  | checkpoint | Confirm discharge actuators fitted
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checkpoint-group |  |  | section | Pressure Test Report Sheet
checkpoint-status |  |  | checkpoint | Test Details & Results
text | f9061108-e755-59f4-bcbe-0328f5110d04 |  | textbox | Test number
select | 96a64886-052a-568f-b040-13cfef70cabd |  | dropdown | Select relevant Test Criteria | GAS SUPPRESSION - PNEUMATIC TEST – 300kpa 10 MINS - PERMITTED LOSS 20% (60kpa)
text | 9597adff-c3f9-503a-99ad-afd9ed9786a7 |  | textbox | Start Date
text | 77706f9b-46b6-5f39-9aeb-62007ad07f1b |  | textbox | Start Time
text | 6a96fdd8-5b3a-5183-86cd-34f661bbd0b7 |  | textbox | Start Pressure
text | 60d8a2ca-1fe8-56e4-ace0-a5546ee2528e |  | textbox | Finish Time
text | a5a03141-ec31-5c72-b9ea-090f37aa888a |  | textbox | Finish Pressure
text | f5f3e57f-c1cc-5894-958f-deb525d039a2 |  | textbox | Gauge Reference
checkpoint-status |  |  | checkpoint | Test completed to specification/drawings & Area left clean/tidy
label | 78eb9954-eab7-554b-9891-9c4c763c74e0 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint-status |  |  | checkpoint | Entire Fire Sign-Off (attach signature)
checklist-sectioned |  |  | checklist | EFPQF09 - FDCIE Install |  |  |  |  | Yes | EFPQF09 - FDCIE Install | 631adbd1-26a0-49ce-bff7-a95c592b0add
checkpoint-group |  |  | section | Documentation
checkpoint-status |  |  | checkpoint | Confirm construction drawings approved for use.
checkpoint-group |  |  | section | Incoming Inspection
checkpoint-status |  |  | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
boolean | b6c9c0f4-64cc-53d7-828a-fc63d5f2c1c8 |  | tickbox | Fire rated cable
boolean | 996d76a6-f8dc-5ef4-8709-476319af9432 |  | tickbox | TPS cable
boolean | 79afd907-dc92-5efe-a1c8-934918efd159 |  | tickbox | FDCIE Panel
checkpoint-group |  |  | section | Installation Rough In / Fit Off
checkpoint-status |  |  | checkpoint | Confirm correct cable type run
checkpoint-status |  |  | checkpoint | Confirm cable support/conduit fixings and spacings
checkpoint-status |  |  | checkpoint | Confirm segregation from other electrical services
checkpoint-status |  |  | checkpoint | Confirm FDCIE mounted in correct location
checkpoint-status |  |  | checkpoint | Loop cables terminated to correct output
checkpoint-status |  |  | checkpoint | Confirm OWS cables terminated to correct output.
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned |  |  | checklist | EFPQF11 - Fire Tank Install |  |  |  |  | Yes | EFPQF11 - Fire Tank Install | 81c549ab-731f-465e-87a3-b99a90dd1ebf
checkpoint-group |  |  | section | Documentation
checkpoint-status |  |  | checkpoint | Confirm construction drawings approved for use.
checkpoint-group |  |  | section | Incoming Inspection
checkpoint-status |  |  | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
boolean | 49191d84-a818-5cbc-a4ee-9681ea841e01 |  | tickbox | Tank Panels.
boolean | fc01d898-0cf9-5938-844a-a7f756fe38c7 |  | tickbox | Roof Purlins.
boolean | fdbdce70-1822-5593-b8ff-a9d771dc9f73 |  | tickbox | Roof Sheet.
boolean | d585b8bf-a6d9-532a-bc1a-f7861b33ca58 |  | tickbox | Access ladder.
boolean | aafec75b-e559-53f3-980e-e3991b88948e |  | tickbox | Vortex.
boolean | 56e8b9d3-4a6b-52de-85af-c3ba4272a205 |  | tickbox | Pipe nozzles.
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Confirm tank slab tolerance within +/- 3mm
checkpoint-status |  |  | checkpoint | Build first panel ring
checkpoint-status |  |  | checkpoint | Build roof including access hatch
checkpoint-status |  |  | checkpoint | Hang tank liner
checkpoint-status |  |  | checkpoint | Fix tank jacks and lift for next panel install
checkpoint-status |  |  | checkpoint | Install ladder sections at each lift
checkpoint-status |  |  | checkpoint | Fix base ring and remove jacks
checkpoint-status |  |  | checkpoint | Ensure internal tank base free of debris
checkpoint-status |  |  | checkpoint | Install geo fabric to base
checkpoint-status |  |  | checkpoint | Stretch tank liner to tank base
checkpoint-status |  |  | checkpoint | Connect pipe nozzles and vortex
checkpoint-status |  |  | checkpoint | Confirm tank level indicator installed
checkpoint-status |  |  | checkpoint | Confirm tank capacity labels installed
checkpoint-status |  |  | checkpoint | Confirm warning labels installed
checkpoint-status |  |  | checkpoint | Confirm ladder guards and inspection hatches installed
checkpoint-status |  |  | checkpoint | Confirm no leaks when tank full
checkpoint-status |  |  | checkpoint | Copy of Installers statement attached
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned |  |  | checklist | EFPQF12 - Fire Brigade Booster Assembly Install |  |  |  |  | Yes | EFPQF12 - Fire Brigade Booster Assembly Install | 95d50e37-d5d1-4448-a0b3-30a00e722c68
checkpoint-group |  |  | section | Documentation
checkpoint-status |  |  | checkpoint | Confirm construction drawings approved for use.
checkpoint-group |  |  | section | Incoming Inspection
checkpoint-status |  |  | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
boolean | 57399eed-6701-518d-8e32-aa7716d3531b |  | tickbox | Fire Boosters
boolean | 2f224ac8-148a-5279-b1c3-d25665a1ba18 |  | tickbox | Suction Connections
boolean | ab90b7e1-fd9a-5e7a-a69d-c6dc3f1efe78 |  | tickbox | Feed Hydrants
boolean | 743af42b-e009-501d-b86c-d844a3051918 |  | tickbox | Isolation valves
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Confirm height of booster outlets between 750mm and 1200mm above standing surface in front of booster
checkpoint-status |  |  | checkpoint | Confirm height of feed hydrant outlets between 750mm and 1200mm above standing surface in front of booster
checkpoint-status |  |  | checkpoint | Confirm height of large bore suction connection between 450mm and 600mm above standing surface in front of booster
checkpoint-status |  |  | checkpoint | Confirm height of small bore suction connection minimum of 400mm above large bore suction connection
checkpoint-status |  |  | checkpoint | Maintain minimum 450mm centre to centre clearance between outlets
checkpoint-status |  |  | checkpoint | Confirm front face of all connections within 150mm of the front of cabinet
checkpoint-status |  |  | checkpoint | Confirm caps and chains installed
checkpoint-status |  |  | checkpoint | Confirm isolation valves chained and locked
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-flat |  |  | checklist | EFPQF19 - Calibration Record (x5) |  |  |  |  | Yes | EFPQF19 - Calibration Record (x5) | 9f116269-1857-4472-9110-3e2bae38b265
checkpoint-status |  |  | checkpoint | 1.Calibration Details - Pass once entered
text | 6f3e6b7e-a317-5b26-a233-cd8e5d70a290 |  | textbox | Equipment
text | 0fad2a3c-807e-5a4f-b50a-17dc5a0096e1 |  | textbox | ID Number
text | 13c9f4ed-40e1-581f-a968-dd02d6a04f66 |  | textbox | Expiry (If applicable)
text | 23ac8f93-2347-544d-aa5a-da5eeeb449d2 |  | textbox | Record Number
text | f42caf19-9209-5c47-838e-ce8464dc3546 |  | textbox | Date Calibrated
checkpoint-status |  |  | checkpoint | 1.Calibration Details - Pass once entered
text | 33ed4e72-a81d-5f57-b05d-ab66e8c0a3a5 |  | textbox | Equipment
text | 4bb37d36-101b-537f-81f2-0ad8257d31e0 |  | textbox | ID Number
text | 286ad1bf-6c14-51da-a4cd-8fa254a25d39 |  | textbox | Expiry (If applicable)
text | 0d7fbb62-759f-5aea-a7f1-c734473bd977 |  | textbox | Record Number
text | 74c746c6-d8aa-5123-9302-dd675cc21aff |  | textbox | Date Calibrated
checkpoint-status |  |  | checkpoint | 1.Calibration Details - Pass once entered
text | bcf1fdfb-56d0-5e3c-9382-6e32535abbfc |  | textbox | Equipment
text | 87f5be18-cf59-5112-9bcd-ccd96850fd16 |  | textbox | ID Number
text | 486cf6e9-0120-5d3b-8f92-58dc055abd0a |  | textbox | Expiry (If applicable)
text | e1f9d661-d5b7-54ef-8223-7eef6a9d6c51 |  | textbox | Record Number
text | 6dfc470f-35d6-5308-9dc1-823f6636b54b |  | textbox | Date Calibrated
checkpoint-status |  |  | checkpoint | 1.Calibration Details - Pass once entered
text | d04d06ab-7094-5f94-b692-de5b15dd8926 |  | textbox | Equipment
text | 938d9861-14ea-5294-8961-b7217903ef1a |  | textbox | ID Number
text | 6b118ca3-d089-5e30-8c29-ad80f492d637 |  | textbox | Expiry (If applicable)
text | 0e29d806-88a9-5a6d-9e6f-15565d43a42f |  | textbox | Record Number
text | dd737e4f-09e9-50d6-96ae-61c443042612 |  | textbox | Date Calibrated
checkpoint-status |  |  | checkpoint | 1.Calibration Details - Pass once entered
text | df2af8bf-44d5-5512-9f09-f63e54787426 |  | textbox | Equipment
text | 3d1825f3-ec6d-5120-ad06-649096d07e31 |  | textbox | ID Number
text | e107256f-ec8b-539a-84b4-c5a90ce26c73 |  | textbox | Expiry (If applicable)
text | 16cf997f-5013-5a57-9b92-0c08732b8828 |  | textbox | Record Number
text | 5e35ac06-b285-57d5-a7c8-04a848fe52a3 |  | textbox | Date Calibrated
checkpoint-status |  |  | checkpoint | Sign-Off Records completed
label | 9bec0c83-f8a4-5a9c-bbb3-a0de4e37522d |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | af6fa11e-a48d-503d-a81c-56eb0194ba0b |  | button | Entire Fire Signature Sign-Off added below | Yes, No
checklist-sectioned |  |  | checklist | EFPQF07 - Fire Alarms Install |  |  |  |  | Yes | EFPQF07 - Fire Alarms Install | aa718109-e144-458b-ab9f-3fe4bc968751
checkpoint-group |  |  | section | Documentation
checkpoint-status |  |  | checkpoint | Confirm construction drawings approved for use.
checkpoint-group |  |  | section | Incoming Inspection
checkpoint-status |  |  | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
boolean | ee7df70d-7334-50e5-98dd-b27d0749117c |  | tickbox | Fire rated cable
boolean | 3ff99e7f-0627-5614-802e-abcbb1e6b324 |  | tickbox | TPS cable
boolean | e9ef973a-40d7-5513-98d0-a10d121bf069 |  | tickbox | Detectors
boolean | 5a1dc367-1a6b-5f1d-b775-6eb4af6fe4b5 |  | tickbox | Strobes
boolean | a41f5dd0-7692-5c33-8be8-a045fb7abc12 |  | tickbox | Speakers
checkpoint-group |  |  | section | Installation Rough In / Fit Off
checkpoint-status |  |  | checkpoint | Confirm correct cable type run
checkpoint-status |  |  | checkpoint | Confirm cable support/conduit fixings and spacings
checkpoint-status |  |  | checkpoint | Confirm segregation from other electrical services
checkpoint-status |  |  | checkpoint | Confirm detector fit off locations
checkpoint-status |  |  | checkpoint | Confirm speaker fit off locations
checkpoint-status |  |  | checkpoint | Confirm strobe fit off locations
checkpoint-status |  |  | checkpoint | Confirm fire interfaces connected to sprinkler installation
checkpoint-status |  |  | checkpoint | Confirm fire interfaces connected to security
checkpoint-status |  |  | checkpoint | Confirm fire interfaces connected to mechanical
checkpoint-status |  |  | checkpoint | Confirm fire interfaces connected to BMS
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned |  |  | checklist | EFPQF08 - MASDS Install |  |  |  |  | Yes | EFPQF08 - MASDS Install | be274e2c-b6bf-4f52-adda-7bd8407de80b
checkpoint-group |  |  | section | Documentation
checkpoint-status |  |  | checkpoint | Confirm construction drawings approved for use.
checkpoint-group |  |  | section | Incoming Inspection
checkpoint-status |  |  | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
boolean | 557a8a79-3f36-55db-9ed8-86d9b3c10216 |  | tickbox | Fire rated cable
boolean | fb68099e-11f6-55f7-9b92-6d3acac34248 |  | tickbox | TPS cable
boolean | d5f7b070-3774-5730-b085-232e2216bf85 |  | tickbox | MASDS units
boolean | d5e2349a-1045-5cf5-a43d-445322b531eb |  | tickbox | MASDS pipework
boolean | 4a92f314-23ed-50f3-9019-f7afe91fd1fc |  | tickbox | MASDS Power supplies
checkpoint-group |  |  | section | Installation Rough In / Fit Off
checkpoint-status |  |  | checkpoint | Confirm correct cable type run
checkpoint-status |  |  | checkpoint | Confirm cable support/conduit fixings and spacings
checkpoint-status |  |  | checkpoint | Confirm segregation from other electrical services
checkpoint-status |  |  | checkpoint | Confirm MASDS pipework installed as per drawing
checkpoint-status |  |  | checkpoint | Confirm MASDS sampling points size & spacing
checkpoint-status |  |  | checkpoint | Confirm MASDS unit fit off locations
checkpoint-status |  |  | checkpoint | Confirm MASDS power supply fit off locations
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned |  |  | checklist | EFPQF01 - Fire Service Pump Install |  |  |  |  | Yes | EFPQF01 - Fire Service Pump Install | ce3fe4e3-f186-4646-a11f-5bc1a56e6488
checkpoint-group |  |  | section | Documentation
checkpoint-status |  |  | checkpoint | Confirm correct construction drawings approved for use.
checkpoint-group |  |  | section | Incoming Inspection
checkpoint-status |  |  | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
boolean | 3a77bc79-4f2b-5bcf-948e-77f681faae0d |  | tickbox | Fire service pumps
boolean | 254ac606-7b20-56f2-ad2a-566a505892f7 |  | tickbox | Pump control panels
boolean | 4c3d8154-9ee3-5205-bdcd-57f2c212a5d5 |  | tickbox | Valves
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Plinths positioned. Min height 150mm
checkpoint-status |  |  | checkpoint | Pumps positioned on plinth
checkpoint-status |  |  | checkpoint | Minimum 1.0-meter clearance required around perimeter pumpset.
checkpoint-status |  |  | checkpoint | Suction connected including isolation valves
checkpoint-status |  |  | checkpoint | Pressure relief valves and drain installed
checkpoint-status |  |  | checkpoint | Discharge check valves installed upstream of discharge isolation valve
checkpoint-status |  |  | checkpoint | Discharge connected including isolation valves
checkpoint-status |  |  | checkpoint | Suction and discharge pressure gauges installed
checkpoint-status |  |  | checkpoint | Flow test arrangement installed
checkpoint-status |  |  | checkpoint | Pump start pressure switches installed and wired
checkpoint-status |  |  | checkpoint | Control panels installed and wired
checkpoint-status |  |  | checkpoint | Battery trays installed
checkpoint-status |  |  | checkpoint | Circulation relief piped to drain
checkpoint-status |  |  | checkpoint | Gland drains installed
checkpoint-status |  |  | checkpoint | Diesel exhaust and muffler installed discharging to atmosphere
checkpoint-status |  |  | checkpoint | External bell and strobe installed
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned |  |  | checklist | EFPQF10 - Fire Hydrant & Hosereel Install |  |  |  |  | Yes | EFPQF10 - Fire Hydrant & Hosereel Install | d81896eb-58c1-461c-a058-6f5058a70709
checkpoint-group |  |  | section | Documentation
checkpoint-status |  |  | checkpoint | Confirm construction drawings approved for use.
checkpoint-group |  |  | section | Incoming Inspection
checkpoint-status |  |  | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
boolean | 1edce9fd-5781-58a3-9fad-2bac9ec9fa3a |  | tickbox | Pipework.
boolean | 8b854722-2aff-5edc-9167-eb00f6de2e9c |  | tickbox | Fittings.
boolean | b1eb292c-7881-5be8-9f05-42ee146268eb |  | tickbox | Hangers.
boolean | 2e5930de-ae78-5f1b-81c4-3637659fdd6d |  | tickbox | Isolation valves.
boolean | 964f0a59-1668-5dd2-855d-6e33e4347e5e |  | tickbox | Hydrant valves.
boolean | ec3e6b83-84a7-56be-bf94-5bf91347dc34 |  | tickbox | Hosereels
checkpoint-group |  |  | section | Installation Rough In / Fit Off
checkpoint-status |  |  | checkpoint | Confirm hanger spacing.
label | 97c26f60-7942-5b4d-95cc-cdb1504d44f0 |  | note | 100mm - max 5m spacing.
label | db850d68-b778-50e9-8c0f-4f28cb702b0a |  | note | ≥ 150mm - max 6m spacing.
checkpoint-status |  |  | checkpoint | Confirm support at change of direction at 1m max.
checkpoint-status |  |  | checkpoint | Confirm support of pipework no more than 1m from end.
checkpoint-status |  |  | checkpoint | Confirm support of horizontal branch from vertical riser no more than 300mm from riser
checkpoint-status |  |  | checkpoint | Confirm pipework installed as per drawing.
checkpoint-status |  |  | checkpoint | Confirm hydrant height at handle between 750mm and 1200mm
checkpoint-status |  |  | checkpoint | Confirm minimum clearance around hydrant handle 100mm
checkpoint-status |  |  | checkpoint | Confirm hydrant valve outlet not inclined more than 35° from horizontal
checkpoint-status |  |  | checkpoint | Confirm outlet has 300mm clearance for a minimum 225 degrees
checkpoint-status |  |  | checkpoint | Confirm hosereel mounting height 1400- 2400mm to centre of barrel
checkpoint-status |  |  | checkpoint | Isolation valve height is 900 – 1100mm
checkpoint-status |  |  | checkpoint | Maintain 100mm clearance around barrel
checkpoint-status |  |  | checkpoint | Confirm hydrant cap and chain installed
checkpoint-status |  |  | checkpoint | Confirm installation pressure gauge installed at top of most remote hydrant
checkpoint-status |  |  | checkpoint | Confirm pipe identification labels installed
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-flat |  |  | checklist | EFPQF06 - Pressure Test Report Sheet |  |  |  |  | Yes | EFPQF06 - Pressure Test Report Sheet | e3d69182-b9b6-4334-b84e-bd3e65411ee7
checkpoint-status |  |  | checkpoint | Test Details & Results
text | 74e78898-5695-5739-a388-8039a6e8749a |  | textbox | Test number
select | dd4f94ab-4763-5999-aaa2-b97bfb87587e |  | dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (60kpa)
text | a600b9fe-1d06-57de-bf48-86f308cad12b |  | textbox | Start Date
text | 53021927-fd0d-5802-a02b-269da3eca161 |  | textbox | Start Time
text | d15b9944-30b8-575f-b485-71599e882252 |  | textbox | Start Pressure
text | 10bc2abc-1976-5269-88bb-b5781b8e61d0 |  | textbox | Finish Time
text | 8ed32d80-ce67-5ab5-9b05-b39cd986825c |  | textbox | Finish Pressure
text | 6a8f973a-646e-546f-8c7d-69d7c75e9dc3 |  | textbox | Gauge Reference
checkpoint-status |  |  | checkpoint | Test completed to specification/drawings & Area left clean/tidy
label | 82d807c3-82d8-5e05-996d-83bc56e92791 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint-status |  |  | checkpoint | Entire Fire Sign-Off (attach signature)
checklist-sectioned |  |  | checklist | EFPQF02 - Wet Pipe Sprinkler Install |  |  |  |  | Yes | EFPQF02 - Wet Pipe Sprinkler Install | e4c5183a-6aa3-4776-866d-18d877cea012
checkpoint-group |  |  | section | Documentation
checkpoint-status |  |  | checkpoint | Confirm correct construction drawings approved for use.
checkpoint-group |  |  | section | Incoming Inspection
checkpoint-status |  |  | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
boolean | b8f62c16-507b-53b1-82c5-c3bf2c9eb861 |  | tickbox | Fabricated pipework.
boolean | b1bf13e7-6ac1-545e-ac82-c8d60a1dcdee |  | tickbox | Fittings.
boolean | b8e2471d-da18-522a-854b-fb807c01fc31 |  | tickbox | Hangers.
boolean | 15af13a0-f753-55e7-8814-32f9e431b993 |  | tickbox | Sprinklers.
boolean | 5502c2f0-fcae-52f3-b02b-a47b13cf748d |  | tickbox | Valves.
checkpoint-group |  |  | section | Installation Rough In / Fit Off
checkpoint-status |  |  | checkpoint | Confirm hanger spacing.
label | 8059895e-3495-5a2e-b9a5-293b3034cc36 |  | note | 25mm - max 4m spacing.
label | bde95ed2-fbb4-517d-8650-6df0986a03dd |  | note | 32 – 100mm - max 5m spacing.
label | 8ccd7439-00fb-5dd3-84b5-377e4816bf0b |  | note | ≥ 150mm - max 6m spacing.
checkpoint-status |  |  | checkpoint | Confirm support at change of direction at 1m max.
checkpoint-status |  |  | checkpoint | Confirm support of pipework no more than 1m from end.
checkpoint-status |  |  | checkpoint | Confirm support of armpiece exceeding 500mm.
checkpoint-status |  |  | checkpoint | Confirm first support of range pipe within 2m of mains.
checkpoint-status |  |  | checkpoint | Confirm pipework installed as per drawing.
checkpoint-status |  |  | checkpoint | Confirm sprinklers installed/Fit Off
checkpoint-status |  |  | checkpoint | Confirm sprinkler guards installed.
checkpoint-group |  |  | section | Pressure Testing
checkpoint-status |  |  | checkpoint | Confirm all open ends plugged.
checkpoint-status |  |  | checkpoint | Confirm isolation and drain valves are closed.
checkpoint-status |  |  | checkpoint | Fill pipework with water to 1600kpa. Hold 2 hours. No pressure loss permitted.
checkpoint-status |  |  | checkpoint | Record pressure test results on Pressure Test Form.
checkpoint-group |  |  | section | Pressure Test Report Sheet
checkpoint-status |  |  | checkpoint | Test Details & Results
text | 837bae02-bc94-59a5-bcfe-c55170897b4c |  | textbox | Test number
select | e81cc654-ed81-57a0-8ed0-c4fe245d7ff5 |  | dropdown | Select relevant Test Criteria | WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS
text | 8aedb5a8-ccef-5cf9-aa08-ef25a30abb7e |  | textbox | Start Date
text | 0ed98a02-c766-580c-aaa8-9aa5f1ef9883 |  | textbox | Start Time
text | 8ff29d83-a88f-554a-afd0-63e56f3619ce |  | textbox | Start Pressure
text | cb9dd8df-a244-55e4-bc39-dd3376c2dd93 |  | textbox | Finish Time
text | 2540b78c-c3fb-5f3d-8d16-3bcbfccdb7d1 |  | textbox | Finish Pressure
text | 7ae35314-8565-5a8e-8ad1-5b7ae8e0c960 |  | textbox | Gauge Reference
checkpoint-status |  |  | checkpoint | Test completed to specification/drawings & Area left clean/tidy
label | 5979d606-9f69-5723-bf3e-7727ab6187eb |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint-status |  |  | checkpoint | Entire Fire Sign-Off (attach signature)