## ITP Cover Page
Whiore Avenue - Wastewater Drainage - Inspection and Test Plan
Project: Tauriko Enabling Project
Number and Revision: DN1210-SP2 - ITP 022-001 - Rev 1
SECTION 1 – GENERAL DETAILS
Project Name: |  |  | Tauriko Enabling Project |  |  |  |  | ITP Number: |  |  | ITP 022-001
Project Number: |  |  | DN1210-SP2 |  |  |  |  | ITP Status: |  |  | IFC
ITP Description: |  |  | Whiore Avenue Wastewater Open Cut/HDD |  |  |  |  | Revision: | 1000 |  | 1
Contract Number: |  |  | 8287 |  |  |  |  | Drawing Sets: |  |  | 232735.02-WSP-DR-WST
Customer: |  |  | Waka Kotahi |  |  |  |  | Specification: |  |  | SH29 Tauriko West Enabling Works Contract No.NZTA8287 Section 22
Quality Specified: |  |  | ISO 9001:2015
Review / Update History | [9 empty] | Verification Activity
Rev: | Status: | Date: |  | Reviewed By: |  | Revision Details: |  |  |  | Activity Key |  |  | Responsibilities Key
0 | Draft for Approval | 2025-07-02 |  | Cordelia Girdler-Brown & Nick Adams |  | CWP 9.1 Please ensure welds are carried out with DVS 2207-1 Added: PE Butt Welding Specification – DVS 2207-1 CWP 9.1 Please ensure the welding WMS is submitted 5 days prior to commencement of the pre-construction welding. Refer to specs for items to be covered off. Already provided within Appendix A. See section 9.1 on jointing. CWP 14.2 Typo noted 'T601' - please change this to T611 Fixed typo to T611 ITP 3.10 The PSD on the ITP is for GAP20. Refer to table G3 for PSD of sand for embedment material Changed to follow table G3 for PSD of sand ITP 9.3/9.4/9.16 acceptance criteria is not wrong, however spec reference refers to pumice sand not AP65. Please refer to Appn. XVIII Updated to appendix XVIII ITP11.3 Unsure where shear vane testing results came from. These should be as per the earthworks specs (125kPa) Changed to: For site won min 125kPa (shear vane) For the JSEA please include working at night and working within the road corridor as hazards. Added to the JSEA 23-24. CWP19, ITP13 As per discussion, road reinstatement methodology is to be added into CWP Added to CWP section 19 under pavement reinstatement. Following TCC requirements. Added ITP pavement requirements section 13 ITP 14-15/ CWP 5 Added comms duct installation |  |  |  | A | Action |  | ENG | Engineer / Engineer's Rep
[10 empty] | B | Report by Breach |  | CR | Customer Rep
[10 empty] | C | Check |  | PD | Project Director
[10 empty] | D | Dimension Inspection |  | PM | Project Manager
[10 empty] | E | Examine |  | OP | Operations Manager
[10 empty] | HP | Hold Point (Engineer) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) |  | HSE | HSE Manager / Rep
[10 empty] | H | Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) |  | PE/SE | QA Manager / Rep
[10 empty] | I | Inspection (Formal inspection activity to be undertaken and recorded) |  | PE | Project Engineer
[10 empty] | M | Monitor on Random Basis |  | SE | Site Engineer
[10 empty] | O | Operation |  | QE | Quality Engineer
[10 empty] | R | Review |  | SUP | Superintendent / Supervisor
[10 empty] | S | Subcontractor |  | SV | Surveyor
[10 empty] | V | Visual Verification |  | ITP | Third Party Inspector
[10 empty] | W | Witness Point (Review of text reports/records or other evidence of compliance) |  | SPEC | Specialist
SECTION 2A – ITP Approval | [7 empty] | SECTION 2B – ITP CLOSEOUT
Position |  | Name: |  |  | Signature: |  | Date: | Position |  | Name: |  | Signature: |  |  | Date:
Downer PM |  | NICK ADAMS |  |  | #VALUE! |  | 2025-03-10 | Downer PM |  | NICK ADAMS
Downer QM |  | CORDELIA GIRDLER-BROWN |  |  |  |  | 2025-03-10 | Downer QM |  | CORDELIA GIRDLER-BROWN
Client (If Applicable) | [7 empty] | Client (If Applicable)

## ITP Master Body
Wastewater Drainage Installation - Whiore Avenue
Tauriko Enabling Works
DN1210 - SP2- ITP022-001 - REV 1
Item No. | Inspection and Test Point | Detail / Activity | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Testing Quantity Required (based from schedule qtys) | Verification Activity |  | Downer Conformance of Compliance Signoff
[7 empty] | Activity | By | ConQA Signature | Date | Comments / Closeout Details | ENGINEERS COMMENTS - Date: | DOWNER RESPONSE - Date:
3 | PRE-CONSTRUCTION HOLD POINTS - MATERIALS, PERSONELL & THIRD PARTY APPROVALS
3.1 | Extent of Line Setout | Ensure line and level of Wastewater has been marked out and agreed with Engineer in accordance with Waste water drawings. Identify any clashes before construction. LOT- markup | As Per Drawings & Markup drawing | Design Drawings | ITP Sign Off / Mark-up | Prior to Construction & Every Revision of IFC Drawings/Data. | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.2 | Pipe Laying | Method statement | As Per Specification and IFC Drawings | PS- 22.3 Appendix V | Wastewater Construction Work Pack Sign off | Prior to Construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.3 | Pipeline Pressure Testing | Method statement | As Per Specification and IFC Drawings | PS- 22.3 Appendix V | Wastewater Pipeline Pressure Testing Work Pack Sign off | Prior to Construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.4 | Butt-Fusion pre construction weld test | One weld on the most common size of pipes used for the project. One weld on the thickest wall (highest PN) pipe | ISO 13953 for tensile strength and failure mode. WMS Report | PS 22.9.6 (a) | Visual Inspection | Two test welds per operative(Welder) | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.5 | EF pre construction Weld Tests | Use the designated welding equipment and the approved WMS. On the largest size of PE pipe used in this Contract | ISO 21751 (strip-Bend test) or ISO 13954 (Peel-decohesion test) WMS Report | PS 22.9.6 (b) | Laboratory Test Report | Prior to Construction. One test welds per operative(Welder) | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG |  |  |  |  | Added EF Pre-construction test incase we get approved to use
3.6 | Material grading: Materials (GAP65/AP65) | NZS4407:2015, Test 3.8.1 - Particle Size Distribution | No Particles >200mm Maximum fines 10% passing 75micron sieve | PS 22.13.1 Appendix XVIII PS 16.5.5 Appendix V | Lab Test Report NZS 4407.3.8.1 | Stockpile Size (m3): 0-400 - 2 tests 400-1,500 - 3 tests 1,500-4,000 - 4 tests >4,000 - 1 test for each additional 1,000m3 Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.7 | Weathering index: Materials (GAP65/AP65) | NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate | AA, AB, AC, BA, BB, or CA | Appendix XVIII PS 16.5.5 Appendix V | IANZ Accredited Report | 2 Tests Per Material, Per Source Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.8 | Crushing Resistance: Materials (GAP65/AP65) | NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load | >100KN | Appendix XVIII Appendix V | IANZ Accredited Report | 2 Tests Per Material, Per Source Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.9 | Maximum Dry Density and Optimum Water Content (AP65/GAP65) | NZS4402:1986, Test 4.1.2 - Heavy Compaction Test | Report Value Only | Appendix XVIII Appendix V | IANZ Accredited Report | 1 Test Per Material, Per Source Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.1 | Material grading: Materials (Sand) | Bedding/Side Zone/ Overlay Zone/Embedment Zone | Sand: Sieve Size % Passing 4.75mm 100% passing 2.36mm 90-100% passing 1.18mm 85-100% passing 0.600mm 70-100% passing 0.300mm 50-100% passing 0.150mm 0-40% passing 0.075mm 0-5% passing | AS/NZS 2566.2 Table G3 PS 22.4.5 | Lab Test Report NZS 4407.2015 Test3.8.1 | 0-400m3 2 Test 400-1500m3 3 Test 1500-4000m3 4 Test >4000 1 Test Additional 1000m3 | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG |  |  |  | The PSD on the ITP is for GAP20. Refer to table G3 for PSD of sand for embedment material | Changed to G3 table PSD for sand
3.11 | Pipes (PE/PVC) | Manufacturer's record and location of extrusion plants. PVC pipes must be Series 1, plain wall construction, rubber ring jointed pipe, unless shown otherwise on the Drawings. All PVC-U (Unplasticised) pipe must conform to the requirements of AS/NZS 1477. Name of the proposed PE resin, the manufacturer, production information on the properties of resin. Full Traceability information and certification of analysis for the resin batch. | Full Traceability information and certification of Material | PS-22.4.1 (d) AS/NZS 1477 | Delivery Dockets | Prior to construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.12 | Flanges, Fittings and bends | Have a pressure rating no less than the designed pressure. Mechanically, chemically and electrically compatible with the class and material of the pipe. Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose. | Engineer approval AS/NZS 4129 | PS-22.4.2 | Delivery Dockets | Prior to construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.13 | Pipe and fittings/bends | Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | Design Drawings | Delivery Dockets / Inspection Checksheet (DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.14 | Fittings (rubber rings) | Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition. | Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition. | PS-22.4.2 | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.15 | Granular Material (Sand, GAP65/AP65) | Confirm Specification and material in good condition. | Confirm Specification and material in good condition. | PS-22.4.1 | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.16 | Bidim/Geogrid | BIDIM A29 Durogrid 30/30 or similar. | Site Engineer Approval | PS-22.4.1 | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.17 | Reinforcing steel (manhole ballast) | Manhole ballast reinforcing steel. | Grade 500E, Confirm the class and type as shown in the drawings. | AS/NZS 4671 Project Specification | Material Certifications. Delivery Dockets | Each Delivery to site | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
3.18 | Wastewater Manhole (WWMH-12 to WWMH-20) | Confirm the class and type as shown in the drawings, and fittings required for MH is same | Confirm the class and type as shown in the drawings, and fittings required for MH is same | Design Drawings | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.19 | Wastewater manhole (WWMH-21 stilling chamber) | Confirm the class and type as shown in the drawings, and fittings required for MH is same | Confirm the class and type as shown in the drawings, and fittings required for MH is same | Design Drawings | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.2 | Horizonal Directional Drilling | Detailed methodology of directional drilling | Engineer Approval | PS 21.6.6a | Engineer APPROVAL | Prior to construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG |  |  |  |  | Added Directional drilling as we have a seperate CWP for HDD that links to this ITP
3.21 | Grouting Methodology | Cement grouting the sleeve annulus | Enginner Approval | PS 21.6.6g | Engineer approval | Prior to construction | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | ENG
3.22 | Pavement reinstatement - Asphalt type to confirm | Prior to construction, confirm with Engineer the type of asphalt to be used. | Asphalt specification. | TCC T460 | Engineer approval | Prior to construction | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | ENG
3.23 | Pipe and fittings. Ducts | Duct Pipes shall be of the 50mm Ducts shall be high impact uPVC Duct colours shall be Salmon Duct colours for the different Utility Structures must be in accordance with the guidelines. | Duct Pipes shall be of the 50mm Ducts shall be high impact uPVC Duct colours shall be Salmon Duct colours for the different Utility Structures must be in accordance with the guidelines. | PS 25.13.6 b) | Delivery Dockets/Material Certification | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | SE
3.24 | Pits Covers | Jointing and pulling pits shall have slip resistant surfaces complying with AS/NSZ 3661-1-1993. the cover set load rating shall be in compliance with AS3996. | Class A-10kN loading - footways and areas only accessible to pedestrian and cyslists. Class B- 80kN loading - footways that may be mounted by vehicle or livestock and light tractor paths. (Light duty) Class C- 150kN loading - grass verges or other areas open to slow moving commercial vehicles such as tractor mowers etc (medium duty) Class D-120kN loading - Carriageway of roads and areas open to commercial vehicles (heavy duty) | PS 25.13.6 c) AS/NZS 3661-1- 1993. | Material Certifications. Delivery Dockets | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | SE
4 | CONSTRUCTION - WASTEWATER PIPELINE - Excavation and Laying
4.1 | Foundation Compliance | On Granular or Cohesive Material | Granular Material: Scala 3 blows/100mm (Or) Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa | Appendix V Table 21:11 | Scala/Shear test result | One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE/ENG
4.2 | Undercut approval | Trench Foundation | 300mm Max cut IFC Drawing Sheet 320 (Or) Engineers approval | IFC Drawing WST 0320. AS/NZS 2566.2/2002 | Lab Test Report / Wastewater line record | If Undercut required | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE/ENG
4.3 | Undercut Backfill Compliance (PAP5) | On Granular Material / On each layer as per specification / on the trench foundation. | Visiual Inspection | IFC Drawing WST 0320 | Lab Test Report / Wastewater line record | Every Undercut | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE/ENG
4.4 | Bedding Zone Compaction Testing | On Granular Material / On each layer as per specification (Sand) | Bedding Zone: 100mm minimum thickness (compacted) over the bottom of the trench. Minimum Compaction- 85%MDD Paeangaroa Sand: clegg of ave 9 CIV and min of 7 CIV. Wilson Sand No.2: clegg 4 CIV | IFC Drawing 0320-1 AS/NZS 2566.2/2002 | Lab Test Report | As per WW Specification. One test per 20m evenly spaced intervals. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.5 | Laying of Pipes | Lay in straight lines, beginning at the lower end of the line. Lay all pipe with manufacturing codes and class markings facing upwards. | As Per Drawings. Facing upwards | PS22.7.1 C | Visual Inspection / Wastewater line record | Every Line | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.6 | Pipe Installation on Curved Alignments | All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202) | AS Per POP 202 | PS 22.7.1 D | Visual Inspection / Wastewater line record | Every Line | M Monitor on Random Basis | SE
5 | CONSTRUCTION ACTIVITY - WASTEWATER PIPELINE (Joint and Connection)
5.1 | Flanges | Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification. | Flanges to AS/NZS 4087 | PS 22.7.5 | Visual Inspection | First flanged joint | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
5.2 | Bends | PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings. Fitting must meets the same PN rating as the adjacent PE 100. Fittings must be suitable for producing the joints shown on the Drawings. | PIPA POP 006 and AS/NZS 4129 | PS 22.4.2 | Visual Inspection | As per the IFC drawing | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
6 | CONSTRUCTION ACTIVITY - WASTEWATER PIPELINE (Butt-Fusion Welding)
6.1 | Butt-Fusion Welding | Use only semi-automatic or automatic welding machines. Maintain a site record for all butt-fusion welds. The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct. | Site Butt Fusion Welding record to be filled out. (Refer to CWP) WMS Report | Appendix 22. PS 22.9.4 C | Visual Inspection / Butt Fusion welding records checklist. WMS Report | Every Welding Point | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
6.2 | Butt-Fusion Construction weld test | Test at least two welds from the first 50 welds. One of the welds to be selected by the Engineer for satisfactory result. | Tensile testing and ductility of welds. | PS- 22.9.6 (a) (iv) | Test report | Two welds for the first 50 welds | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
6.3 | Survey | Inspection of Pipeline Inverts | Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance | PS- 21.7.6 Table 21.15 | Survey Data / As-built record | Pipeline invert to be surveyed at chainages as indicated in the drawings. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
6.4 | Photograph of Each Weld | Take sharply focused photo while clamped | Unique weld identifier visible | N/A | Weld Records; Photos | Each weld | I Formal inspection activity to be undertaken and recorded. | SUB
7 | CONSTRUCTION ACTIVITY - WASTEWATER PIPELINE - Electrofusion Welding
7.1 | EF Construction weld test | EF weld quality to be maintained. | EF coupler and EF saddle testing | PS- 22.9.6 (b) (iv) | Test report | 1 test per 5 welds | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
7.2 | EF Welding | Required if Butt fusion welding cannot be perform. EF Jointing in accordance with PIPA POP 001. The lead welder or welding supervisor must verify on the site record form. | Site EF Welding record to be filled out. (Refer to CWP) and checklist. Photo of every weld. WMS Report | PS 22.9.5 Appendix 22 | Visual Inspection / Electrofusion (EF) welding record checklist. WMS Report | Every Welding Point | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
7.3 | Survey | Inspection of Pipeline Inverts | Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance | PS- 21.7.6 Table 21.15 | Survey Data / As-built record | Pipeline invert to be surveyed at chainages as indicated in the drawings. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
7.4 | Photograph of Each Weld | Take sharply focused photo while clamped | Unique weld identifier visible | N/A | Weld Records; Photos | Each weld | I Formal inspection activity to be undertaken and recorded. | SUB
8 | CONSTRUCTION ACTIVITY - WASTEWATER PIPELINE INSTALLATION - Directional Drilling
8.1 | Check levels while drilling | Inspection of Pipeline Inverts | Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance | PS- 21.7.6 Table 21.15 | Survey Data / As-built record | Pipeline invert to be surveyed at chainages as indicated in the drawings. | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
8.2 | Drilling Fluid Mix | Viscosity record | Viscosity record | PS 21.6.6 | Viscosity record /checksheet | Every shot | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
8.3 | Correct Reamer used | Reamer size to confirm on site | Reamer size to confirm on site | PS 21.6.6 | Checksheet | 1 per drill shot | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
8.4 | Pipe Damage | Damage <10% of wall thickness | Damage <10% of wall thickness | PS 21.6.6 | Visual inspection | Each pipe | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
8.5 | Tracer Wire | Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings. Mark fire hydrant positions in accordance with SNZ PAS 4509 | Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings. Mark fire hydrant positions in accordance with SNZ PAS 4509 | PS 22.7.3 a | Visual Inspection / Wastewater line record | Every Line | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
8.6 | Drill Report | Drill report to be submitted | Drill report to be submitted | PS 21.6.6 | Report | Every Line | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
8.7 | Settlement monitoring and ground deformation (Baseline measurements) | Topo survey completed before and after drill shot | Topo survey completed before and after drill shot | PS 21.6.6 | Survey data | Every 6m | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
8.8 | Cement Grout - Annulus | The sleeve annulus are to be cement grouted after installation to prevent settlement. | The grouting mix is to be: 1. 1:1 Sand/cement ratio 1 : 1 2. Water/Cement ratio 1 : 0.67 by weight | PS 22.5.8b | Visual inspection, lab report | Every Grout | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
9 | CONSTRUCTION - WASTEWATER Manhole installation
9.1 | Foundation Compliance | On Granular or Cohesive Material | Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa | Appendix V PS 21.7.2 Table 21:11 | Shear vane or Scala test result | 1 Test/Manhole | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
9.2 | Undercut approval | On Subgrade | Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material. | PS 21.6.5 Table 21.5 | Lab Test Report | If Undercut required | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
9.3 | Undercut Backfill Compliance AP65 | On Granular Material | Average 95% MDD, min >92% OR Clegg 25% CIV | Appendix XVIII | Lab Test Report | 1 Test per Undercut | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE |  |  |  | acceptance criteria is not wrong, however spec reference refers to pumice sand not AP65. Please refer to Appn. XVIII | Changed to appendix XVIII from PS 16.5.11
9.4 | Bedding Compaction Testing AP65 | On Granular Material | Average 95% MDD, min >92% OR Clegg 25% CIV | Appendix XVIII PS- 21.6.11 | Lab Test Report | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE |  |  |  | acceptance criteria is not wrong, however spec reference refers to pumice sand not AP65. Please refer to Appn. XVIII | Changed to appendix XVIII from PS 16.5.12
9.5 | Survey | Inspection of Structure | Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm. | PS- 21.7.6 | Survey Data | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SV
9.6 | Man Hole joints inspection | Inspection of joints | Right joint type used, no visual leak or breakage | PS 22.7.10 | Visual inspection | 1 Test/Manhole | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
9.7 | Inspection | Inspection of Structure | Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure. | PS- 21.6.11 | Manhole/Catchpit Record | 1 Checksheet per manhole/catchpit | I Formal inspection activity to be undertaken and recorded. | SE
9.8 | Plumb | The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise. | The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise. | PS-22.7.10 | Survey Data | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SV
9.9 | Step Rungs | Step rungs evenly spaced at nominal 300mm vertical intervals | Lowest rung more than 450mm above floor highest rung not more than 600mm below the top surface of MH cover | PS-22.7.11 | Visual inspection | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
9.1 | Manhole frame and covers | Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame. | Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame. | PS 22.7.10 | Visual inspection | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
9.11 | Concrete Formwork - surveyor to check | Equivalent to check the position of the formwork | +\- 100mm of design | Project Specifications 27.4.5 (b) NZS 3109:1997 | Pre-pour Check Sheet | 1 Set Every 20m Centres 1 set = 5 tests | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SUP
9.12 | Concrete Formwork - surveyor to check | Equivalent to check finished height of framework | +\- 10mm of design | Project Specifications 27.4.5 (b) NZS 3109:1998 | Pre-pour Check Sheet | 1 Set Every 20m Centres 1 set = 5 tests | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SUP
9.13 | Pre-pour inspection | Pre-pour inspection of manhole before ballast | Stable form work, ready for pour | Visual Inspection | Visual inspection | Pre each manhole ballasts installation | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
9.14 | Manhole Ballast (concrete & reinforcing steel) | Additional manhole ballast. | All Concrete to be 25MPa at 28 days. Minimum cover to steel = 50mm. Reinforcing steel to be grade 500E and to comply with AS/NZS 4671. | IFC Drawing Sheet WST 0321 NZS 3109 5.6.3(B). AS/NZS 4671 PS Table 22.4 specific manhole requirements | Visual inspection | Per manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
9.15 | Sidefill Compaction Testing | From the bedding layer to the overlay layer of pipe. | AP20/GAP20 Testing to be completed on maximum 200mm lifts of backfill - 85% MDD AP20/19mm chip | PS- Table 21.12 | Lab Test Report | 4 Density test per layer at Quarter Points around the Structure. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE |  |  |  | acceptance criteria is not wrong, however spec reference refers to pumice sand not AP65. Please refer to Appn. XVIII | Changed from 16.5.12 to appendix XVIII
9.16 | Backfill Compaction Testing | From Overlay layer to the subgrade layer | AP65 Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal. AP65-Clegg 28%CIV | Appendix XVIII | Lab Test Report | 4 Density test per layer at Quarter Points around the Structure. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
10 | CONSTRUCTION - WASTEWATER PIPELINE - Inspection
10.1 | Pipe Inspection | Inspection of Drainage line | Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness | Internal | Wastewater line record | Continious 1 per Line | I Formal inspection activity to be undertaken and recorded. | SE
11 | CONSTRUCTION - WASTEWATER PIPELINE - Backfill
11.1 | Emebment Zone - (Side Haunch Overlay ) | Granular Sand backfill Compacted in 200mm Layers. NDM/CleggTesting to be completed on maximum 200mm lifts of overlays . NDM BS to be Carried Out | in 200mm layers. More than 85% of MDD. | IFC Drawing 0320-1 | Lab Report / Wastewater line record | One test per 20m evenly spaced intervals. 200mm lift | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
11.2 | Pipe Markers | Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings. Mark fire hydrant positions in accordance with SNZ PAS 4509 | AS Per Drawings. | PS 22.7.3 a | Visual Inspection / Wastewater line record | Every Line | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
11.3 | Backfill Compaction Testing | Backfill Compacted in 200mm Layers. NDM Testing to be completed on maximum 200mm lifts of backfill. | GAP65/AP65or site won material Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill. 95% NDM on Shared and Carriageway. OR 25% CIV For site won: Shear Vane min 125kPa | PS- 22.13.5 NDM Standard 25832 NZS 4402 Test 4.1.3 IFC Drawing 0320-1 PS - 16.5.5 | Lab Report / Wastewater line record | As per WW Specification. One test per 20m evenly spaced intervals. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE |  |  |  | Unsure where shear vane testing results came from. These should be as per the earthworks specs (125kPa) | For site won min 125kPa
12 | CONSTRUCTION - WASTEWATER PIPELINE TESTING
12.1 | Pressure Acceptance Testing | Backfill/cover with embedment before testing End caps in place, provision for filling the pipeline and bleeding air. | Wastewater Rising Main Pipelines – 800kPa Ensure the STP is not more than 25% above the rated pressure of any pipeline component. | PS 22.7.12 TCC IDC IT-6 | Test Report Pressure Log in.csv or .xlsx format | All Pipeline All valves | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
12.2 | Constant Pressure Test | Backfill/cover with embedment before testing, plan for where water will be diverted or sent to | There is no failure of any pipe, fitting or other pipeline component. There is no visible leakage at pipe joints or other fittings. The make-up water volume does not exceed the maximum allowable quantity as calculated. Q ≤ (0.14 x L x D x H). | PS 22.7.15 TCC IDC IT-6 | Test Report Pressure Log in.csv or .xlsx format | All Pipeline | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
12.3 | Pressure Rebound Test | Backfill/cover with embedment before testing, plan for where water will be diverted or sent to | There is no failure of any pipe, fitting, or other pipeline component, and There is no visible leakage at any joint or fitting. The volume of water bled off (ΔV) is less than the calculated ΔV(max allowable air), and The pressure has not dropped below the rebound peak within 30 minutes, or The test has been extended to 90 minutes and the pressure has not dropped more than 20 kPa below the rebound peak value after 60 minutes. | PS 22.7.16 TCC IDC IT-6 | Test Report Pressure Log in.csv or .xlsx format | All Pipeline | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
13 | CONSTRUCTION ACTIVITY - PAVEMENT REINSTATEMENT
13.1 | Sub-basecourse layer | AP65-1 is to match the exisiting granular pavement depth. | Compacted in 200mm lifts. 95% NDM on Shared and Carriageway. OR 35% CIV | PS 22.13.5 TCC T460 TNZ B/02 section7.6 | NDM/Clegg test result | Every 50 metres | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE/ENG
13.2 | Basecourse layer | AP40 (M/4) 150mm | Compacted in 200mm lifts. 95% NDM on Shared and Carriageway. OR 35% CIV | PS 22.13.5 TCC T460 TNZ B/02 section7.6 | Compacted in 200mm lifts. 95% NDM on Shared and Carriageway. OR 35% CIV | Every 50 metres | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE/ENG
13.3 | Surfacing | Asphalt to match type, texture and thickness of existing surfacing. Once asphlat type is confirmed then will confirm with engineer what testing on the surfacing will need to be done. | In accordance with TCC drawing T460 | PS 22.13.4-5 TCC T460 | Visual Inspection/Engineer Approval/NDM | Every 50 metres | I Formal inspection activity to be undertaken and recorded. | SE
14 | CONSTRUCTION ACTIVITY - COMMUNICATION DUCT INSTALLATION
14.2 | Bedding | Duct bedding to be on top of the wastewater pipeline cover. (refer to CWP section 5.7 for diagram) | Clean Imported Sand or SAP 7 to be placed 50mm minimum thickness (compacted) over the wastewater pipeline | PS 25.13.2 g) | Checklist | Each Cable | M | SE
14.3 | Installation of Ducts | Laying ducts in same trench as wastewater | Must have 50 mm bedding material between the two ducts. | PS 25.13.7 b) iii | Checklist | Each Cable | M | SE
14.4 | Draw Wires | A draw wire shall be intalled in all ducts and within all sub-ducts to facilitate the hauling-in of cable after the completion of the ducting. | Pigmented, stranded polypropylene or equivalent rot-proof material draw wire of 5kN breaking load. ≥20 years design life. The ends of draw wires shall be made fast within the pits and be secured to the duct plugs. Blue colour wire | PS 25.13.7 e) ii to iv | Checklist | Each Cable | M | SE
14.5 | Caps | All duct ends shall be capped | Capped ducts | PS 25.13.7 e) v | Checklist | Each Cable | M | SE
14.6 | Tracer Wire and marker tape | Warning tape to be placed above services. | Warning Tape to be placed no more than 300mm above the topmost duct | PS 25.13.7 b) iii & f) | Checklist | Each Cable | M | SE
14.7 | Overlay | 150 mm minimum sand placed on top of duct. No mechanical compaction will carry out till 300mm from top of duct. | 100 mm minimum sand placed on top of duct. | PS 25.13.7 b) ii | Checklist | Each Cable | M | SE
15 | CONSTRUCTION ACTIVITY - COMMUNICATION PIT INSTALLATION
15.1 | Pit Installation Location | Locations shall be avoided where running water can flow over the lid or where mud and debris can fall or be washed onto the lid . Confirm location on site with Engineer. | Pit lid and concrete apron shall be flush with ground level in grass, concrete or asphalt areas. When pit is located on a slope of 10 to 30 degrees, the lid shall be flush with ground on the upper side. When slope is greater than 30 degrees, the lid shall be up to 100mm above the ground level on the upper side. | PS 25.13.8 a) i and ii | Checklist | Each Pit Location | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
15.2 | Pit Installation Bedding | Bedding with 150mm compacted GAP20 hard-fill coverd with 20mm compacted sand. Pits shall be carefully lifted into place and lined up with the ducts to penetrate the chamber. | 150mm compacted GAP20 hard-fill covered with 20mm of compacted sand | PS 25.13.8 d) | Checklist | Each Pit Location | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
15.3 | Pit Installation Sidefill concrete | Plastic pits shall be cast into the ground with 150mm concrete surround | Plactic pits shall be cast into the ground with 150mm concrete surround | PS 25.13.8 d) | Checklist | Each Pit Location | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
15.4 | Pit Installation Backfilling | Backfill and compact the ground around concrete pits. Extra care to be taken to avoid damaging the ducts in 200mm layers of GAP 65. | Min 92% compaction rate and Average of 95%. | PS 25.13.10 a) modified | Checklist | Each Pit Location | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
15.5 | Pit Installation Concrete | Top 300mm of pit shall be concreted around with a with of 150mm with a 20MpA concrete. | 20 mPa | PS 25.13.8 d) iv. | Concrete Dockets | Each Pit Location | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
15.6 | Pit Installation Clean up | Clean out all pit after completion of the work | Pit are free of dirty, mud,water and foreign materials | PS 25.13.8 e) | Checklist | Each Pit Location | M | SE
15.7 | Survey As Built | As Built every ducts joint before backfill | Completed as per drawings | Standard Practise | Survey Asbulit | On going | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
16 | POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
16.1 | Survey As-Builts | Quality check on the pipeline and structure based on the tolerances in RITS. | Meets spec as per drawings and capture any NCR or change to design. | Project Specifications | Red pen markup only | Post works completion of a lot | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE