## ITP-xxx
|  |  | Inspection and Test Plan - Control and Supervision of the Works | [7 empty] | FHC-ITP-001
[11 empty] | Revision : 0 | Date : 25/09/2025
Client: |  | Bass Coast Shire Council |  | Construction Process: |  | Prepared by: |  | Reviewed by : |  |  | Approved by :
Project: |  | Cowes Streetscape |  | Watermain Installation Works |  | Name: Crystal D'Mello |  | Name: Oliver Brooks |  |  | Name: Shaun Kent
Job No: |  | 8B6200 |  | Specifications: MRWA, WSA
|  |  |  | Structure / Component: Water Main |  | Signed : |  | Signed : |  |  | Signed :
|  |  |  | Location: Cowes |  | Date : 25/09/25 |  | Date : |  |  | Date :
Lot No: |  |  | Lot Details: | [5 empty] | Lot Size/ Quantity:
Item | Task/Activity Description |  | Inspection / Controls and Verification Detail |  |  |  |  | HP/ WP/ AP/ IP/ TP/ SCP | Responsibility | Checked by:
No. |  |  | Frequency | Acceptance Criteria | Reference Documents | Inspection / Test Method | Record of conformity |  | Project Engineer Site Engineer Superintendent Surveyor Foreman | Client | Fulton Hogan | FH's Sub-contractor | Date
1 | Preliminary Works
1.1 | Check for correct documentation |  | Prior to commencing any activity | Ensure that the current revision drawings are being used and have been issued as IFC. | Drawings and drawing registers | Verify | ITP Signed | HP* | Site Engineer | N/A
1.2 | Subcontractor Accreditation |  | Prior to commencing any activity | Ensure that the Subcontractor is accredited with Westernport Water | Subcontractor Accreditation | Verify | ITP Signed | HP* | Site Engineer | N/A
1.3 | Permits |  | Prior to commencing any activity | Obtain all applicable permits (including required Westernport Water approvals) | Permits and Approvals | Verify | ITP Signed | HP* | Site Engineer | N/A
1.4 | Implementation of all measures and controls |  | Prior to commencing any activity | All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP | PSP, EMP, TMP, JSEA, SWMS, WP | Visual Inspection | ITP Signed | HP* | Site Engineer | N/A
1.5 | Material Inspection - Pipes & Fittings |  | Prior to commencing any activity | Use only products and materials approved and catalogued by Westernport Water Works. Pipe and fittings to be inspected for defects/damage and cross referenced with delivery docket for each delivery. Westernport Region Water Corporation Representative to inspect pipes and fittings prior to placement. | WSA-03-12.2 | Delivery Dockets | ITP Signed | HP | Site Engineer/ Foreman/ WPW | N/A
1.6 | Material Inspection - Quarry Material |  | Prior to commencing any activity | Quarry materials to be cross referenced with delivery docket and must adhere to MRWA standards | MRWA 04-03.1 | Verfiy Delivery Dockets | ITP Signed | HP* | Site Engineer | N/A
2 | Construction Works
2.1 | Excavation Permit |  | Prior to any excavation | An excavation permit must be issued prior to any excavation commencing. Plant and equipment shall be appropriate for the task. Excavation operations shall not disturb areas outside the limit of excavation | Excavation permit | Verify | ITP Signed | HP* | Site Engineer/ Foreman | N/A
2.2 | Set out |  | Prior to any excavation | Ensure set out is consistent with IFC design. | IFC Drawings | Verify | ITP Signed | HP* | Site Engineer/ Foreman | N/A
2.3 | Excavation/Trenching |  | Each Trench | DN180PE pipe to be installed, trench width to be excavated as per MRWA-W-202 Table 202-A When excavating trenches in excess of 1.5m in depth, worksafe notification must be lodged prior to commencement of works and on or more of the highlighted measures must be adopted to prevent ground collapse Mandatory monitoring of ground conditions following inclement weather NDD to be utilised where location of assets is not confirmed or when manual or mechanical excavation is not permitted | MRWA-W-202 (Table 202-A, Figure 202-B) Worksafe Excavation Compliance Code Edition 2, Dec 2019 | Visual Inspection | ITP Signed | WP | Site Engineer/ Foreman/ Superintendent
2.4 | HDD (Horizontal Directional Drilling) (Trenchless) |  | Each Line | HDD to be utilised in the construction of the approximately 100m section on the northern side of "The Esplanade" to reduce environmental impact and to minimise disturbance to areas adjacent to the area of works (WSA-03-2.10) All HDD works to be completed by nominated Fulton Hogan subcontrator Maintain the minimum clearances between exisiting services and new main | WSA-03-2.10 WSA-03 (Table 5.5 Clearances between watermains and underground services) | Visual Inspection | ITP Signed | WP | Site Engineer/ Foreman | N/A
2.5 | Place bedding material & compact |  | Each Trench | Place uniform layer of 100mm-200mm of embedment material along base of trench. | WSA PS 360 WSA PS 361 | Delivery Dockets | ITP Signed | WP | Site Engineer/ Foreman | N/A
2.6 | Pipe Installation |  | Each Line | In-trench welding to be completed by certified PE welder. Only butt welding is permitted. Samples for destructive weld testing to be completed and sent off for testing. Install pipe and fittings as per the design drawings. At the end of shift ensure that a temporary seal is installed to prevent the ingress of debris. DI fittings to be wrapped and taped to limit effects of corrosion Place embedment material around pipe ensuring minimum 450mm of cover is acheived Ensure detectable marker tape is installed above first layer above embedment material in open cut areas. In sections where HDD is utilised, a 2mm diameter grade 316 stainless Steel tracer wire is to be affixed to the pipe (WSA-03-15.12.3) Following construction, a visual inspection is to be completed. | MRWA-W-202 (Table 202-A, Figure 202-B) Figure 4.1, WSA-03-4.3.6 WSA-03-15 WSA-03-4.2.6 PIPA - POP014, POP003, POP004 Design Drawings WSA-03-15.12.3 | Visual Inspection | ITP Signed | WP | Site Engineer/ Foreman | N/A
2.7 | Decomissioning of main |  | Each Line | Disused AC pipes need not be removed provided they do not interfere with the operation or maintenance of adjacent services. Cutting of collars and pipes should be completed by wheeled pipe cutter and/or hammer and chisel while the collar or pipe is wetted. All cutting works on AC main to be completed by authorised subcontractor. Subcontractor to safely dispose of all asbestos produced as part of the cutting works as per government legislation. | WSA-03-11.5.2 | Visual Inspection | ITP Signed | WP | Site Engineer/ Foreman | N/A
2.8 | Backfill |  | Each Trench | Select fill (AS2566.2-2002) or Ordinary fill (AS2566.2-2002) to be used to backfill trench in non trafficable areas WSA approved materials to be used as per Table 203-B, MRWA-W-203 20mm CL3 wet mixed crushed rock or 20mm CL4 crushed rock to be used in trafficable areas, backfill material to be compacted in layers to achieve required density. Compact to 95% modified. When using hand held or walk behind compactor, avoid compaction within 300mm of top of pipe. For larger compaction devices, avoid compaction within 800mm of top of pipe. | MRWA 04-03.1 MRWA-W-202 (Table 202-A, Figure 202-B) MRWA-W-201 (Table 201-A and Table 201-B) | Compaction Test | ITP Signed | TP | Site Engineer/ Foreman/ Superintendent
2.9 | Fittings |  | Each Line | All fittings to be inspected for defects/damage and cross referenced with delivery docket for each delivery All fittings to be torqued as per MRWA spec and manufacturer standards | MRWA-W-306B (Figure 306B -A) MRWA-W-306B (Table 306B-A ,Table 306B-B, Table 306B-C) WSA-03-12.2 | Visual Inspection | ITP Signed | IP | Site Engineer/ Foreman | N/A
3 | Testing & Reinstatement
3.1 | Asset Recording |  | Each Lot | Asset recording to be completed by nominated Fulton Hogan subcontractor | N/A | As Built | ITP Signed | SCP | Licensed Surveyor | N/A
3.2 | Swabbing |  | Each Lot | Testing request for swabbing to be lodged with consultant prior to commencement Swabbing to be completed following pipelines construction to ensure internal cleanliness of pipe prior to pre-testing,pressure testing, chlorination, water quality and connections in preperation for commisioning Slightly oversized foam swabs to be inserted into main during construction at connection points Swabbing procedure to follow steps set out in WSA-03-18.3 | WSA-03-18 | Visual Inspection | ITP Signed | HP | Site Engineer/ Subcontractor/ WPW | N/A
3.3 | Pressure Test (pre test) |  | Each Lot | Fulton Hogan to complete pre-test to ensure functionality of constructed main | N/A | Visual Inspection | ITP Signed | WP | Site Engineer/ Foreman/ Subcontractor | N/A
3.4 | Pressure Test (Official) |  | Each Lot | Testing form for pressure test to be lodged with consultant prior to commencement of works Pressure test PE pipelines in accordance with clause MRWA 19.4.1.1 | WSA-03-19.4 | Visual Inspection | ITP Signed | HP | Site Engineer/ Subcontractor/ WPW | N/A
3.5 | Water Quality |  | Each Lot | WQ (Water Quality) to be completed by nominated Fulton Hogan subcontractor, all works to be completed as per WSA and MRWA standards WQ results to be sent to consultant once received | WSA-03, Annexure 1 (Table 1.2) MRWA Specification 04-02-2.1 | Water Quality Report | ITP Signed | HP | Site Engineer/ Subcontractor/ WPW | N/A
3.6 | Connection |  | Each Lot | Connection to exisiting AC (Asbestos Cement) main to be completed via the use of specialised SOC-FL or mechanical coupling Cut in works on AC (Asbestos Cement) main to be completed by authorised subcontractor, Fulton Hogan team to assist with installation of fittings to facilitate connection Fulton Hogan to notify consultant of shutdown date 2 weeks following recieval of successful WQ results Consultant to book shutdown as per dates indicated by Fulton Hogan | WSA-03-5.9 WSA-03-11.8 | Visual Inspection | ITP Signed | HP | Site Engineer/ Subcontractor/ WPW | N/A
3.7 | Backfilling / Site Restoration |  | At completion of each Separable Portion | The site shall be reinstated/restored to its pre-existing condition as per WSA-03-23 Areas of excavation will be backfilled to exisitng surface level with valve and hydrant covers to be flush with the finished surface level Grassed areas impacted as part of the construction process will be reinstated to an original condition | WSA-03-23.1 WSA-03-23.4 | Visual Inspection | ITP Signed | WP | Site Engineer/ Foreman | N/A
Final Inspection
The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
| Print Name: |  | Position: |  | Signature: |  |  |  |  | Date: / /
Legend
HP | Hold Point | Work shall not proceed past the HP until released by the Superintendent |  |  | IP | Inspection point |  | Formal Inspection to be done and recorded
HP* | FH Hold Point | Work shall not proceed past the HP* until released by FH |  |  | TP | Test Point |  | Product compliance test to be undertaken and recorded/reported
WP | Witness Point | An inspection which must be witnessed by the Superintendent |  |  | SCP | Survey conformance point |  | A qualified surveyor to check product/section/structure and report
AP | Approval Point | Written or verbal approval given by the Superintendent