## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | FHC-ITP-001 - Watermain Installation | itp |  |  |  |  | FHC-ITP-001 - Watermain Installation Rev0
section | Preliminary Works
checkpoint | 1.1 Check for correct documentation
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: Ensure that the current revision drawings are being used and have been issued as IFC.
label | REFERENCE DOCUMENTS: Drawings and drawing registers
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: ITP Signed
label | HP*
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | 1.2 Subcontractor Accreditation
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: Ensure that the Subcontractor is accredited with Westernport Water
label | REFERENCE DOCUMENTS: Subcontractor Accreditation
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: ITP Signed
label | HP*
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | 1.3 Permits
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: Obtain all applicable permits (including required Westernport Water approvals)
label | REFERENCE DOCUMENTS: Permits and Approvals
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: ITP Signed
label | HP*
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | 1.4 Implementation of all measures and controls
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
label | REFERENCE DOCUMENTS: PSP, EMP, TMP, JSEA, SWMS, WP
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | HP*
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | 1.5 Material Inspection - Pipes & Fittings
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: Use only products and materials approved and catalogued by Westernport Water Works. Pipe and fittings to be inspected for defects/damage and cross referenced with delivery docket for each delivery.
label | ○ Westernport Region Water Corporation Representative to inspect pipes and fittings prior to placement.
label | REFERENCE DOCUMENTS: WSA-03-12.2
label | INSPECTION/TEST METHOD: Delivery Dockets
label | RECORD OF CONFORMITY: ITP Signed
label | HP
label | RESPONSIBILITY: Site Engineer/Foreman/WPW
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.6 Material Inspection - Quarry Material
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: Quarry materials to be cross referenced with delivery docket and must adhere to MRWA standards
label | REFERENCE DOCUMENTS: MRWA 04-03.1
label | INSPECTION/TEST METHOD: Verify, Delivery Dockets
label | RECORD OF CONFORMITY: ITP Signed
label | HP*
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
section | Construction Works
checkpoint | 2.1 Excavation Permit
label | FREQUENCY: Prior to any excavation
label | ACCEPTANCE CRITERIA: An excavation permit must be issued prior to any excavation commencing.
label | ○ Plant and equipment shall be appropriate for the task.
label | ○ Excavation operations shall not disturb areas outside the limit of excavation
label | REFERENCE DOCUMENTS: Excavation permit
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: ITP Signed
label | HP*
label | RESPONSIBILITY: Site Engineer/ Foreman
textbox | Date Completed:
checkpoint | 2.2 Set out
label | FREQUENCY: Prior to any excavation
label | ACCEPTANCE CRITERIA: Ensure set out is consistent with IFC design.
label | REFERENCE DOCUMENTS: IFC Drawings
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: ITP Signed
label | HP*
label | RESPONSIBILITY: Site Engineer/ Foreman
textbox | Date Completed:
checkpoint | 2.3 Excavation/Trenching
label | FREQUENCY: Each Trench
label | ACCEPTANCE CRITERIA: DN180PE pipe to be installed, trench width to be excavated as per MRWA-W-202 Table 202-A
label | ○ When excavating trenches in excess of 1.5m in depth, worksafe notification must be lodged prior to commencement of works and on or more of the highlighted measures must be adopted to prevent ground collapse
label | ○ Mandatory monitoring of ground conditions following inclement weather
label | ○ NDD to be utilised where location of assets is not confirmed or when manual or mechanical excavation is not permitted
label | REFERENCE DOCUMENTS: MRWA-W-202 (Table 202-A, Figure 202-B), Worksafe Excavation Compliance Code Edition 2, Dec 2019
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | WP
label | RESPONSIBILITY: Site Engineer/Foreman/ Superintendent
textbox | Date Completed:
checkpoint | 2.4 HDD (Horizontal Directional Drilling) (Trenchless)
label | FREQUENCY: Each Line
label | ACCEPTANCE CRITERIA: HDD to be utilised in the construction of the approximately 100m section on the northern side of "The Esplanade" to reduce environmental impact and to minimise disturbance to areas adjacent to the area of works (WSA-03-2.10)
label | ○ All HDD works to be completed by nominated Fulton Hogan subcontrator
label | ○ Maintain the minimum clearances between exisiting services and new main
label | REFERENCE DOCUMENTS: WSA-03-2.10, WSA-03 (Table 5.5 Clearances between watermains and underground services)
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | WP
label | RESPONSIBILITY: Site Engineer/ Foreman
textbox | Date Completed:
checkpoint | 2.5 Place bedding material & compact
label | FREQUENCY: Each Trench
label | ACCEPTANCE CRITERIA: Place uniform layer of 100mm-200mm of embedment material along base of trench.
label | REFERENCE DOCUMENTS: WSA PS 360, WSA PS 361
label | INSPECTION/TEST METHOD: Delivery Dockets
label | RECORD OF CONFORMITY: ITP Signed
label | WP
label | RESPONSIBILITY: Site Engineer/ Foreman
textbox | Date Completed:
checkpoint | 2.6 Pipe Installation
label | FREQUENCY: Each Line
label | ACCEPTANCE CRITERIA: In-trench welding to be completed by certified PE welder. Only butt welding is permitted. Samples for destructive weld testing to be completed and sent off for testing.
label | ○ Install pipe and fittings as per the design drawings. At the end of shift ensure that a temporary seal is installed to prevent the ingress of debris. DI fittings to be wrapped and taped to limit effects of corrosion
label | ○ Place embedment material around pipe ensuring minimum 450mm of cover is acheived
label | ○ Ensure detectable marker tape is installed above first layer above embedment material in open cut areas. In sections where HDD is utilised, a 2mm diameter grade 316 stainless Steel tracer wire is to be affixed to the pipe (WSA-03-15.12.3)
label | ○ Following construction, a visual inspection is to be completed.
label | REFERENCE DOCUMENTS: MRWA-W-202 (Table 202-A, Figure 202-B), Figure 4.1, WSA-03-4.3.6, WSA-03-15, WSA-03-4.2.6, PIPA - POP014, POP003, POP004, Design Drawings WSA-03-15.12.3
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | WP
label | RESPONSIBILITY: Site Engineer/ Foreman
textbox | Date Completed:
checkpoint | 2.7 Decomissioning of main
label | FREQUENCY: Each Line
label | ACCEPTANCE CRITERIA: Disused AC pipes need not be removed provided they do not interfere with the operation or maintenance of adjacent services.
label | ○ Cutting of collars and pipes should be completed by wheeled pipe cutter and/or hammer and chisel while the collar or pipe is wetted.
label | ○ All cutting works on AC main to be completed by authorised subcontractor.
label | ○ Subcontractor to safely dispose of all asbestos produced as part of the cutting works as per government legislation.
label | REFERENCE DOCUMENTS: WSA-03-11.5.2
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | WP
label | RESPONSIBILITY: Site Engineer/ Foreman
textbox | Date Completed:
checkpoint | 2.8 Backfill
label | FREQUENCY: Each Trench
label | ACCEPTANCE CRITERIA: Select fill (AS2566.2-2002) or Ordinary fill (AS2566.2-2002) to be used to backfill trench in non trafficable areas
label | ○ WSA approved materials to be used as per Table 203-B, MRWA-W-203
label | ○ 20mm CL3 wet mixed crushed rock or 20mm CL4 crushed rock to be used in trafficable areas, backfill material to be compacted in layers to achieve required density. Compact to 95% modified.
label | ○ When using hand held or walk behind compactor, avoid compaction within 300mm of top of pipe. For larger compaction devices, avoid compaction within 800mm of top of pipe.
label | REFERENCE DOCUMENTS: MRWA 04-03.1, MRWA-W-202 (Table 202-A, Figure 202-B), MRWA-W-201 (Table 201-A and Table 201-B)
label | INSPECTION/TEST METHOD: Compaction Test
label | RECORD OF CONFORMITY: ITP Signed
label | TP
label | RESPONSIBILITY: Site Engineer/Foreman/ Superintendent
textbox | Date Completed:
checkpoint | 2.9 Fittings
label | FREQUENCY: Each Line
label | ACCEPTANCE CRITERIA: All fittings to be inspected for defects/damage and cross referenced with delivery docket for each delivery
label | ○ All fittings to be torqued as per MRWA spec and manufacturer standards
label | REFERENCE DOCUMENTS: MRWA-W-306B (Figure 306B -A), MRWA-W-306B (Table 306B-A ,Table 306B-B, Table 306B-C), WSA-03-12.2
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | IP
label | RESPONSIBILITY: Site Engineer/ Foreman
textbox | Date Completed:
section | Testing & Reinstatement
checkpoint | 3.1 Asset Recording
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Asset recording to be completed by nominated Fulton Hogan subcontractor
label | REFERENCE DOCUMENTS: N/A
label | INSPECTION/TEST METHOD: As Built
label | RECORD OF CONFORMITY: ITP Signed
label | SCP
label | RESPONSIBILITY: Licensed Surveyor
textbox | Date Completed:
checkpoint | 3.2 Swabbing
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Testing request for swabbing to be lodged with consultant prior to commencement
label | ○ Swabbing to be completed following pipelines construction to ensure internal cleanliness of pipe prior to pre-testing,pressure testing, chlorination, water quality and connections in preperation for commisioning
label | ○ Slightly oversized foam swabs to be inserted into main during construction at connection points
label | ○ Swabbing procedure to follow steps set out in WSA-03-18.3
label | REFERENCE DOCUMENTS: WSA-03-18
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | HP
label | RESPONSIBILITY: Site Engineer/Subcontractor/WPW
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 Pressure Test (pre test)
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Fulton Hogan to complete pre-test to ensure functionality of constructed main
label | REFERENCE DOCUMENTS: N/A
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | WP
label | RESPONSIBILITY: Site Engineer/Foreman/Subcontractor
textbox | Date Completed:
checkpoint | 3.4 Pressure Test (Official)
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Testing form for pressure test to be lodged with consultant prior to commencement of works
label | ○ Pressure test PE pipelines in accordance with clause MRWA 19.4.1.1
label | REFERENCE DOCUMENTS: WSA-03-19.4
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | HP
label | RESPONSIBILITY: Site Engineer/Subcontractor/WPW
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.5 Water Quality
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: WQ (Water Quality) to be completed by nominated Fulton Hogan subcontractor, all works to be completed as per WSA and MRWA standards
label | ○ WQ results to be sent to consultant once received
label | REFERENCE DOCUMENTS: WSA-03, Annexure 1 (Table 1.2), MRWA Specification 04-02-2.1
label | INSPECTION/TEST METHOD: Water Quality Report
label | RECORD OF CONFORMITY: ITP Signed
label | HP
label | RESPONSIBILITY: Site Engineer/Subcontractor/WPW
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.6 Connection
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Connection to exisiting AC (Asbestos Cement) main to be completed via the use of specialised SOC-FL or mechanical coupling
label | ○ Cut in works on AC (Asbestos Cement) main to be completed by authorised subcontractor, Fulton Hogan team to assist with installation of fittings to facilitate connection
label | ○ Fulton Hogan to notify consultant of shutdown date 2 weeks following recieval of successful WQ results
label | ○ Consultant to book shutdown as per dates indicated by Fulton Hogan
label | REFERENCE DOCUMENTS: WSA-03-5.9, WSA-03-11.8
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | HP
label | RESPONSIBILITY: Site Engineer/Subcontractor/WPW
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.7 Backfilling / Site Restoration
label | FREQUENCY: At completion of each Separable Portion
label | ACCEPTANCE CRITERIA: The site shall be reinstated/restored to its pre-existing condition as per WSA-03-23
label | ○ Areas of excavation will be backfilled to exisitng surface level with valve and hydrant covers to be flush with the finished surface level
label | ○ Grassed areas impacted as part of the construction process will be reinstated to an original condition
label | REFERENCE DOCUMENTS: WSA-03-23.1, WSA-03-23.4
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | WP
label | RESPONSIBILITY: Site Engineer/ Foreman
textbox | Date Completed:
checkpoint | Final Inspection
note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
textbox | Date:
checklist | FHC-ITP-008 - Stormwater Drainage | itp |  |  |  |  | FHC-ITP-008 - Stormwater Drainage Rev1
section | Preliminary Works
checkpoint | 1.1 Check for correct documentation
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: Ensure that all employees and subcontractors are:
label | — using the correct and complete set of drawings
label | — all drawings are the latest revision
label | REFERENCE DOCUMENTS: Drawings and drawing registers
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed off
label | HP*
label | RESPONSIBILITY: Site Engineer / Site Foreman
textbox | Date Completed:
checkpoint | 1.2 Implementation of all measures and controls
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
label | REFERENCE DOCUMENTS: PSP, EMP, TMP, JSEA, SWMS, WP
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: This ITP signed off
label | HP*
label | RESPONSIBILITY: Site Engineer / Site Foreman
textbox | Date Completed:
checkpoint | 1.3 Material Approval
label | FREQUENCY: Prior to Placement
label | ACCEPTANCE CRITERIA: Material intended for use is to be submitted to the client prior to placement to verify it conforms to required specifications.
label | REFERENCE DOCUMENTS: Material specification sheets
label | INSPECTION/TEST METHOD: Verfiy
label | RECORD OF CONFORMITY: Teambinder Acceptance
label | HP*
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | 1.4 Precast Materials acceptance
label | FREQUENCY: Each Delivery
label | ACCEPTANCE CRITERIA: Precast reinforced concrete pipes shall be accepted on the basis of full compliance with the requirements of this section and AS/NZS 4058.
label | REFERENCE DOCUMENTS: Cl. 701.05e
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: This ITP signed Receival and Inspection Checklist
label | IP
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | 1.5 Precast Pipe & Culvert Compliance
label | FREQUENCY: Prior to Commencing
label | ACCEPTANCE CRITERIA: Precast Reinforced Concrete Box Culverts to comply with requirements of VicRoads Section 619.
label | ○ Precast Reinforced Concrete (Portland) Pipes shall comply with requirements of AS 4058
label | REFERENCE DOCUMENTS: VicRoads Spec. Cl.619, Cl. 701.04, Cl. 701.05(a), AS4058, AS4680
label | INSPECTION/TEST METHOD: Document review & Site inspection
label | RECORD OF CONFORMITY: Receival & Inspection Checklist, Manufacturer cetificate or accreditation
label | IP
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | 1.6 Precast Drainage Pit Compliance
label | FREQUENCY: Prior to Commencing
label | ACCEPTANCE CRITERIA: All concrete shall be manufactured to the concrete mix design registered by VicRoads and comply with the requirements of Section 610.
label | REFERENCE DOCUMENTS: VicRoads Spec. Cl.610, Cl. 705.04, AS5100
label | INSPECTION/TEST METHOD: Document Review
label | RECORD OF CONFORMITY: Receival & Inspection Checklist, Manufacturer cetificate or accreditation
label | IP
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | 1.7 Bedding material classification
label | FREQUENCY: Prior to start
label | ACCEPTANCE CRITERIA: Materials used for bedding and selected backfill shall be free from perishable matter and lumps and shall conform with the requirements of Table 701.091 and Table 701.092.
label | REFERENCE DOCUMENTS: 701.09(d), 701.091, 701.092
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: Test Reports from supplier
label | TP
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | 1.8 Backfill material Classification
label | FREQUENCY: Prior to start
label | ACCEPTANCE CRITERIA: Ordinary backfill shall be free from perishable matter and shall conform with the requirements of Table 701.091.
label | REFERENCE DOCUMENTS: 701.09(d), 701.091
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: Test Reports from supplier
label | TP
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | 1.9 Mortar material classification
label | FREQUENCY: Prior to start
label | ACCEPTANCE CRITERIA: Cementituous grouts shall be minimum Type C class dual shinkage compensating, with a minimum 28 day compressive strength of 40 Mpa
label | REFERENCE DOCUMENTS: 610.33
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: Test Reports from supplier
label | TP
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
section | Construction Works
checkpoint | 2.1 Excavation Permit
label | FREQUENCY: Each lot
label | ACCEPTANCE CRITERIA: An excavation permit must be issued prior to any excavation commencing.
label | ○ Plant and equipment shall be appropriate for the task.
label | ○ Excavation operations shall not disturb areas outside the limit of excavation
label | REFERENCE DOCUMENTS: Excavation permit
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: ITP Signed
label | HP*
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | 2.2 Set out drainage
label | FREQUENCY: Prior to backfilling
label | ACCEPTANCE CRITERIA: The position of all drainage lines are to be confirmed with the superintendent
label | REFERENCE DOCUMENTS: Drawings 701.10
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | HP
label | RESPONSIBILITY: Site Engineer/ Superintendent
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.3 Excavation (pipes)
label | FREQUENCY: Each Trench
label | ACCEPTANCE CRITERIA: Horizontal clearance ( between the walls of trench to the side of pipe shall be 300mm – 600mm for pipes, and 0.5 to 1 times the overall height of the culvert for box culverts. Trench walls to be vertical where practical
label | Depth of trench:
label | ○ > 100mm below underside of pipe (for pipe width < 1500 mm)
label | ○ > 200mm below underside of pipe (for pipe width > 1500 mm)
label | REFERENCE DOCUMENTS: 701.151, 701.15
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | IP
label | RESPONSIBILITY: Site Foreman
textbox | Date Completed:
checkpoint | 2.4 Excavation (pits)
label | FREQUENCY: Each Pit
label | ACCEPTANCE CRITERIA: A minimum clearance of 400mm is required around the external faces of precast pits.
label | REFERENCE DOCUMENTS: 705.05b
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | IP
label | RESPONSIBILITY: Site Foreman
textbox | Date Completed:
checkpoint | 2.5 Compact base of trench
label | FREQUENCY: Each Trench
label | ACCEPTANCE CRITERIA: Compacted to refusal using mechanical plant.
label | REFERENCE DOCUMENTS: 701.15
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | IP
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | 2.6 Place bedding material & compact
label | FREQUENCY: Each Trench
label | ACCEPTANCE CRITERIA: Bedding and backfill materials shall be placed and compacted in layers not exceeding 150 mm loose thickness. Bedding shall be compacted to refusal using hand held mechanical equipment. Bedding material which has a swell equal to or greater than 2.5% shall be maintained at a mean moisture ratio of 92% between the completion of rolling and the placement of the overlying layer.
label | REFERENCE DOCUMENTS: 701.20, 701.20a
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed, Delivery dockets
label | IP
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | 2.7 Place pipes & precast pits
label | FREQUENCY: Each Line/Pit
label | ACCEPTANCE CRITERIA: Pipes & pits placed as shown on the drawings. No laying to occur until bedding lines and levels and compaction requirements have been satisfied
label | REFERENCE DOCUMENTS: Drawings
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | IP
label | RESPONSIBILITY: Site Engineer / Site Foreman
textbox | Date Completed:
checkpoint | 2.8 Jointing pipe sections
label | FREQUENCY: Each Line
label | ACCEPTANCE CRITERIA: All interlocking (flush) joint reinforced concrete pipes shall be mortar jointed, or wrapped with a 200 mm wide external joint rubber band.
label | REFERENCE DOCUMENTS: 701.18
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | IP
label | RESPONSIBILITY: Site Engineer / Site Foreman
textbox | Date Completed:
checkpoint | 2.9 Sealing - for joining culvert sections and pipe penetrations in pits
label | FREQUENCY: Each Pit
label | ACCEPTANCE CRITERIA: Contact areas between top and bottom sections of box culverts to be mortared. The joints between various components such as drainage pits, access chambers and pipes shall be made watertight using a cementitious mortar in accordance with the requirements of Clause 610.32.
label | REFERENCE DOCUMENTS: 610.32, 701.17c
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | WP
label | RESPONSIBILITY: Site Engineer / Site Foreman
textbox | Date Completed:
checkpoint | 2.10 Survey of laid pipe or pit
label | FREQUENCY: Prior to backfilling
label | ACCEPTANCE CRITERIA: The location of each run of drainage has been verified prior to backfilling and conforms to the following tolerances: (a) offset of entry pits required to match lines of kerbs or barriers ±20 mm
label | (b) plan location of pits other than offsets to kerb lines or barriers ±100 mm
label | (c) invert level of pipes at pits ±50 mm
label | (d) departure from design grade of pipe runs ±10 mm in 10 m provided minimum grade is not less than 1:250
label | REFERENCE DOCUMENTS: 701.1
label | INSPECTION/TEST METHOD: Survey Conformance Point
label | RECORD OF CONFORMITY: ITP Signed
label | SCP
label | RESPONSIBILITY: Site Engineer/ Surveyor
textbox | Date Completed:
checkpoint | 2.11 Haunching & compaction of bedding material
label | FREQUENCY: each lot
label | ACCEPTANCE CRITERIA: Height of additional bedding material = 30% of nominal pipe diameter or culvert height.
label | ○ Loose layer thickness <=150mm
label | ○ Compacted to refusal using hand held mechanical equipment.
label | ○ 1 lot = 150mm layer
label | REFERENCE DOCUMENTS: 701.16, 701.20
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | WP
label | RESPONSIBILITY: Site Engineer / Site Foreman
textbox | Date Completed:
checkpoint | 2.12 Place & compact backfill material over pipes
label | FREQUENCY: each lot
label | ACCEPTANCE CRITERIA: Backfill under paved area: fill trench with selected back fill material to subgrade level
label | ○ Backfill under area not paved: Back fill trench with selected back fill to a level 0.3 m above the top of pipe or culvert, and ordinary back fill above that level
label | ○ Loose layer thickness <= 150mm.
label | ○ 1 lot = 150mm layer
label | REFERENCE DOCUMENTS: 701.19, 701.20
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | IP
label | RESPONSIBILITY: Site Engineer / Site Foreman
textbox | Date Completed:
checkpoint | 2.13 Place & compact backfill material around pits
label | FREQUENCY: Each Pit
label | ACCEPTANCE CRITERIA: Loose layer thickness <= 300mm.
label | ○ Compacted to refusal using hand held mechanical equipment.
label | REFERENCE DOCUMENTS: 705.18
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | IP
label | RESPONSIBILITY: Site Enginer
textbox | Date Completed:
checkpoint | 2.14 Backfilling with cement stabilised sand
label | FREQUENCY: Each culvert
label | ACCEPTANCE CRITERIA: Where approval is given from superintendent, culverts in trenches may be backfilled to half the pipe diameter or box culvert height with 3% stabilised sand with a water content sufficient to ensure penetration beneath the pipe or box culvert invert without leaving free surface water.
label | REFERENCE DOCUMENTS: VicRoads Spec. Cl. 701.19(a)
label | INSPECTION/TEST METHOD: Site Inspection
label | RECORD OF CONFORMITY: Superintendent approval, ITP signed
label | AP
label | RESPONSIBILITY: Project Engineer / Superintendent
textbox | Date Completed:
checkpoint | 2.15 Install step irons
label | FREQUENCY: Each Pit
label | ACCEPTANCE CRITERIA: For pits > 1m deep.
label | REFERENCE DOCUMENTS: 705.12
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | IP
label | RESPONSIBILITY: Site Enginer
textbox | Date Completed:
checkpoint | 2.16 Pit base shaped with concrete to match pipe invert
label | FREQUENCY: Each Pit
label | ACCEPTANCE CRITERIA: As shown on Standard VicRoads drawing - Pit & Pipe Invert levels SD 1002
label | REFERENCE DOCUMENTS: Standard VicRoads drawing SD 1002
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | IP
label | RESPONSIBILITY: Site Enginer
textbox | Date Completed:
checkpoint | 2.17 Place pit covers
label | FREQUENCY: Each Pit
label | ACCEPTANCE CRITERIA: Covers must be set to within ±10mm of the design levels shown on the drawings
label | REFERENCE DOCUMENTS: 705.17
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: ITP Signed
label | IP
label | RESPONSIBILITY: Site Engineer / Site Foreman
textbox | Date Completed:
checkpoint | 2.18 Repairs to damaged pipes and box culverts
label | FREQUENCY: Each damaged pipe or culvert
label | ACCEPTANCE CRITERIA: No repairs shall be undertaken without the superintendents approval of the repair materials and procedures
label | ○ All repair procedures undertaken in accordance with Cl 701.25
label | REFERENCE DOCUMENTS: 701.31a
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: ITP Signed
label | HP
label | RESPONSIBILITY: Site Engineer/ Superintendent
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | Testing & Completion
checkpoint | 3.1 Compaction and moisture content of backfill & bedding material
label | FREQUENCY: at least 20% of all lots
label | ACCEPTANCE CRITERIA: Backfill material shall be compactied to a mean density ratio of 97% using standard compactive effort.
label | ○ Bedding shall be compacted to refusal using hand held mechanical equipment. Bedding material which has a swell equal to or greater than 2.5% shall be maintained at a mean moisture ratio of 92% between the completion of rolling and the placement of the overlying layer.
label | REFERENCE DOCUMENTS: 701.20a, 701.20b
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: Test Reports
label | TP
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | 3.2 CCTV inspection
label | FREQUENCY: each lot
label | ACCEPTANCE CRITERIA: All drainage lines constructed shall be inspected, after completion of earthworks to subgrade level and prior to construction of pavement layers, by an independent testing organisation using closed circuit television (CCTV) to verify that the flow of water is not obstructed by waste construction material left inside and to check for visible signs of defects.
label | REFERENCE DOCUMENTS: 701.3
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: CCTV Report
label | HP
label | RESPONSIBILITY: Site Engineer/ Superintendent
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 Flushing of pipes
label | FREQUENCY: Each line
label | ACCEPTANCE CRITERIA: All pipes to be flushed clean upon completion
label | REFERENCE DOCUMENTS: 701.28
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: ITP Signed
label | IP
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | 3.4 Final inspection
label | FREQUENCY: Each line
label | ACCEPTANCE CRITERIA: Pit and pipes to be clean suitable for use prior to hand over
label | REFERENCE DOCUMENTS: 701.28
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: Lot Maps
label | IP
label | RESPONSIBILITY: Site Engineer
textbox | Date Completed:
checkpoint | Final Inspection
note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
textbox | Date: