## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist-flat | Master Cable Tray, Ladder & Basket Installation |  | Master Cable Tray, Ladder & Basket Installation
| checkpoint | Setting Out: Tray, Ladder and Basket has been run level, straight and parallel with the building lines as per C2112.3.
| checkpoint | Installation: Tray, Ladder and Basket has been installed per agreed technical submission requirements and as per C2112.10, 11 & 13.
| checkpoint | Installation: Fixings and fastenings are of material appropriate to the parts being fixed and the loads imposed as per C2112.3 and approved Gravity Support methods.
| checkpoint | Installation: Fixings and fastenings are of material appropriate to the parts being fixed and the loads imposed as per C2112.3 and approved Seismic Support methods.
| checkpoint | Installation: HST3 M12 x 145 seismic anchors are used/installed as per the WSP seismic design
| checkpoint | Installation: Correct embedment (145mm) of HST3 seismic anchors has been achieved in accordance with Hilti installation instructions.
| checkpoint | Installation: Correct torque setting (60nM) of HST3 seismic anchors has been achieved in accordance with Hilti installation instructions.
| checkpoint | Installation: Joints and accessories fit closely and are correctly matched as per C2112.3.
| checkpoint | Installation: All sharp edges have been removed, cut ends/cut-outs are neat and square and protected against corrosion as per C2112.3.
| checkpoint | Installation: Cable support systems have been assembled so that sharp edges, screws or other fixing materials do not penetrate the cable corridor as per C2112.3.
| checkpoint | Installation: Colour coding of Tray, Ladder and Basket has been installed as per C2112.9.
| checkpoint | Installation: Solar shields, covers and guards have been installed as per C2112.12.
| checkpoint | Installation: Non-continuous runs of Tray, Ladder and Basket have been provided with additional earth continuity straps bolted between sections as per C2112.8.
| checkpoint | Sign-Off: All changes to the current construction drawings have been documented and issued to James Eymael for action.
| checkpoint | Sign-Off: Any comments below.
| checklist-flat | Master Transformer Installation |  | Master Transformer Installation
| checkpoint | All staff briefed on safety requirements and installation procedure
| checkpoint | Confirm floor loading specifications satisfactory for installation
| checkpoint | Verify that drawings are latest revision and manufacturer's manuals available on site
| checkpoint | No damage to Transformer, foundation matches transformer fixing arrangements, no damage to bushings, and paint work to specification.
| checkpoint | Impact recorder removed and returned.
| checkpoint | Check location, orientation, level and alignment and vibration pads installed.
| checkpoint | Record stud embedment depth
| checkpoint | Transformer Hold Down completed as per: CAL002Transformer Hold Down Design V1.mcdx
| checkpoint | Connection to earth grid complete. Two separate paths to earth.
| checkpoint | Installation of HV & LV bushings as per manufacturer's specification.
| checkpoint | Primary connections made as per manufacturer's specification, correct grease used, secondary connection made correctly, tight and protected.
| checkpoint | Bus flexibles have specified phase-phase and phase-earth clearances, temporary earth points installed.
| checkpoint | Clean insulator surface, no porcelain damage
| checkpoint | Clean the transformer windings from inside and outside, by air blower
| checkpoint | Serial numbers are in correct order and recorded, system numbers and phases correctly identified
| checkpoint | All bolts tightened as specified check transformer manufacturer's checklist.
| checkpoint | Cable installation and termination checklist completed,
| checkpoint | All auxiliary wiring tight in terminals and in accordance with drawings. Terminal crimp lugs and bootlace ferrules used. Trunking and termination covers in place.
| checkpoint | Calibrate temperature sensors. Test alarm, fan start (where applicable) and trip temperature operation.
| checkpoint | Drawings are 'as built'