## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | RFI-R-DN1205-DOW-RFI-0409.22-ITP 05 - Commissioning | itp |  |  |  |  | RFI-R-DN1205-DOW-RFI-0409.22-ITP 05 - Commissioning
section | 1.0 Pipe Testing and cleaning
checkpoint | 1.1 - Chlorination (1)
label | Responsibility - Operator/ Engineer
label | Specification Reference - RITS 6.3.11
label | Conformance Criteria Summary - Chlorine to be liquid only
label | Method - TDS and photo
label | Frequency - Each completed pressure test line
label | Hold / Witness Point - HOLD
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.1 - Chlorination (2)
label | Responsibility - Operator/ Engineer
label | Specification Reference - RITS 6.3.11
label | Conformance Criteria Summary - Chlorine to be between 10mg/l and 100mg/l
label | Method - Chlorine strips
label | Frequency - Each pressure tested line
label | Hold / Witness Point - HOLD
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.2 - Flushing
label | Responsibility - Operator/ Engineer
label | Specification Reference - RITS 6.3.11 & 6.3.11.1
label | Conformance Criteria Summary - Line to be flushed into sewer or Dichlorination unit to be used into kerb/catchpit
label | Method - Visual
label | Frequency - Each pressure tested line
label | Hold / Witness Point - HOLD
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.3 - Bacto Testing (1)
label | Responsibility - Engineer
label | Specification Reference - RITS 6.3.11.2
label | Conformance Criteria Summary - Tests to be taken at equivalent to 1 per 100m of installed pipe where possible
label | Method - HCC Attendance – Written confirmation
label | Frequency - Each pressure tested line
label | Hold / Witness Point - HOLD
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.3 - Bacto Testing (2)
label | Responsibility - Engineer
label | Specification Reference - RITS 6.3.11.2
label | Conformance Criteria Summary - <1MPN per 100mls (E.coli and Total Coliforms)
label | ○ <20CFU/ml Heterotrophic Plate Counts
label | ○ Miscellaneous
label | Method - Lab Test
label | Frequency - Each pressure tested line
label | Hold / Witness Point - HOLD
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.4 - Watermain to be kept charged (Provisional)
label | Responsibility - Engineer
label | Specification Reference - RITS 6.3.13
label | Conformance Criteria Summary - After any watermain has been laid, tested and disinfected, it shall be kept continually charged with water, and under pressure. If the permanent connection to the existing reticulation is delayed by more than 5 days, a temporary small diameter connection shall be made from the existing reticulation. The pressure must be maintained while other underground services are being laid in the vicinity of the new main.
label | Method - Sample records
label | Frequency - Each pressure tested line
label | Hold / Witness Point - HOLD
holdpoint | AUTHORITY HOLDPOINT