## Master List Templates
Id | Type | Name | Values | Prompting Name | Prefix | Postfix
2cf5781e-70d2-4d7a-ac1f-91597358bd4c | checklist | ITC 001 - Main Switchboard Installation Checklist |  | ITC 001 - Main Switchboard Installation Checklist
0d5ffe8c-d2c1-4b2e-b3b3-f27b63e72c4a | section | Section 1: Installation inspection checklist
0e539a67-2eae-425e-8610-31752c58c2e0 | checkpoint | Current approved workshop drawings available on site database
afa6e17f-ab4c-40d3-a732-8ee046af71c4 | checkpoint | Approved factory acceptance testing documents available on site data base
8b86ea1c-a130-4e2f-83aa-d0774b47fa78 | checkpoint | Switchboard installed in final location as per approved drawings
eb10d271-d252-42ed-9ab6-63bf32324f03 | checkpoint | Switchboard manufacturer Site acceptance testing complete and signed off and available on site data base
fc34c45f-5ede-4577-9d2f-5689eb22967a | checkpoint | Confirm labels are correct
e3f93df0-19ce-4b05-a874-e572141a3f07 | checkpoint | Confirm Earthing connections are installed
d2ab7e92-0af7-4a91-8d90-def979cf50de | checkpoint | Busbar connections: Confirm witness marks applied where visible
e94eae65-6641-43ce-a23d-aab8d2552bf5 | checkpoint | Confirm each cubicle is free from dust and foreign debris
0a960f01-c425-462a-91d3-c52ab86d8cab | checkpoint | Confirm door seals intact
fa5e9d9a-882e-4a65-aabf-97ee64028e25 | checkpoint | Confirm door handles and hinges operate correctly, verify locking
06b46854-1008-4a3f-b287-8b88e35a64c2 | checkpoint | Undertake functional testing of all isolators - document results on ITC 019
caaf5c80-b26f-416f-bc7e-b7f974d9aa2f | checkpoint | Undertake functional testing of all circuit breakers -results on ITC 019
928a601d-0a69-48e2-b386-f1c44b58b619 | checkpoint | Confirm Multiple Earth Neutral Link (where Fitted)
712872a1-9975-4efc-8c05-681e923c9357 | checkpoint | All cubicles open/check list signed UNTERMINATED SECTION OF ITC 004
2eb00f1d-4f8f-42af-abe1-7a9ff6017d36 | section | Section 2: Busbar insulation testing, all results less than 1MΩ is classed as a fail
6a9ebab3-26e2-4fd0-8798-cd4deca19321 | checkpoint | L1 - EARTH
dc698667-78d4-5056-a178-63b4ab986951 | textbox | MΩ
6e8b9335-4565-405c-85cf-969557f1ec85 | checkpoint | L2 - EARTH
e5f88551-0a0d-548a-bfcc-fe8c0dc4df34 | textbox | MΩ
c38dacf6-3794-4399-bc60-bff10a2326a7 | checkpoint | L3 - EARTH
aab87287-88f3-5d77-ab18-688d67eaeaeb | textbox | MΩ
813be960-24db-4690-923f-7b30d6757974 | checkpoint | NEUTRAL - EARTH
bbcd0f98-6833-5e40-bb02-86e9875a0cb0 | textbox | MΩ
947438c7-daac-4e0f-ab7b-e09c2134cf20 | checkpoint | L1 - L2
c4030fad-a24f-5a32-a2fa-000cb6d15714 | textbox | MΩ
1afdd2ed-dcfc-4902-928c-aa0872a92582 | checkpoint | L1 - L3
126b9f3a-85f1-5bed-839b-c43421ac83bf | textbox | MΩ
43e52b96-ef97-4a60-8ca6-6419306ceeb1 | checkpoint | L3 - L2
95884cc7-6570-5607-8e0f-911046104357 | textbox | MΩ
54523fb5-86db-43e2-84a7-f0d375a8884f | checkpoint | L1 - NEUTRAL
95b60f79-3c7d-524a-ab59-d18244c025a8 | textbox | MΩ
14f1382f-351e-4963-891c-b952c6106b3f | checkpoint | L2 - NEUTRAL
dc6d2dd2-8dcb-55e4-8a34-5bec37fa3542 | textbox | MΩ
b974995f-b279-4c72-a2b3-4a6c4faaf86d | checkpoint | L3 - NEUTRAL
b387792d-a9cd-50e0-8ac6-ab5fb2906e09 | textbox | MΩ
55364ce4-9773-4372-86aa-e14c9af34ce3 | section | Section 3: Switchboard earthing busbar(s) continuity and resistance verification
009ea31e-f419-42d6-bd49-5ad2b468957b | checkpoint | POINT TO POINT TEST OF SWITCHBOARD
db11b2ad-be6d-55f2-8295-b48eb4e35120 | textbox | SECTION:
17ebdd12-0ec2-5628-a5ad-835ac59c7ce3 | textbox | RESULT Ω:
555eac3d-d178-5c79-8cf0-13bd8da12df9 | textbox | SECTION:
1a3adc41-e733-5dff-8a10-d16c9d482491 | textbox | RESULT Ω:
74473b43-e00b-555e-8c0c-86724810aee2 | textbox | Test Equipment Type i.e. Multimeter
d0536893-dbe5-5952-9cc0-dc22e052867f | textbox | Brand/Model
d6a7efca-074b-5eb9-a572-884781e3c7c0 | textbox | Serial No.
3eaa8672-4c6d-50a4-9da4-2e582fcffb5c | date | Calibration Due
df038483-b526-4838-9a5b-f4e8134a5f34 | checkpoint-no-value | COMMENTS:
e730b226-0ff1-5b1a-82aa-272f179076a7 | note | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed. | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed. |  | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed. | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
ce694feb-51ce-4817-b56d-a327353d9e92 | checkpoint | FINAL ACCEPTANCE: Foreman ot higher
b1a85420-e34d-4f64-9765-5d3f97e60bfe | signoff | Signoff
5e38d075-27f3-4cdf-9084-9897eb4786fd | checklist | ITC 002 - Main Switchboard Pre Energisation Test Report |  | ITC 002 - Main Switchboard Pre Energisation Test Report
ff86b89a-a168-45ce-b4ec-e9eedae13090 | section | Details
2f959846-74a5-4359-ac6d-214364264e98 | checkpoint | Confirm ITC 001 has been completed and signed off
1b5beda8-a27a-41c4-9cdf-3da95cc81c6e | checkpoint | Confirm section 4 of ITC 005 has been completed and signed off
431d09ea-6311-4ead-9318-f69de6deeece | checkpoint | Confirm ITC - 019 has been completed and signed off
ce6cdd98-1c2d-42c6-8abe-d319e557cace | checkpoint | Referenced Drawing Number and Revision
fa2002c8-0ea9-403c-8ba0-e1d921825f80 | checkpoint | Correct cable glands used.
4968d36b-f1d8-4865-8b1c-7f5024fecab9 | checkpoint | Cables lugged and terminated correctly
57d2c40e-52f2-47c9-af4d-5997b246732f | checkpoint | All cable terminations bolted, torqued and witness marks applied.
b16b9e63-4d31-40b6-89c8-2e727c0e3192 | checkpoint | All cables restrained in switchboards
a601d463-1f26-440c-ba64-ba8a6eb41f58 | checkpoint | All Cables visually inspected, ensuring cable sheaths are intact and in good condition.
db3bae27-4e33-4bc9-b62b-15412677cd77 | checkpoint | Cables are labelled correctly at origin and destination as per schedule, if required.
21561afa-db70-4173-ab0c-b9e0e1b1df63 | checkpoint | Cables are terminated at destination, and made safe.
ce01f478-01a6-4722-af46-087c1aaf258c | checkpoint | If cables are not terminated at the destination, remove from breaker and make safe
188d8149-169d-4179-b13e-f3d2cd434500 | checkpoint | All Exposed conductors are covered or protected in cubicle or terminal box.
0d297b45-2654-4908-a364-f78a64724aaa | checkpoint | Switchboard is clean and free access is available around the board
e49102d7-3df6-4458-b5f6-83279bde95be | checkpoint | Final Visual Inspection undertaken by Senior GRiD representative (Project Manager or higher)
1864d24e-73c1-47c8-ac34-775a8dae8a29 | signoff | Signoff
520a0496-18fe-41d2-bc5c-2f9addb2d593 | checkpoint | Supply Authority or Regulatory Body inspection completed
1ce1c1f5-03c6-5644-866d-0656703c8dbb | date | Date completed:
362ddf1a-e164-4cba-9ee8-dae940dff307 | checkpoint | All works complete in switchboard
88770ec0-47df-4115-aa5f-feb7629a6cba | checkpoint | All switchboard doors, escutcheons and covers reinstated and ready for energisation.
5f2308e1-c121-4bc0-a4c7-8365f802bfd1 | checkpoint | Notice of intent to energise form complete and signed by Principle Contractor, please attach.
550adf1d-b0e8-423c-9f91-83735666f0a2 | checkpoint-no-value | COMMENTS:
ef29f765-64c1-5fd8-9ffd-146eba23af77 | note | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed. | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed. |  | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed. | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
bac6206e-9025-4875-81d1-6d866ecc3d42 | checkpoint | FINAL ACCEPTANCE: Foreman or higher
a1ec2efb-d759-4471-8ca3-fca20aeaa14c | signoff | Signoff
d30ba9e6-eeb2-4b3d-9205-a289f0ab6261 | checklist | ITC 004 - Switchboard Cubicle Checklist |  | ITC 004 - Switchboard Cubicle Checklist
f424d7af-5214-459c-9562-ef8597e4e17e | section | Section 1: Cubicle Checklist
4c0a7e41-e34c-4960-99c8-87ad06d8c590 | checkpoint-no-value | CUBCLE REF
b31c3382-cd93-5bb4-b5d7-701ffe94f566 | textbox | CUBCLE REF #
7650db03-7b0b-4b8b-b29b-ac6e5dc56502 | checkpoint | UN-TERMINATED or cubicles with no terminations
7ed27afb-675d-59e5-9a82-d474ec2ecdc0 | button | OPENED | Yes,No
a1c5dacd-80ef-5cd3-880c-b73eefe15cc3 | button | FREE OF DEBRIS | Yes,No
31f2d885-c067-52d1-8779-00cc875dc29c | note | ADD PHOTOS
1e279405-6dd5-4c1c-a50d-83312d17a717 | checkpoint | TERMINATED
92d83068-51c9-53ca-82a2-9109636c4fc8 | button | CABLES TERMINATED | Yes,No
ac8831c3-07ce-50e2-b17e-c0bf5d56377b | button | CLEAN/FREE OF DEBRIS | Yes,No
e28cda10-fc69-5384-87b7-59d0c9677cae | note | ADD PHOTOS
aa2fabdf-6184-40af-8e54-2be98f652710 | checkpoint-no-value | COMMENTS:
8ad53d05-4a6a-5e2e-b2ee-41511fab508d | note | The above Electricians working for GRiD ELECTRICAL SERVICES Pty Ltd Certify the Electrical installation corresponding beside relevant Electrician’s name, has been tested and verified to ensure it is electrically safe and is in accordance with the wiring rules and any other standard applying to the electrical installation under the Electrical Safety Acts of that particular state/Territory at the date that the test was completed. | The above Electricians working for GRiD ELECTRICAL SERVICES Pty Ltd Certify the Electrical installation corresponding beside relevant Electrician’s name, has been tested and verified to ensure it is electrically safe and is in accordance with the wiring rules and any other standard applying to the electrical installation under the Electrical Safety Acts of that particular state/Territory at the date that the test was completed. |  | The above Electricians working for GRiD ELECTRICAL SERVICES Pty Ltd Certify the Electrical installation corresponding beside relevant Electrician’s name, has been tested and verified to ensure it is electrically safe and is in accordance with the wiring rules and any other standard applying to the electrical installation under the Electrical Safety Acts of that particular state/Territory at the date that the test was completed. | The above Electricians working for GRiD ELECTRICAL SERVICES Pty Ltd Certify the Electrical installation corresponding beside relevant Electrician’s name, has been tested and verified to ensure it is electrically safe and is in accordance with the wiring rules and any other standard applying to the electrical installation under the Electrical Safety Acts of that particular state/Territory at the date that the test was completed.
35cde7ec-6de5-4a11-9d6a-6670fb226308 | checkpoint | FINAL ACCEPTANCE: Foreman or higher
344ae83f-c3b0-42c9-a03b-e02ac1172bc5 | signoff | Signoff
a7dcbc4b-1864-4355-ba9f-7baf88004d24 | checklist | ITC 005 - Main, Submain & Consumer Main Test Record |  | ITC 005 - Main, Submain & Consumer Main Test Record
18224c63-6831-41b2-a245-d3a819a3ce16 | section | Details
1773b5b7-7c2c-46ab-95a7-1c6d40d5359f | checkpoint-no-value | Referenced Drawings and Revision Number
b2ac76a2-129a-5702-b461-1c2f9ba1e4a3 | textbox | Referenced Drawings and Revision Number:
60c06762-e79f-45fa-aef2-ad36aafcf893 | section | Section 1: Cable details
b0b3d9a3-4f56-48d1-bf4e-443eeba3ebfd | checkpoint-no-value | Cable details
82097a64-b2a7-584e-9049-db4515402efe | textbox | Cable Identification
01865faf-4c45-5bbd-9ae2-2fb55ab2c813 | textbox | Cable size and type:
1a297a2a-bef2-5135-8024-96889fc0fd16 | textbox | Cable installation method
b91ea26e-5f61-5a2f-9e29-813da4f631fe | textbox | Cable origin:
736446ef-381a-546f-8e38-ce5213527064 | textbox | Approximate length:
89657e27-3e9e-56d7-8072-224349778601 | textbox | Cable thermal rating
367ace92-fe7e-5390-b4d8-aaf522407b54 | textbox | Cable destination:
cc0fe942-95dc-5bb7-a886-127d1356e462 | textbox | Number of cores/configuration
8ed69a9b-a7bc-5843-b03f-21796f4de862 | textbox | Supplies Life Safety Services?
4cf735c5-078a-48fe-a6f6-3e939fe89783 | section | Section 2: Cable protection details
0b1d2874-0ec2-4be1-87c9-458183643463 | checkpoint-no-value | Cable protection details
00e2ed61-a762-559b-b97f-c7316d95f48a | textbox | Protection type and details
4c9fdfd1-8839-598d-8481-0d4bea554c23 | textbox | Breaking Rating (KA)
ceeedfde-9988-579b-b6c7-1be61b4635e6 | textbox | Protection device ID
3170bdfc-d5a0-58c7-9bf9-de3565ae0b12 | textbox | Short time overload (Short Circuit)
b883742f-3ef0-52d0-8124-537fc7e470b7 | textbox | Protection rating (A)
2eb65a42-d2c2-5092-9340-8ae6003750db | textbox | Long time overload (Thermal Overload)
b3a3300e-095b-413b-93ab-a164c01c45b6 | section | Section 3: Visual Inspection of Cable according to AS/NZS 3000 and AS/NZS 3017
3c6f589e-14b5-4a0d-aaea-54fe34f0e011 | checkpoint | Confirm that the cable is provided with adequate support and secured across the cables entire length, ensuring the cable does not move under fault conditions and installed according to prescribed methods.
6ccc0804-dd4d-4c6f-abf2-291f32117143 | checkpoint | Confirm that the cable used is as per the current cable schedule, confirm if the cable is installed as per drawings current drawings.
83b77891-27f2-4425-8401-adcc2a01fa7a | checkpoint | Confirm that the cable is protected against mechanical damage, environmental and other external influences.
76b4f36f-0d4c-44ef-86e8-ada66659a7e7 | checkpoint | Confirm cables are correctly labelled as required.
e4fac2a4-39d1-429c-be76-518c06574e7e | checkpoint | Confirm that the cable is terminated as per the termination specifications at both ends and that exposed parts covered. If this cannot be achieved sub mains are to be removed at both ends and made safe
6742215b-6769-4a63-ac66-a8a9a409a459 | checkpoint | Confirm cables are torqued to specifications
ee03c50f-24e0-481b-a06f-1031bb7af477 | checkpoint | Confirm that the cable does not impact or interfere with other services.
ef66624d-14fc-42ca-9871-0c970bfcc9a2 | section | Section 4: Non-Energised testing according to AS/NZS 3000 and AS/NZS 3017
daa9fc0d-3aec-4ca4-bac2-b860a4ebf763 | checkpoint | 4.1 MAIN EARTH CONTINUITY & RESISTANCE TEST
d0709955-1a5b-5c83-a453-50049baa9933 | textbox | EARTH SIZE |  |  |  | mm2
aaf01a55-1f61-5d3e-83bb-a57e1c543e99 | textbox | FROM
6f0a9240-0586-5db5-a7fd-b94f30934e2c | textbox | TO
ea68dcd7-a1c3-5fda-9eec-4c425fb7c6e3 | textbox | POINT TO POINT READING Ω |  |  |  | Ω
af2b7d3d-1858-48d4-a0cd-4b4c80aa7ace | checkpoint-no-value | 4.2 INSULATION RESISTANCE TEST VALUE MUST BE GREATER THEN 1MΩ AT 500V DC
f72938bd-b9ba-49b6-9dae-9ad168340718 | checkpoint | L1 - EARTH
07b925ca-3ea6-55a1-895d-c2ae7e2edeb1 | textbox | MΩ
345bef18-9114-4490-a369-b9b51c577f27 | checkpoint | L2 - EARTH
2ede98eb-47cb-5821-86c9-4efaca87a14e | textbox | MΩ
5cac27aa-1f2d-4d03-bfd6-4ac3d10bcec4 | checkpoint | L3 - EARTH
2343b6e6-e094-5f1a-8c18-b2923a3d055d | textbox | MΩ
38925067-030c-4d0b-b99f-dae994260a59 | checkpoint | NEUTRAL - EARTH
0d1e307a-9be5-5213-bc3d-c8c833e248f7 | textbox | MΩ
97ba013f-3aa3-452d-8a10-4d3be64fe4e3 | checkpoint | L1 - L2
ac8125c2-0b4f-596d-ad24-06daf76f6ca7 | textbox | MΩ
633b23b6-b6b2-4eee-ade8-d885e13e9fec | checkpoint | L2 - L3
658a76e7-bd8e-5753-a1eb-0735ae170555 | textbox | MΩ
53521295-a198-4e53-9969-04abf80871cc | checkpoint | L1 - L3
0b4b2daf-5e1a-5415-a2fa-c186d25a11b1 | textbox | MΩ
7c6c89ee-83f3-4451-ac40-68adc36d9737 | checkpoint | L1 - NEUTRAL
25023f2e-83b4-55c8-8d53-f89383bd72fa | textbox | MΩ
1a447c8a-29fd-407f-9f65-6a0be8ce8408 | checkpoint | L2 - NEUTRAL
d9471604-ab90-5ba0-9668-6b786ba3ecd2 | textbox | MΩ
32ceb21c-56b2-4400-b28e-42075a8126c9 | checkpoint | L3 - NEUTRAL
2bacb2d5-07ee-5c16-b65d-ffedf28d2250 | textbox | MΩ
9b3cf681-5850-468f-9eb1-ab72625c9a7d | checkpoint-no-value | 4.3 Polarity testing measurement of cable origin to end
a3f8b6ff-78b5-4bbf-a6ca-12b64fb229b7 | checkpoint | L1 TO L1
8f812a4a-ff9f-4c4d-ba83-91be1a69de88 | checkpoint | L2 TO L2
4244a35c-db6b-4066-a6e2-8dc02d8a0d9d | checkpoint | L3 TO L3
8fdcf037-d944-4b74-8717-f0c3f068150e | checkpoint | N TO N
decb331d-c2f2-450e-8e72-e796534386ff | checkpoint | 4.4 Isolation padlock/ tag installed on the main switch of field device i.e distribution board
78a64ef6-1d7e-404a-84d0-185984ed5891 | section | Section 5: ENERGISED testing according to AS/NZS 3000 and AS/NZS 3017
ec54e1bd-adc5-4d15-8b20-d7bb6a6fa519 | checkpoint | Confirm ITC 002 has been completed
62d6f7fc-8016-4b02-8826-23e376135e14 | checkpoint | Confirm cables are terminated at both ends
ac24ad3d-3bc4-4c12-96cf-ff6b2f2dd15a | checkpoint | Known Live source
00763c0b-0365-5f40-82f6-6f98e289c394 | textbox | V
d12be903-df90-436c-bbc7-8aef6eea6d02 | checkpoint | L1 - Earth
667ad6c2-2f83-5303-8809-55465ae6cbec | textbox | V
fafd9cd3-c165-4e11-86ba-8969712fc265 | checkpoint | L2 - EARTH
c64ae04c-37ca-51ec-b18d-26721d37890c | textbox | V
1a690259-3cf2-439b-b035-332a2b176036 | checkpoint | L3 - EARTH
300b78d5-a3bc-5152-9c38-6a4c6fffd40b | textbox | V
17ef2b00-025a-4297-bfa6-17cb0eea772f | checkpoint | L1 - L2
4f0749c3-6bf8-5851-b709-b7f3ed67e87f | textbox | V
1393835f-b9ec-42ec-b3fe-0736911e9e13 | checkpoint | L1 - L2
78196b12-8592-5bb8-b7db-6a16c7853ca8 | textbox | V
28856d48-adb1-4873-9190-99ad4edb70a3 | checkpoint | L3 - L1
a60ea408-0554-51bd-8dc5-5878d48100c8 | textbox | V
de6c4f00-989f-4209-a2ee-a0d985235f1f | checkpoint | NEUTRAL - EARTH
3d3c9675-e807-5b5d-999f-da124839ae23 | textbox | V
acc75d98-89cf-471e-8982-9db737f53d54 | checkpoint | L1 - NEUTRAL
518a851e-13b8-501a-ad2e-cf074d0661e6 | textbox | V
66c60a77-ae59-4978-b697-042db326dec8 | checkpoint | L2 - NEUTRAL
4990d13a-0f6d-5bed-95ad-682e9efcc540 | textbox | V
e5aa7c7b-4d75-413e-8334-7f49beff2148 | checkpoint | L3 - NEUTRAL
7903e942-3645-511e-847e-b04d1b5dc110 | textbox | V
323de0b5-0dc4-4f9b-a844-b6482134c00a | checkpoint | Known Live source
c46f8559-a36b-5af6-85ff-dad17828c335 | textbox | V
4e3ab974-c7f6-4faf-9963-0b9ad4e0e6ae | checkpoint | 5.2 Phase Rotation testing according to AS/NZS 3000 and AS/NZS 3017
b0d34536-2883-522a-bc16-6c63b31fb957 | button | CLOCK WISE 1-2-3 | Yes,No
458dacdd-35fc-5f6d-9d26-3d49c3b25380 | button | COUNTER CLOCK WISE 3-2-1 | Yes,No
334a232d-0c46-48f0-bff1-a2a3b17b6959 | checkpoint | 5.3 Fault loop Impedance testing according to AS/NZS 3000 and AS/NZS 3017
9ddfc579-faed-5771-9dca-8191faaaaf85 | textbox | MEASURED IMPEDANCE VALUE Ω |  |  |  | Ω
ec8b8bc1-e6b1-543c-97dd-dc0631243cbc | textbox | CALCULATED MAXIMUM VALUE (Ω) as per the cable schedule report |  |  |  | Ω
5e07b22f-09a5-48f6-ab80-a07dd4891605 | section | Section 6: Test equipment register
1047db26-7590-4dc2-9d9d-a7283e183566 | checkpoint | Test equipment register (1)
10c0dee5-8b0d-5c0a-8c95-ef16a569636f | textbox | Test Equipment Type
e76bf34b-06ec-5698-a56d-7ab9f05627bf | textbox | Make/ model
e6ef370d-f10c-56dd-97df-1a7b2da58d0d | textbox | Asset Number
0e78d7ad-918a-53e4-80ca-74e9e986846c | textbox | Serial No.
016b3444-b3dd-54f7-8337-b1f5a3546673 | textbox | Last Calibration
ff781f50-6b17-5997-8678-75952d1b2c34 | textbox | Next Calibration due
744a0b22-01f3-5151-97c1-5d52d5e0a9ab | textbox | Tester
0f8b6dac-e6f7-5b69-995b-0e445565f116 | date | Date
d94b1843-c609-4927-a7ab-93ee92893f43 | checkpoint | Test equipment register (2)
2a291c50-d37b-5689-b9dd-f90fbd7bdae0 | textbox | Test Equipment Type
00cb5b68-d8b8-527f-9e53-b180a4079d54 | textbox | Make/ model
afd48e25-01a1-5859-9892-628affd53586 | textbox | Asset Number
cb2cc9af-3ab0-5a46-88a7-c33fb260ef32 | textbox | Serial No.
2775d1c9-96cd-5629-9970-4f9665f2a987 | textbox | Last Calibration
19f6a07d-fac5-50f5-bd23-8605d9ef58c0 | textbox | Next Calibration due
546e30fc-209c-58f2-b265-62ae5433e416 | textbox | Tester
20b81241-4b06-5b4c-b90e-6afeb32b7386 | date | Date
8b1b281d-24cc-4acc-9e84-9fb2063db00c | checkpoint | Test equipment register (3)
493455c9-8d69-5aa5-9557-3c4df925e0b8 | textbox | Test Equipment Type
eeeb639f-7c4e-5aa5-bf52-e46e29fc49a8 | textbox | Make/ model
12c6af4e-950b-5015-bf54-039598381d3a | textbox | Asset Number
b12dfb18-8a81-58ca-81bf-87eb337dd27d | textbox | Serial No.
35a14abb-35c9-51c2-9495-1bd5b1fa3c2f | textbox | Last Calibration
cf475aa7-6516-5179-aa18-8f761b9b6bcf | textbox | Next Calibration due
aa5aeca0-ec1b-54da-b6e0-2335596c3ccf | textbox | Tester
b521ef2f-87a8-591d-9519-253b8a0ca7dc | date | Date
db82d0e2-c1b0-43fa-8b2a-a12dc0bbab63 | checkpoint | Test equipment register (4)
65bab557-5a99-5209-98a8-e4e7d0bfa023 | textbox | Test Equipment Type
88f55db0-4840-5ade-900d-6894e631c5d8 | textbox | Make/ model
8225e77b-42aa-50e4-90fc-f1cff174e492 | textbox | Asset Number
4e4d46d8-4d58-5eff-9b15-a7b9b908ea76 | textbox | Serial No.
327c4955-f73e-539c-a68b-c265aec5036e | textbox | Last Calibration
c84990f5-d6ec-5b8a-a70a-b2a4bead9c05 | textbox | Next Calibration due
0b199568-7a6d-5a52-ab60-be46a8c10172 | textbox | Tester
c3db9579-fde8-5bc4-965a-d66daa28785e | date | Date
5fdbc64d-d36a-469c-9040-2515c6bad857 | checkpoint-no-value | COMMENTS:
2b1b6f6a-13fe-5575-a570-784c20e4d8df | note | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
9631c341-b929-4c3b-a6f3-7d06cc71ecf0 | checkpoint | FINAL ACCEPTANCE: Foreman or higher
fe115178-bfa0-4bae-81d9-44dbccffd018 | signoff | Signoff
b4352a8c-875a-40e1-bfee-29c1ee79d675 | checklist | ITC 006 - Commissioning of Light and Power Circuits |  | ITC 006 - Commissioning of Light and Power Circuits
bce3c3f3-ace7-46b0-bb39-c9bfc155bfa6 | section | Section 1: Test and Commissioning Activities as per AS3000 & AS3017
e2bb2892-a96f-4285-a9af-5c97e0ec9146 | checkpoint-no-value | Details
33bf3f33-ad87-5d16-ae49-8963b4329b39 | textbox | RCD Rating |  |  |  | mA
f5907bda-3e5c-557e-90d0-94554b89251c | textbox | RCD Location |  |  |  | DB/ Field
d989af3f-ed3c-52b0-b71e-1315a7b6c32b | textbox | Circuit Destination / Circuit Designation
3d27373d-d8d0-5301-907b-d07b1e5ee1b2 | textbox | Number of Points per Circuit
b9c50a2d-5fb1-5e21-ace6-f991ae4df56c | button | ITC - 20 & ITC - 33 Complete. | Yes,No
66494414-7ea7-5fe3-8056-9732f93b9943 | note | If not STOP until complete
cd09c17b-2280-514b-80a6-0ac8bb5c1ed9 | button | Visual Inspection to confirm all points are installed | Yes,No
f821fbff-e415-4ffe-869b-e300b4405a98 | section | DE-ENERGISED TESTS
8b055e3e-fad1-49d4-a32a-f5f017933378 | checkpoint | Confirmation all labels are installed
dc4b7ca2-1ae1-5617-9038-85ed35a4ce21 | textbox | Earth Continuity Ω
5c0267f6-c850-4461-84a8-fe0c533f27c0 | checkpoint | Polarity/ Phasing
9d72d024-8bd8-5a32-8beb-543fae232dbe | textbox | PH
1d6062f6-89d0-5581-aeb6-f97a261f7d6f | textbox | N
137e08c5-db82-5e9e-8278-6514761c9fda | textbox | E
c3d6400b-60a9-4c39-a83d-020202f4c7ed | checkpoint-no-value | Insulation Resistance Readings
d7b78908-abc3-5991-b88e-0332b2a3e345 | note | Anything less then 1M ohm is classed as a fail
36ca5fd8-a83e-4448-a342-da1df0795e4a | checkpoint | PH - E
8eb2794b-d0f0-5b8f-b6c0-fc617c0450ef | textbox | MΩ
60c81ffc-19b5-433c-99b7-98c15f459510 | checkpoint | PH - N
8dc6d015-fffb-5462-88ba-0d0b24512742 | textbox | MΩ
151f495a-3e30-4029-82d7-4fa8a24f861d | checkpoint | N - E
f06337f3-026e-5166-be1c-316d45621cd8 | textbox | MΩ
e3c525b7-f67c-4fc2-b3c3-a5daa9829021 | checkpoint | PH - PH
05531c34-4ec0-5ee2-ad54-ed2faff8105f | textbox | MΩ
6efd8fb9-0859-4b28-b613-0eb630332443 | section | ENERGISED TESTS (DE-ENERGISED SECTION TO BE COMPLETED AND SIGNED FIRST)
3c3ade5b-5f45-481c-b21c-96a15d6f9142 | checkpoint | Confirmation all labels are installed
c581b87c-2221-4724-871f-c6f7882c637e | checkpoint-no-value | Voltage Readings
67a08dff-42b2-545d-a3b1-f285c336663d | textbox | PH-N |  |  |  | Volts
b0f8d040-c3e9-5093-a634-8e137fecb2d0 | textbox | PH-E |  |  |  | Volts
8e4eec3f-9253-5a87-a795-f07b238a7c0f | textbox | N-E |  |  |  | Volts
769c50c2-d9ec-56db-a430-67b561e946a8 | textbox | 3 phase |  |  |  | Voltage
42b33e22-8761-4172-a251-d810cc213e2a | checkpoint | < >
920f88bd-4ca5-51c0-b786-205434ba1666 | textbox | L1 - L2
3dffcb22-10cc-5a5a-b1b5-bf988e47fe67 | textbox | L1 - L3
c4e38d79-f30f-5478-a6bb-a9b78386f406 | textbox | L2 - L3
188bf26f-3405-5008-b286-97d74a8ef283 | textbox | Phase Rotation
916ce495-fb34-4f80-94ed-48aa8a66654f | checkpoint | RCD PUSH BUTTON TEST
8b215857-5a13-45c9-81ed-7cb8597362e0 | checkpoint | RCD TRIP TIME TEST
d4f1307d-d98a-55c8-b683-271ac0cbd69d | textbox | 0° |  |  |  | mSec
4b357f57-0431-563f-9d89-07dd6863f36f | textbox | 180° |  |  |  | mSec
8d4777c1-627a-47e1-a281-3d44b6d9b439 | checkpoint | Fault Loop Impedance - not required for RCD protected socket outlets
4bc000b6-0c85-58de-ac55-a40a1bb02584 | textbox | Ω
7d7380b7-e42a-4cf0-bd1c-d1f0208da027 | section | Section 2: Test equipment register
809138a2-0b88-4b00-8300-ca3895bdf550 | checkpoint | Test equipment register (1)
86054bbe-2373-5524-aab8-21ab8a4aa850 | textbox | Test Equipment Type
808aeade-7c34-5d9e-8637-f38af2821520 | textbox | Make/ model
4bf2ce02-b847-59d3-9a70-42b304229816 | textbox | Asset Number
5471c245-f389-5f6f-822e-54ca41d62551 | textbox | Serial No.
cdccbeca-cebc-5d87-9d12-46a04752ab9a | textbox | Next Calibration due
962121a8-b9f6-4e03-aca8-a9674a18e234 | checkpoint | Test equipment register (2)
83df334d-ab18-5f65-8c0d-4e48b77b79b2 | textbox | Test Equipment Type
17186ff0-2f44-5a06-8226-092d0824c808 | textbox | Make/ model
820045ed-b99f-5719-be69-e8e24600301e | textbox | Asset Number
e2f61bb8-82af-530b-993f-e11eaad4deae | textbox | Serial No.
2fed4206-0e96-597e-842a-8bac5756a3ce | textbox | Next Calibration due
af56d876-fa1f-4735-83a0-6092a579afb6 | checkpoint | Test equipment register (3)
a4f0a33a-f4b3-557c-87a4-d7d30d8c5a08 | textbox | Test Equipment Type
052b5c6d-ac1f-5440-a79f-6b8eee42a443 | textbox | Make/ model
82d32951-731f-527d-8497-78f6e7c1f3ac | textbox | Asset Number
922a5a08-c369-5846-bbdb-fdc223e557a9 | textbox | Serial No.
7f8d5673-6177-5a3b-baa0-f89c5708fb11 | textbox | Next Calibration due
8e20e6cf-20b2-46de-977b-1252abeb4764 | checkpoint | Test equipment register (4)
4e298dd9-d0de-5dab-bb39-61659e60d070 | textbox | Test Equipment Type
95cdbb45-36b7-5bd2-90d8-cb5cf010bee8 | textbox | Make/ model
d8fa7103-fc5d-54bb-8a15-0db786e24d91 | textbox | Asset Number
e9f5e24a-2931-5d34-ad6e-5b6f3b8da757 | textbox | Serial No.
7b406366-b95a-5454-a211-6556f31e13f7 | textbox | Next Calibration due
6128b278-39fa-4860-b9fc-6a6af7660983 | checkpoint-no-value | COMMENTS:
fb22c258-1d5b-57d0-a20b-20bc081aa742 | note | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
f7191344-3d86-4061-832a-66233b206fca | checkpoint | Signoff
f71e525a-b05c-43d5-9589-7f0efb6305bc | signoff | Signoff
491e66bd-e3a0-4c34-afbd-2a86f8614b39 | checklist | ITC 007 - Conduits In Slab and Walls |  | ITC 007 - Conduits In Slab and Walls
4081829b-0ba2-4e62-847c-7691eb0dda8d | section | Referenced drawings and revision number
9480018c-121e-41dc-af44-ca870cbd8276 | checkpoint-no-value | Details
763e61a3-cb3e-59db-be90-96c4cc8083e2 | textbox | Referenced drawings and revision number
d6851428-eb0e-4c88-ad55-1a8d251dbda5 | section | Section 1 - Inspection
6566a8b3-53cc-4198-a276-8595cf108bf6 | checkpoint-no-value | LEVEL / AREA
50e89f72-1ead-5eaf-97fb-e941cdf280f5 | textbox | LEVEL / AREA
a2f78223-64b2-4fc6-b097-2ed3f11e4834 | checkpoint | CORRECT DRAWING USED FOR MARKING OUT
278c9425-36a6-4b46-a91c-073e41c9555c | checkpoint | CORRECT SIZE AND TYPE OF CONDUIT INSTALLED
b4169892-00b6-4d4b-bebe-72b1216abafc | checkpoint | APPLICATION OF GLUE TO ALL JOINS AND BOXES
85b805a6-5767-40f1-9cf3-d2b8e24dd319 | checkpoint | SUFFICIENT TIES & CHAIRS ALONG CONDUIT RUNS
75c5a29b-558a-4e04-bb67-06ba602b40b4 | checkpoint | ANY VERTICAL CONDUITS CAPPED OFF
cfe87781-f9f3-4467-8e91-2f760135127a | checkpoint | CLEARANCE FROM OTHER SERVICES
89cee5e9-3c62-497b-acfe-3e79a180a653 | checkpoint | CHECK SUFFICIENT SPACING BETWEEN CONDUITS
09f00648-20d7-5140-8c75-6d031e484bf3 | note | Add photo
071b68cb-5bf1-4f85-9feb-892ffebd2852 | checkpoint-no-value | PHOTOS
66c2b4c9-cebe-5233-abdb-1a72669c8d24 | note | Attach photos
7f9a980b-336b-4c76-b754-96c282ef20c5 | checkpoint | CONFIRM ALL POINTS ARE LOCATED AS PER THE DRAWINGS
4b7c025f-62e5-412c-84dc-f51237ae973c | checkpoint | CONDUITS INSPECTED FOR BREAKS PRIOR TO CONCRETE POUR
08b322be-a018-456f-a4cb-98df22659cc3 | checkpoint-no-value | COMMENTS:
15827fb0-127a-503d-ae43-8c731010d9d6 | note | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
8f3ef438-70f4-49e2-882b-17abf5370e73 | checkpoint | Signoff
c533314b-f995-4ee8-9de7-317f7ddbc8cb | signoff | Signoff
f7277d7b-2228-459f-84fd-ee6d65fdd74b | checklist | ITC 010 - Inground Conduits |  | ITC 010 - Inground Conduits
653e7e0e-9413-4c5b-bdb5-8b82d5776061 | section | Referenced Drawings and Revision Number
f4944924-80dd-436b-a589-3f1474053149 | checkpoint-no-value | Details
8277e707-2277-538d-98d5-7796afcf6379 | textbox | Referenced Drawings and Revision Number
15a7602f-2e4d-43bd-9262-7326f40324e2 | section | INGROUND CONDUITS AND UNDERGROUND SERVICES INSPECTIONS
6ad5e47a-5067-4857-92c0-7505c1b0f5b5 | checkpoint-no-value | Description of Work Area
e8900b83-4192-59e8-b7b5-614f8fc0dac7 | textbox | Description:
8e14d1bb-6226-45d6-bbe8-5af18b2e6905 | checkpoint-no-value | Attach mark-up of work area
5f46909f-7c94-4758-8da7-7ec98a202701 | checkpoint | Investigation of Existing Services Completed, including review of existing services documentation & BYDA drawings and service scan
ea860d72-5f00-4ae4-9e64-66d1d964edad | checkpoint-no-value | Validation of Imported Material undertaken as per RAP requirements. Upload material validation certificate.
bb5d3356-b427-439e-b230-2c2bd875ac88 | checkpoint | Set-out inground conduits, pits and any other items in accordance with the IFC documentation ahead of commencing excavation
31ba68c0-f6f3-4202-afc6-723b39920dce | checkpoint | Excavate to design levels. Check that minimum cover requirements are achieved (650mm minimum cover for LV & 300 for comms).
616339dd-e6ef-4a65-bb6b-d556c4cd7b15 | checkpoint | Inspect trench and ensure it is free from sharp materials
93ea2d56-6bfe-401c-b48a-f8579d8ec82b | checkpoint | Place bedding sand in bottom of trench. Check that 50mm bedding sand is achieved.
7e988a67-26e5-4a7e-994d-3ac091f75413 | checkpoint | Place conduits, glue and pull through draw wire
73422594-5caf-44be-80ec-fa2b33c41920 | checkpoint | Verification of correct conduit sizeas per IFC documentation.
dd158023-94d4-4981-8117-17181b526aeb | checkpoint | Take photos of conduits prior to backfill.
368831de-c9bb-461f-ac96-6842bdcf203a | checkpoint | Surveyor to survey conduits prior to backfill.
e42873b5-26b5-4997-8fd1-f7ef22645667 | signoff | HOLD POINT
128576e6-50bb-479f-afec-392093fa9a8b | checkpoint | Principle contractor to inspect conduits prior to backfill.
d4f387fc-c5f7-4158-a164-8095f6cafa65 | signoff | HOLD POINT
5343f3a7-9df6-4247-9744-32cdddb998c9 | checkpoint | Place and compact sand to 300mm above the top of conduits.
03675d18-147a-4a98-bcc0-b74f126a6ea8 | checkpoint | Place warning tape.
bcb8f97b-7062-4b68-8dd7-ba4a28b9b11a | checkpoint | Place and compact suitable material to remaining depth of trench.
eb1fd9b4-2a98-4482-a591-475e8d4527fe | checkpoint | Undertake compaction testing per the civil documentation.
a4e374e8-9865-47a9-a858-9fa2fc79d717 | checkpoint | Pits cleaned and free of holes. Refer to ITC 10A
91894598-22f0-45ba-8f4c-4632275c1539 | checkpoint-no-value | Attach as-built survey
c5e368fb-8aad-4fc2-9f47-c98083727b2c | checkpoint-no-value | Attach any other relevant items (optional)
9bc62323-cb8a-49ff-ab1b-124db2eaffe4 | checkpoint | Grid final acceptance - Foreman or higher
8a35b1d8-315c-4585-8bce-86360c27e359 | signoff | HOLD POINT
d5aea051-47be-458b-8630-97d5da93eca8 | checkpoint | Client to review completed ITC and confirm acceptance
819b65b7-8315-43ef-a0d7-a79fdb5f1cab | signoff | HOLD POINT
af6ef55c-b14c-40eb-93ed-addc208c7613 | checklist | ITC 010A - Inground Pits |  | ITC 010A - Inground Pits
3212c14b-cee3-4e7a-9489-9fac4234278b | section | Referenced Drawings and Revision Number
458b8b8a-40f8-47f7-8f1d-64ad7f29170b | checkpoint-no-value | Details
f5bd0caf-85e9-594d-af0f-2bc62d29d936 | textbox | Drawing and revision number
72bb4e79-5c0c-4086-a751-1b840173e929 | section | INSPECTION AND TEST RECORD FOR: INGROUND PITS
eb1a221b-d231-4ec6-85a8-7e879243d2c5 | checkpoint-no-value | Description of Work Area
856f34f5-c905-5d12-9de1-05c4a7093558 | textbox | Description:
a8ab8a0d-c738-46a6-b453-cf94b7f6b5ec | checkpoint-no-value | Attach mark-up of work area
a3f02e3b-6330-4f69-a3c6-011893916a63 | checkpoint | Set-out pits and any other items in accordance with the IFC documentation ahead of commencing excavation
1a070df1-4ae5-4b8b-a79b-af27b49e6607 | checkpoint | Excavate to design levels.
31ee27c9-1061-4d4f-b4d4-b4323d074412 | checkpoint | Ensure Drainage Holes are provided on bottom of pit
1db6d5f5-af2c-4cd3-89b7-a2df747a58cb | checkpoint | Ensure connected connection to Stormwater System where applicable.
07f96660-15cd-48a6-b315-c582242842c0 | checkpoint | Place bedding sand in bottom of trench.
889c5d0d-dc56-5adf-b662-c976a6dd94f1 | note | Check that 100mm bedding sand is achieved.
e798f0da-31bd-45a1-b6e9-951c9c465bdb | checkpoint | Place Hessian Underlay above
ee261dd1-892e-4582-84ed-71d7bca59839 | checkpoint | Place Gravel above Hessian Underlay .
646e1d09-200c-585e-86a8-f053ac0579ed | note | Check that 150mm gravel is achieved.
3f92216e-59f8-46cf-b1e9-d11679aa9112 | checkpoint | Install Pit ensure levelled to correct RL
d4585cdb-b30c-4fe0-9f75-82680544a61c | checkpoint | Take photos of pits prior to backfill.
201c75d3-6166-50bc-8034-995fa11ed69e | note | (Upload separately below).
c2ec1325-9207-4b5a-a1ef-56ac242c17fc | checkpoint | Client to inspect pits prior to backfill.- hold point, email
4cde0a7e-b1f5-4253-8407-9b2195a1a67f | checkpoint | Place and compact suitable material to remaining depth around pits inline with manufactures data sheet. Hold point, email
54938bf1-9a32-4111-b185-d3054350c23a | checkpoint | Pits cleaned & sealed
384a8d32-7e2d-4209-96d2-df28a91d7659 | checkpoint | Ensure Pit Lids are clearly labelled with service type
7ebe3d02-4911-4502-9c47-fca8b71143fc | checkpoint-no-value | Attach photos of conduits
22f92548-4181-404d-80ec-e4427de846a9 | checkpoint-no-value | Attach as-built survey
ab3ac4b0-444f-43ab-ae8d-3e19646d1265 | checkpoint-no-value | Attach any other relevant items (optional)
96e24ecd-a1f0-4e59-8287-f9e0f89c9b4d | checkpoint-no-value | Client to review completed ITC and confirm acceptance - final acceptance
9638d819-2c41-4e16-8ec1-3169ffcb2b9e | signoff | Client Final Acceptance
30acc8fa-f0c5-4774-b035-8d8625754460 | checklist | ITC 012a - Earthing & Bonding |  | ITC 012a - Earthing & Bonding
c1e919c0-4cc8-4632-93ba-cd0157ce8b19 | section | Referenced Drawing and Revision Number
df10a991-3264-44e2-9bde-75df6db334d5 | checkpoint-no-value | Details
fd9a5937-d6e2-58e9-a175-f643ac0d8dd8 | textbox | Referenced Drawing and Revision Number
2fed4073-e98f-4d5a-9fc6-04a5f186ec01 | section | INSPECTION RECORD
3a021c5c-9413-4b6e-94b5-854763f7ad39 | checkpoint | Approved construction drawings available
853fffb1-cc64-59f0-b33e-a1ba8dfd5cf4 | textbox | Origin of Earthing Conductor
bc5fa5a4-6a6d-50db-8df0-484adb0fae1f | textbox | Reinforcement bonding point installed to
dab1cd2c-0680-415f-8dd5-753537bd9577 | checkpoint | Earthing cables secure to wall
559c30df-96d6-4be3-99e6-c177bf31ce20 | checkpoint | Size and installation of Earthbar as per design
a77c9b61-3243-4b9c-abff-581d121611e7 | checkpoint | Earth cables torqued and marked at Connection points
dee8d400-0e17-4e71-8f37-99189f695aa1 | checkpoint | Earth cables labelled at Connection points
726a0a21-a747-4293-9e03-b312dde3e2e0 | checkpoint | Bonding conductor complete throughtout rooms
c32e6be0-605d-4dcc-86bf-44b542806fe1 | checkpoint | Bonding of equipment complete throughout room
8e455d5d-f4b3-5fdc-b042-0b2036968dce | textbox | Reinforcement bonding testing complete, results recorded
b199b97a-a2fa-5183-8dd7-b16b09240794 | textbox | Bonding complete for earth bar (test results recorded)
f1c42790-6e69-4d2c-952c-e8e0bba2e2ba | checkpoint | Final Test report suppled and available on site data
946abf42-008f-45a9-9eb5-785fb3f3fbbd | section | BONDING CONNECTIONS
6ad38b3e-f8cb-4e6a-9e89-22e3adb2b5f8 | checkpoint-no-value | Details
5f04528c-0666-5b44-8fea-5bb49126dc58 | textbox | BONDING CONNECTIONS
f8a8dd1a-664c-4019-a905-959141a63b91 | section | TEST EQUIPMENT USED FOR VERIFICATION
2c523baa-ef2e-41ff-b8fb-df37386b5156 | checkpoint | TEST EQUIPMENT USED FOR VERIFICATION
db9bcbd0-9926-52ec-a89f-bb88d6c02bbc | textbox | Test equipment
e1276265-27ef-54dc-9003-e3a95a6321fe | textbox | Serial No.
4434b1c0-af18-5f3f-9c74-de8034eea8dd | textbox | Calibrated on
ea78378e-3772-474d-8f04-9efb08d3d4d5 | checkpoint-no-value | COMMENTS:
7ebb3bdc-a7dd-544d-8bd2-c49e7205a8d3 | note | The electricains noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the inspection/ test was completed.
7f1d46f1-6524-478c-abd5-990ca2321163 | checkpoint | Signoff
40c99127-7226-4ff7-b4b5-9d0aab20c561 | signoff | Signoff
9346cbe2-d830-48d9-9c1a-f9287875a315 | checklist | ITC 015 - Cable Containment and Seismic Restraint Systems |  | ITC 015 - Cable Containment and Seismic Restraint Systems
d9a97776-6f06-4419-b3b0-0f50823a11a4 | section | Referenced Drawings and revision number
b04d7554-2b1d-48bd-911f-dcdaa4744575 | checkpoint-no-value | Details
e1051e25-642b-517c-8dbc-74b2fcec519e | textbox | Referenced Drawings and revision number
fbbcf968-ff37-4d5b-ac99-53aabf2e83e5 | section | Section 1 - Visual Inspection
769416e4-a477-4d24-9f10-f0c5c6323bc0 | checkpoint-no-value | Details
38a17611-ca93-5393-8e5f-86064b7517aa | textbox | LEVEL / AREA
ba56588c-1966-53ac-ba86-77739c58cb20 | textbox | DRAWINGS USED - REVISION
f95b2042-c5dd-48d7-b805-fce48fa01858 | checkpoint | TRAY/BASKET CORRECT SIZE FOR APPLICATION AS PER DRAWING
05940b43-b63c-4b9d-b5db-1071fceb9f33 | checkpoint | CLEARANCE MAINTAINED FROM OTHER SERVICES (IF TRAY MOVED, CONSULTANTS NOTIFIED
2405061d-40c3-4dde-b06b-a9179d3ed2d4 | checkpoint | SUPPORT HARDWARE SPACING ADEQUATE OR AS SPECIFIED BY THE SUPPLIER
2e2fdabe-8809-4fa4-b915-ec4125d991ca | checkpoint | TRAY/BASKET FREE OF SHARP EDGES AND OTHER DEFECTS
f604c933-5b32-4db1-9032-86f507991cda | checkpoint | EARTHING REQUIREMENTS AS SPECIFIED HAVE BEEN INSTALLED
4e23ac14-b6ee-4ce2-9543-57bad7a57f8e | checkpoint | TRAY/ BASKET READY FOR CABLE INSTALLATION
5f8c54cb-6a2c-4d52-8b83-30fba570c2da | checkpoint | SEISMIC RESTRAINTS INSTALLED TO SUPPLIER SPECIFICATION
68b6806e-a2d6-430d-98de-9e7fab52b926 | checkpoint-no-value | COMMENTS:
a74c4b47-5463-5651-bf9a-8c4738e233ae | note | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
664bf883-c216-4184-b2b2-288f13cf9e60 | checkpoint | Signoff
78a07d7b-c284-4df1-acae-39ec43c8a6e8 | signoff | Signoff
025b2c4d-bc03-4b18-aa27-fc8378d4923a | checklist | ITC 018 - Lighting Lux Levels Test |  | ITC 018 - Lighting Lux Levels Test
1cc9b2b5-310d-4642-a957-b4faafc69e39 | section | LIGHTING LUX LEVEL
c05c9a51-cef9-4a4b-948f-560fdc77269a | checkpoint-no-value | Referenced Drawings and revision number
42c7b858-14d7-5d1e-b064-36a5e7e2d19c | textbox | Referenced Drawings and revision number:
a2ed7943-4acf-4d0a-bb5f-5d17538afe44 | checkpoint-no-value | LIGHTING LUX LEVEL
22094515-6012-5f87-a792-23c7637d159e | textbox | Room Name / No.
d74a05ba-1b62-5c49-8129-321ef0b3b5c4 | textbox | Result Position 1
dbb2f03e-df57-5711-96bf-1da3594f1ca2 | textbox | Result Position 2
adeda1cc-8a45-5339-82a3-465958b492dc | textbox | Result Position 3
d2fa2701-d4a6-5991-91c8-1db04334c5d9 | textbox | Result Position 4
70405f9a-112d-51e1-91f7-e937015eb9fc | textbox | Result Position 5
af41fba1-b949-531e-998c-09094adab49b | textbox | Average Result
d36de59a-67fc-5596-8b2c-f19bef9a1dc8 | textbox | Required minimum result
eb161b46-0aa2-5b5b-8a1c-f20b3b99fbaf | textbox | Time Taken
3568de78-be8c-4bcf-9d81-1dc5be2c48d3 | section | Recommended Illumination levels***
81896167-48e9-4184-bd87-f8348353bd33 | checkpoint-no-value | *** Based on measurements taken at the actual working areas, measurements need to be taken at several points and averaged to gain a accurate overall reading.
35c49da7-30f0-40f9-921e-adde077382c6 | checkpoint-no-value | (Location) specific location
c1248e83-de1f-5442-873f-414a1030062c | textbox | (Office) Conference, reception room |  |  | Min. lux: 320 | Min. lux: 320
7f1120fa-f7f6-5865-9fc0-642402489c89 | textbox | (Office) Clerical work areas |  |  | Min. lux: 320 | Min. lux: 320
4ef761d3-0599-5329-bfc5-61eac3e5148f | textbox | (Office) Typical drafting areas |  |  | Min. lux: 600 | Min. lux: 600
73c50c00-4f7b-5dbd-8b11-1cdc73a96ef4 | textbox | (Hotel) Public room, Cloakroom |  |  | Min. lux: 160 | Min. lux: 160
b8de4087-0458-5946-bd23-233aeb59a7cf | textbox | (Hotel) Reception, Cashier |  |  | Min. lux: 160 | Min. lux: 160
97e5c6fa-50ab-5e4a-8f38-0ada6af06bbd | textbox | (Factory) Packing work, Entrance Passage |  |  | Min. lux: 160 | Min. lux: 160
7ee13c75-520c-5feb-b219-86704acf6a4e | textbox | (Factory) Visual work at Production line |  |  | Min. lux: 240 | Min. lux: 240
f159c0ab-232d-5985-a053-70aa886abb60 | textbox | (Factory) Inspection work |  |  | Min. lux: 400 | Min. lux: 400
5ce3127e-0190-5d26-90c9-ba1d6dd2eeac | textbox | (Factory) Electronic parts assembly lines |  |  | Min. lux: 600 | Min. lux: 600
e03bdbda-5aab-530c-ada6-1f61891d0755 | textbox | (Hospital) Waiting room, Warehouse |  |  | Min. lux: 160 | Min. lux: 160
e368d7d0-63ec-597d-88ef-fd755046e75b | textbox | (Hospital) Medical examination room and Operating room |  |  | Min. lux: 320 | Min. lux: 320
a9ca9bd7-3962-5e67-b0fd-598d2e457c0d | textbox | (Hospital) Emergency Treatment area |  |  | Min. lux: 800 | Min. lux: 800
a44279e4-f1ea-5acc-a3aa-da38ec6337b9 | textbox | (Schools) Auditorium, Indoor Gymnasium |  |  | Min. lux: 160 | Min. lux: 160
adc82acc-34a8-54f2-9521-d71d39748d2c | textbox | (Schools) Class room |  |  | Min. lux: 320 | Min. lux: 320
647eab6e-3503-54d1-b9a0-ef50a3e39cd5 | textbox | (Schools) Laboratory, Library, Drafting room |  |  | Min. lux: 600 | Min. lux: 600
fd49a582-c6b4-4d49-be13-e446afb89614 | section | LUX MEASUREMENT DEVICE DETAILS
edfbb0be-4da7-437d-a583-e4068a964f93 | checkpoint-no-value | Details
a1b62935-83b8-5f2f-9f07-2646fc3c5dd8 | textbox | Make and model
99c3946d-0313-5e98-827d-d60cdd9c83d7 | textbox | Serial
f30980bf-bb83-5895-816a-f6465be49cf5 | textbox | Last Calibration
b413ba2b-46cc-4cd5-842f-a51594292279 | checkpoint-no-value | COMMENTS:
9b93cb2b-b30d-5f95-913c-2a7fe8f965e3 | note | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
4dbcab85-dea8-4fea-92f4-94cf0efe447d | checkpoint | FINAL ACCEPTANCE:
7ce4a356-c01d-4bea-b45c-ad1b4ef500ea | signoff | Signoff
9f963508-ca91-4525-81cb-be861a264f18 | checklist | ITC 019 - De-Energised Isolator Circuit Breaker Functionality Test Main Switchboard |  | ITC 019 - De-Energised Isolator Circuit Breaker Functionality Test Main Switchboard
d89348ec-4f34-413b-a412-da49df4c0409 | section | Referenced Drawing and Revision Number
70672f46-6fb2-4455-8dff-303f6de64ab5 | checkpoint-no-value | Details
391a66fe-7c44-54f6-9eca-b101e0ca9581 | textbox | Referenced Drawing and Revision Number
8469d480-ce0b-449f-8432-742f7410bd3a | section | Inspection Conditions: Ensure all steps are completed in order
64acad42-ab83-487c-b620-8b605fcb4de0 | checkpoint-no-value | Details
66b76815-5663-5adb-8115-53815b3cb815 | textbox | Equipment number:
83188907-49e1-52be-b32c-c29ab4b94c04 | textbox | Rating:
c5391714-35de-52b6-b36d-d5c35222bbb9 | textbox | Type:
da03f2ca-daec-5e14-a6f8-79b196582717 | textbox | Manufacturer:
a3e23594-805f-55bb-a2dd-ed6a19e57452 | textbox | Interlock type:
5b9af467-2490-438b-a60f-b915162a3377 | checkpoint | STEP 1 - Open cubicle and undertake a visual inspection
6319fe9e-c233-47d7-a82d-bfc2e62d3f3e | checkpoint | STEP 2 - Verify the settings against the single line and the cubicle door
9ad62fd3-ce3c-4ad3-bf7c-9f40d868ccb0 | checkpoint-no-value | STEP 3 - Verification of circuit contacts in Closed Position
c04f3eb8-0a97-5799-b25a-a48f6ee4d9d7 | textbox | Switch Closed
066c2bcb-5997-4f94-8720-c48b2f86e517 | checkpoint | A to E
d01adc7a-8f85-4380-ad90-4c86e979d618 | checkpoint | B to E
712557dd-6516-46fb-a290-3d183165ba5f | checkpoint | C to E
bf3d5b20-3447-4901-b333-f0a0ecd04439 | checkpoint | A to B
220126e7-fe9a-4aee-a984-7b7725eb3779 | checkpoint | A to C
a348d6ce-ae8c-4427-a3cb-c721a2f89223 | checkpoint | C to B
64d0662b-9dd3-4fe4-87c7-6ab983aa20fe | checkpoint | A to A
44bfb003-4647-491c-b13a-2e2a20fe5517 | checkpoint | B to B
0a7cd422-8a99-453f-8a98-da63e9c4082f | checkpoint | C to C
2dc3c480-29cf-4679-b2eb-680825d86468 | checkpoint | A to N
54d768f6-1922-4071-b637-e568f0ed995d | checkpoint | B to N
9a86424c-1584-4abb-ae85-a7e7b1a7cb9e | checkpoint | C to N
72775f13-5d8f-4c02-95c3-913df24e8077 | checkpoint | N to N
114737a6-5967-4691-8dc7-64f0774ccc9b | checkpoint | STEP 4 - Verification of circuit contacts in the open position
b65558c4-824b-409b-8443-a93de4327210 | checkpoint | STEP 5 - Visually confirm the door interlock is in the open position and immediately close the cubicle.
ab907eb3-8cbb-4e4b-94a3-a397d0e95c9d | checkpoint | STEP 6 - Re-confirm the operating mechanism in the open position.
f0b18e7c-a547-4159-a61d-c18be65945a9 | checkpoint | STEP 7 - Prove operation of the interlocking device.
49a4fb09-4a30-4ed2-9997-b8de83079c87 | checkpoint-no-value | STEP 8 - Document the status of circuit breaker.
f981738b-7717-56f6-b4c4-35ffb522bded | button | Status: | Open,Closed
a429a21b-d249-47a6-8277-b228e922c3e6 | checkpoint-no-value | Equipment Details
33d40d63-5f74-5701-8b64-c605b3b549fd | textbox | Test Equipment Type
889e00fd-a9c8-51da-92f4-8cd7b70a778d | textbox | Brand/Model
ff812773-3b1c-560c-ba17-abb29304680b | textbox | Serial No.
af70a4da-8cda-5ccd-a348-60b4d2ef91b9 | textbox | Calibration Due
263bec92-538a-46a6-b9e1-9b78a219a61e | checkpoint-no-value | COMMENTS:
a0ee1c87-fc69-5e1c-b745-8e11ce2c7a7a | note | The electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the above inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the inspection/ test was completed.
683016f5-0a52-4f53-bbfa-f7847bf981c5 | checkpoint | FINAL ACCEPTANCE: Foreman or higher
c1f4805f-a1f2-4d69-be50-a51061be36a6 | signoff | Signoff
a991b5c5-83f5-457b-b020-12db2dc902e5 | checklist | ITC 020 - Wall and Ceiling Rough in |  | ITC 020 - Wall and Ceiling Rough in
381c2a9b-b5e7-46ea-8ee4-60abc534f5d9 | section | Referenced drawings and revision number
7da3cb25-7996-4415-b85c-afa4d950e048 | checkpoint-no-value | Details
cee259ad-0187-53e4-a789-3937008bff51 | textbox | Referenced drawings and revision number
561b3346-8bd9-44d4-9341-7dae900deac6 | section | Section 1 - Inspection
509ffbb5-d278-484e-ba73-d499e90157e1 | checkpoint-no-value | Number of points on the circuit
0bc89870-5c7b-5a1d-a312-103e3d6e8683 | number | Number of points on the circuit:
4871d447-af5c-4a41-b3d7-2064203b9916 | checkpoint | Is the circuit complete
cc7ae867-5e74-41d2-bbdd-9edc6e62ba52 | checkpoint | Power cables installed in correct location
3d873264-be36-420e-9f58-cc3b502a67d0 | checkpoint | General and Emergency lighting cables installed in correct location
6672b680-eadb-454d-b628-f9f3d1a35bdc | checkpoint | Lighting control cabling installed in correct location? i.e. Darli, Cbus
cbde6462-5f82-42bb-974a-ddee6afb07f5 | checkpoint | Segregation of services maintained
68dd2fbb-6d10-45f3-a12d-6bbd61c17591 | checkpoint | Penetrations sealed - Fire proofing completed
cf0dbaf3-2b07-4d9f-87cd-932476f2be53 | checkpoint-no-value | COMMENTS:
9d3cd487-522c-559c-b7af-06f26fedfd81 | note | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
b4dafa9d-319a-4881-b2b4-263a9c342135 | checkpoint | Signoff
33e65b11-b5e6-4461-8c7b-19533c6f1fcd | signoff | Signoff
df0b9b84-9d9f-4fa2-9391-37dacff7631e | checklist | ITC 030 - Distribution Switchboard Installation Checklist |  | ITC 030 - Distribution Switchboard Installation Checklist
2f65c489-fefd-484f-bee5-ca66daf104d4 | section | Section 1: Installation inspection checklist
d4df36fd-1ace-4b69-8721-efe7f63d46d3 | checkpoint | Current approved workshop drawings available on site database
4e7091f7-a9db-4107-9eb8-27e1e9ace62d | checkpoint | Switchboard installed in final location as per approved drawings
759e609f-7632-4de1-bcb0-1f50e60744d5 | checkpoint | Confirm labels are correct
a98fd0cf-9bba-4b48-a99c-4a86f642479f | checkpoint | Confirm each cubicle is free from dust and foreign debris
6940ca9e-0c82-4b60-b3de-1b98b8a811e7 | checkpoint | Confirm door seals intact as per approved shop drawings
dddc7f9d-3a55-4ace-9e5c-758566285269 | checkpoint | Confirm door handles and hinges operate correctly, confirm locking
998fcf48-f942-410e-8116-0b593975b6cd | checkpoint | Confirm Earthing connections are installed
b38e01db-078e-4aa1-a944-909c919508cb | checkpoint-no-value | (Switch Closed) Undertake functional testing of all main isolators:
a439bf7a-2a69-55ed-8021-2f2acc226696 | textbox | Switch Closed
bcfd2c51-64ab-4fc7-9a7b-516a1300c61a | checkpoint | A to E
e740fc1d-2e99-4665-9945-887feab22ed7 | checkpoint | B to E
84e90c7a-3280-4a28-bf5d-305722f84f93 | checkpoint | C to E
b473e211-257d-4de8-994a-0e1e1732a882 | checkpoint | A to B
6c9b499c-c100-4d94-8a83-e4ab6493b41c | checkpoint | A to C
5e7217e9-bda8-4b75-9a55-2a674096f421 | checkpoint | C to B
e6190229-66dc-417f-af4b-9554482ef88d | checkpoint | A to A
894f4a05-9679-4d13-9ccb-11b822bedf36 | checkpoint | B to B
8cb821eb-f55b-4846-ad61-48197a86384f | checkpoint | C to C
de615d37-998c-4343-af92-9294938260ef | checkpoint | A to N
50be5cd1-3c2c-4aee-aadb-8b176c7187e3 | checkpoint | B to N
1c70e30c-c948-42b6-8e57-d6a34f004325 | checkpoint | C to N
2eb654ae-3a54-4e60-826f-9d51555e1b5c | checkpoint | N to N
4ac0d7ef-d4f6-40a6-bed9-20537b89bc9a | checkpoint-no-value | (Switch Open) Undertake functional testing of all isolators:
f1884aba-a1e1-53ef-8147-e0eee37a256d | textbox | Switch Open
36a7db8f-7f02-4b15-a763-9c139ceed0ea | checkpoint | A to E
402c7c7c-107e-4756-a3a5-704b1783eae0 | checkpoint | B to E
1e2f6150-0259-4b56-93af-1109b61437f0 | checkpoint | C to E
b060d55c-7986-49a4-a237-e87acc9cd40e | checkpoint | A to B
4ce3a82f-2610-4253-ba50-f83c63b254d1 | checkpoint | A to C
1774cd0b-b0f9-42ef-acb1-f10be0dabcc9 | checkpoint | C to B
c3798a6e-ad4a-43bd-aa46-d4a7bcc79a59 | checkpoint | A to A
758b82b5-8a2f-47d8-ae8c-796e4d168b3a | checkpoint | B to B
618a1007-b88d-4653-a05c-135c42b7ddb3 | checkpoint | C to C
67591584-4161-4962-99ea-676a90fe3723 | checkpoint | A to N
1dcaf346-6cc8-4d1a-a27f-b42a9f8aa0c7 | checkpoint | B to N
55f78ade-fe9b-4e1f-97a1-770037f0c80a | checkpoint | C to N
17f55b6b-5429-4dc4-b214-38b3fc8c280c | checkpoint | Terminations are tight and correctly tensioned with witness marks in place
a97f9b26-6bee-46ed-91a4-7cd68f9a71f1 | checkpoint | ITC 005 complete and submitted
bb4ab2ad-e7f5-45e7-80d5-b5455a1abcad | checkpoint | All subcircuit breakers are securely mounted and installed with locks
d5c30017-24d1-4a51-9cd2-ce00a900dfe3 | checkpoint | All subcircuit cabling is neatly tied and secure in switchboard with no visible damage
6ebaa146-0b11-4899-97c3-e9f2d8e5e701 | checkpoint | Currently terminated subcircuits are tested, verified and labeled with up to date drawings and documented on ITC 006
67602158-5d29-4fe1-98e9-5273ad26d06c | checkpoint | Photos taken of all cubicles
dcd96a96-223a-50b1-904e-059879272560 | note | Attach photos
c7750185-ade6-4f59-a00b-cc4bf5210f2c | section | Section 2: Busbar insulation testing, all results less than 1MΩ is classed as a fail
9014578c-ecf7-482c-b679-63698d3a77fa | checkpoint | L1 - EARTH
bdb33f95-9893-523b-933e-89fdd9a5b35d | textbox | MΩ
c1626b18-be7d-4e7e-ba13-376f7f672974 | checkpoint | L2 - EARTH
684b6eaf-f80b-53bb-bec9-cbc638b27290 | textbox | MΩ
3c8679c7-617e-41e2-acd9-98139677c4b5 | checkpoint | L3 - EARTH
a9282a52-b6c4-57f1-bc18-33f898559574 | textbox | MΩ
a8bf1c45-f0fe-4188-b6cd-41aa5df87663 | checkpoint | NEUTRAL - EARTH
0dce8013-5c04-59dd-bcc0-7041efbf1054 | textbox | MΩ
e0a0f81f-850f-4bd9-953c-395f07e2fbc8 | checkpoint | L1 - L2
b9d66344-ea4c-5da0-b3d9-4f8572da8bad | textbox | MΩ
8b58c595-6d4e-418b-b637-aca0dbcc7442 | checkpoint | L1 - L3
07ea6fc9-040b-53e5-84e1-95e586655399 | textbox | MΩ
7987d5f2-18e4-4c95-b583-3ec422b7623e | checkpoint | L3 - L2
a210e1b5-233b-5072-af3b-7e33935d24f1 | textbox | MΩ
de37316c-5eb6-4ea3-aa53-46a312796491 | checkpoint | L1 - NEUTRAL
973fad02-00e6-51e0-a65c-5596090abe9f | textbox | MΩ
fcfd9ddd-db79-4b88-a644-ef188ba22f6d | checkpoint | L2 - NEAUTRAL
7593cb39-b04c-52cf-9ec9-2ddc5c1464c9 | textbox | MΩ
d7a832cd-06c2-4dba-8340-9ebbcc791ad5 | checkpoint | L3 - NEUTRAL
411d193b-268c-509c-9877-2307c2dfb57f | textbox | MΩ
d48e0a9c-aa30-4944-8b09-cff7df1d988f | checkpoint-no-value | Equipment Details
5851c1d0-252a-54ac-9855-b2f9508c2cb2 | textbox | Test Equipment Type
bf8f210e-18c9-533c-82de-6f1edd7491ac | textbox | Brand/Model
17a1bfba-d843-5b65-895f-41bb649f4081 | textbox | Serial No.
5f0f9759-957c-50eb-a1c4-8fc22e83f902 | textbox | Calibration Due
5ab69315-9c8d-4095-b846-0584564b42cf | checkpoint-no-value | COMMENTS:
53b97f6e-d8ba-57a9-9a3e-6cc846883a18 | note | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
1dc08157-42a8-4e7a-a0eb-9fde6b0a7bba | checkpoint | FINAL ACCEPTANCE: Foreman or higher
f0822cee-b2d1-4b52-8183-5f6b1764fa91 | signoff | Signoff
17a57eec-38f8-488e-ba71-6c5dd53e319a | checklist | ITC 033 - Low Voltage Fit-off of Final Sub-Circuit Equipment |  | ITC 033 - Low Voltage Fit-off of Final Sub-Circuit Equipment
af015562-9c6c-405a-ab95-3aa4cbaa1458 | section | Referenced drawings and revision number
60e2235c-258a-4db9-82dc-967e2ff35cb8 | checkpoint-no-value | Details
522db14d-387a-572b-8729-214e98756980 | textbox | Referenced drawings and revision number
4e59a548-0a7a-43b1-9c16-d88fd83f1e0e | section | Section 1 - Inspection of electrical equipment and accessories installed
9c5fc012-e61f-4bc9-8763-7827481c29de | checkpoint-no-value | Fit off inspection
3da7450a-d501-5c1d-94fc-9401c78f5b35 | textbox | Number of points
17d3f6e4-7972-4210-aff7-d815d3c05feb | checkpoint | Installed in Correct Location as per drawings
c89b1de9-28c7-49c4-b647-7ab9333aec18 | checkpoint | Has lighting control been installled in correct location
f0535e0c-5ffb-403e-bf46-ba6d7f9995d8 | checkpoint | Has the correct equipment i.e. gpo, light, been installed as per the drawing
34ddc6ea-96a5-4710-9d90-9fe14213279a | checkpoint | Fit off into Electrical Equipment or Field Device - no unterminated cables
c84bf038-3106-4d5b-b333-ddba5b648e79 | checkpoint | Mounted Correctly
4c118fbf-546c-4a32-be1c-9e7b08f79ad3 | checkpoint | Area left clean and tidy
d2382d2d-41b5-49c1-9e7a-3dd3791b2c51 | checkpoint-no-value | COMMENTS:
44edf5a1-984f-53a8-8604-cf4367b708b6 | note | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
97b5632d-391f-471f-b76f-f2bf0275577d | checkpoint | Signoff
5a23f972-8255-4953-880b-7dca090bcac5 | signoff | Signoff
8e7b5369-8b7d-4e2d-aa1e-7662b2de0e2c | checklist | Upload CCEW Attachment |  | CCEW Attachment
9eb3019c-517b-475f-82b1-17a146c1cca9 | section | Details
0b4dd643-c271-4c6e-9469-a55b1f9a68ba | checkpoint-no-value | ATTACHMENT:
acbf1ce2-f774-4d7a-b0a0-d848eab990a2 | checklist | WHS-PRO-041 F-03 Construction Switchboard and Wiring Checklist - 6 Monthly |  | WHS-PRO-041 F-03 Construction Switchboard and Wiring Checklist - 6 Monthly
c9fa3416-6acd-400b-b97e-aeca8efe2864 | section | Details
013d1e3d-5595-4198-9e75-498fa410aa87 | checkpoint-no-value | Details
a077c624-1cd2-5666-a3af-be2e2e5bd874 | textbox | Tag Number
ec5f675f-190f-51e2-93c9-2d2f9d8dc59e | textbox | Construction Board Location
bbafae91-d1ab-5715-9c1b-acd25b1c22d4 | textbox | Fed From
1b72b5fc-c205-461d-a2e7-7e50a3e61f5f | section | Section 1: Switchboard/ Load Centre
617f35ef-7930-40e6-a315-3cc17e56fa2f | checkpoint-no-value | Construction Switchboards complete ALL check points, Load Centres (lunch shed, site offices etc.) complete noted check points only.
5e2928d9-bad0-49cd-b83d-9158bb75805e | checkpoint | All electrical equipment and lighting/ power supplied from a 30mA RCBO
8cb96d72-21fc-5a9f-8f78-2444be0ca178 | note | Load Centres
81730cf0-4b57-4ab8-80cd-e949b6ec38b3 | checkpoint | Readily accessible, i.e. not obstructed in any way
e57df476-94a7-5e63-9689-37ed7e9922b4 | note | Load Centres
746e52ca-2003-4ae2-8bb0-c9e2f57b889b | checkpoint | Robust construction with a minimum IP23 rating
df4c8f8e-ebad-4f11-9f1f-715034bf9f51 | checkpoint | Complete operational checks of all RCD’s i.e. push the test button
94412fe3-8890-5aeb-9592-332f00324d5a | note | Load Centres
615632a2-0dc1-4d98-bf0e-ab6c60445180 | checkpoint | Spider boards are not exposed to the weather
cf3b8570-56f8-4ea0-972b-7cb2c8c41212 | checkpoint | Live components are effectively protected (check pole fillers)
924b02f2-eb4d-596f-b657-16dca28284c8 | note | Load Centres
5862117f-8d0a-4114-9502-6c0da8397a39 | checkpoint | Insulated Tie bar has been fitted for flexible cords
716144bb-636b-4b60-8a5d-7e2bf0bd2c33 | checkpoint | Switchboard/ Load centre door is lockable, non-removable without a tool and fitted with a retention device to stay in the open position
2f31148b-10ab-5aa5-91b9-b32b3fa94bca | note | Load Centres
5b516584-9c2e-445d-b500-39ea06c53b95 | checkpoint | Mounting is secure and stable including secured to the floor
2f116294-7bca-5369-a4e8-9f1041b2c54f | note | Load Centres
5b254852-58bb-4d67-b0bc-2a5cf196dcf9 | checkpoint | Where there is more than one breaker, marking provided by means of number, letters or both to distinguish one from the other (unique ID)
371afaae-930f-5eaf-a703-680e5ff28740 | note | Load Centres
1180d76e-33b4-4b85-bd76-deae4f363058 | checkpoint | Marked with appropriate signage such as “danger 240V / 415V”, “lightning bolt”, “source of supply is identified” and” Keep Closed- Run all leads through the bottom”.
15310cbf-73dd-5535-9772-9a903b5184fb | note | Load Centres
dfb242e1-1aa4-4e64-91f5-a2f96a2f90e5 | checkpoint | Main isolator installed capable of isolating all downstream circuits, is labelled appropriately i.e. MAIN SWITCH and is capable of being locked or within a lockable space.
e648c8c6-cb9e-5bb7-99a4-a937db938d16 | note | Load Centres
fe51ef93-3170-420f-b230-d993c82c990f | checkpoint | Visual indicator of periodic test, i.e. current test tag installed
5655ec40-f377-55f8-8b2c-0a324dbb1be8 | note | Load Centres
c6922096-3f33-4b27-844b-2841271e6785 | checkpoint | Construction DB Register complete
329a8c10-d2cb-525f-8a39-daaa7b967bd7 | note | Load Centres
9c01d7de-2a59-40d5-a115-df4c6c538685 | section | Construction Wiring
a9474edd-b8ca-42a8-8991-78224ee32e73 | checkpoint | Confirm wiring is not tied or bundled with permanent wiring system
cfb95b8e-7b25-4923-9bf4-2184e9bb93bc | checkpoint | Marker tape (yellow “construction wiring”) installed at intervals not exceeding 5 meters (unless cable is readily distinguishable colour from permanent installation)
2ac503ae-a532-46dd-b6f5-833f0ae396e7 | checkpoint | Permanent wiring in vicinity to be marked “live wiring”
b69801cd-86ab-4b84-9b2c-bdeb6ff69d6b | checkpoint | Mechanical protection installed as required including the use of plain screw adaptors (glands are not to be used)
1face744-e752-468a-85ac-9f4e163d0b14 | checkpoint | Visually inspect each circuit or sub mains entire route length to verify integrity of the installation as is practicable and safe.
903efd3b-6cd2-4b98-9e76-f6b95092c462 | section | Lighting
66fe4d46-ce6a-4f11-959a-375c5b692336 | checkpoint | Adequate access lighting provided, minimum 40 lux
f30c9fbd-8953-458a-9944-441df9ffe970 | checkpoint | Emergency Lighting over switchboard installed
e12bae5a-36a5-4b5a-b1ec-e055f3414f3c | checkpoint | Lamps protected from mechanical damage
780703f2-74b0-4c5f-a83a-4672f09f3369 | checkpoint | Emergency lighting (when required) adequate for safe egress – minimum 20 lux average
97f7b8ca-25d4-464f-8c1c-c3d25f21a4e5 | checkpoint | Emergency Lighting Register complete, site plan marked up accordingly
6b13fca7-3957-4905-b923-7bd5b2c97852 | checkpoint | Visually inspect each circuit entire route length to verify integrity of the installation as practicable
d0847937-47db-41a3-be7c-ad0037addbab | section | Emergency Lighting Battery Test – to be completed every six months
a86dc617-05a9-4fd8-9bb4-3e8e16932aba | checkpoint-no-value | Circuit Breaker Number
d329b189-ab7e-5deb-bf8f-fef4760aa2ca | textbox | Circuit Breaker Number:
82d4c347-633f-4301-a042-805877d14965 | checkpoint | LED charge indicator is working
8605db0e-3486-457e-8648-360a3965a2f3 | checkpoint | Battery Operates for 1 hour
6a8ebce6-eefe-4db1-9bc8-9d0e19cc6b8e | checkpoint | The Electricians noted above, working for Grid Electrical Services, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation un der the electrical safety act of that particular state/ territory at the date the test/ inspection was completed, in particular AS3000 & AS3012.
ed92105f-6c39-4ec6-9031-c03c0381bbf7 | signoff | Signoff
f63706d8-27d7-48f3-af26-473c7e4348ba | checklist | WHS-PRO-041 F-03 Construction Switchboard and Wiring Checklist - Annual |  | WHS-PRO-041 F-03 Construction Switchboard and Wiring Checklist - Annual
34fbf7d2-c205-44ce-9d84-85d57cc7d444 | section | Details
6d704a92-a71b-4feb-a11f-4a90f91bda05 | checkpoint-no-value | Details
f139e21e-ef5a-505a-92aa-0e885fab168c | textbox | Tag Number
3459d98d-c742-5619-9fd5-4a87ce1cd76d | textbox | Construction Board Location
d25d41ae-304f-5cc6-bdb6-8384805c79aa | textbox | Fed From
e6af2285-0fa6-4bbe-8bf3-ee65c1bd31cf | section | Section 1: Switchboard/ Load Centre
c05dc352-35e0-4aa4-88a1-849a4370cae1 | checkpoint-no-value | Construction Switchboards complete ALL check points, Load Centres (lunch shed, site offices etc.) complete noted check points only.
acc20fb9-227a-48d4-b931-1b706f2751c3 | checkpoint | All electrical equipment and lighting/ power supplied from a 30mA RCBO
150ec67d-39ac-525a-af4e-ba710b86786a | note | Load Centres
edc59b54-86fe-4922-bb32-034dc7c90afc | checkpoint | Readily accessible, i.e. not obstructed in any way
8ed303cd-316e-5bc3-9ee9-a2e54cd79a84 | note | Load Centres
e9b0f7f1-5af6-4d77-a658-f40251a0097b | checkpoint | Robust construction with a minimum IP23 rating
9793bf86-cf5d-4a95-a911-e5d14978f069 | checkpoint | Spider boards are not exposed to the weather
e349d1d5-a0c3-442a-8e70-18ace437d289 | checkpoint | Live components are effectively protected (check pole fillers)
f2f34949-191a-5ebb-a37a-9b1e0f8abd7f | note | Load Centres
f11ba251-1689-4dd3-9036-00f5c712cd47 | checkpoint | Insulated Tie bar has been fitted for flexible cords
2fa3db73-5528-4047-b47a-52cae41605c4 | checkpoint | Switchboard/ Load centre door is lockable, non-removable without a tool and fitted with a retention device to stay in the open position
2ad99f68-18fd-54c5-98ac-ce506dc89881 | note | Load Centres
b1f69731-e470-4160-88a5-83d9722cb636 | checkpoint | Mounting is secure and stable including secured to the floor
fa977253-1871-5fb3-b490-2e0f4615582d | note | Load Centres
d4fd4051-fd74-4a9d-ab40-598edb8eecb2 | checkpoint | Where there is more than one breaker, marking provided by means of number, letters or both to distinguish one from the other (unique ID)
3d4caaf2-dfcf-5455-a8cb-663a4f193b54 | note | Load Centres
42c6284c-3813-4de7-b90f-e0dc9713be55 | checkpoint | Marked with appropriate signage such as “danger 240V / 415V”, “lightning bolt”, “source of supply is identified” and” Keep Closed- Run all leads through the bottom”.
8836b28f-3360-5fb5-b2b9-113ab8bb46bd | note | Load Centres
b822d822-eb27-462a-9f26-a6b4fe0820b5 | checkpoint | Main isolator installed capable of isolating all downstream circuits, is labelled appropriately i.e. MAIN SWITCH and is capable of being locked or within a lockable space.
c17a4a72-aa78-5910-a5f3-e5940ae1a31b | note | Load Centres
28f0b2ca-26aa-42f5-b79a-41d1569c18f7 | checkpoint | Visual indicator of periodic test, i.e. current test tag installed
79b9f5f7-eebd-548f-9196-9193204adc33 | note | Load Centres
eabb2415-ce12-44a3-9b11-f9df24c0fd7c | checkpoint | Construction DB Register complete
86b4860b-e147-54a6-a42c-d4fce1880f23 | note | Load Centres
19ccc07d-ddaa-429e-8640-db6a0f15c93b | section | Construction Wiring
176dbdd8-af66-409d-8e07-0a09404878ff | checkpoint | Confirm wiring is not tied or bundled with permanent wiring system
5ff8a73e-6d6b-466c-862f-c4de81c2fdfe | checkpoint | Marker tape (yellow “construction wiring”) installed at intervals not exceeding 5 meters (unless cable is readily distinguishable colour from permanent installation)
30aaa1e0-59c7-4e2b-966e-c918c98ea7ba | checkpoint | Permanent wiring in vicinity to be marked “live wiring”
05ab87e4-5fd7-450a-bd67-3b3b3fad4087 | checkpoint | Mechanical protection installed as required including the use of plain screw adaptors (glands are not to be used)
9bc8b8db-5bf0-444f-af98-c2c1acbe0421 | checkpoint | Visually inspect each circuits or sub mains entire route length to verify integrity of the installation as is practicable and safe
a7b0dc3a-6f29-4c9c-ac1d-60c99571f34a | section | Lighting
5960c4a2-e129-472d-aca2-8898684c89b3 | checkpoint | Adequate access lighting provided, minimum 40 lux
c19fb719-9002-4833-aabf-f917fe71cc5b | checkpoint | Emergency Lighting over switchboard installed
bdbb7b6c-ec2f-4b5a-a390-b4a53b99fb76 | checkpoint | Lamps protected from mechanical damage
7abc85ce-6047-4874-b5a8-fd51aef1e0eb | checkpoint | Emergency lighting (when required) adequate for safe egress – minimum 20 lux average
99e09e7c-fe28-4310-85e6-ebe4741e437b | checkpoint | Emergency Lighting Register complete, site plan marked up accordingly
6832eeb0-058d-43ba-9e72-c09c026b60bb | checkpoint | Visually inspect each circuit entire route length to verify integrity of the installation as practicable
494b2ccd-c1b1-4f63-8f90-781bed467bce | section | Testing Equipment
f6570d2f-d338-4dbf-82f0-4639a70df839 | checkpoint-no-value | Testing Equipment:
cba5ba04-f2a1-56b3-b50d-a8400d72d440 | textbox | Serial Number:
712ae6c2-e8b4-56c4-aab1-83dfff4d3317 | textbox | Cert Number:
0f758979-de97-5400-9d2a-99df53563d79 | date | Calibrated Date:
956c69d3-5ee0-5eda-8615-7b3abb358aad | date | Calibrated Due Date:
8352532a-ce66-4644-ac7f-0f4e2657e009 | section | Emergency Lighting Battery Test – to be completed every six months
f0846109-46c9-4929-aadf-e4410983a3b0 | checkpoint-no-value | Circuit Breaker Number
05a09279-2d98-5ec8-ae13-a052c60cb6d1 | textbox | Circuit Breaker Number:
48eed226-5865-4621-b99a-7ba58a37eeb0 | checkpoint | LED charge indicator is working
10650576-c17e-4cad-8867-d68d2e6ccb63 | checkpoint | Battery Operates for 1 hour
1bc17bcd-5b5b-46f6-a74a-26b9c00d09ba | section | RCD Test – trip time and operational check to be completed on initial installation, then Operational Check monthly and trip time every 12 months
52f58615-bacd-46fc-8fcd-e61fe0091e0a | checkpoint | RCD Test (1) - Operational Check (push button test)
e52ef11e-b0b4-532f-a703-904b648b2b8f | textbox | ID No.
56623fe6-eb10-5f8f-81f3-7373098217ee | textbox | Description
6a306c84-9cd9-58db-8250-a1a2440dfe72 | note | Trip time
860e7e30-0760-5524-895c-1a39909961bf | textbox | 0*
e6d08ffa-8b2d-501a-9140-0a58821926a2 | textbox | 180*
5c3cd721-93b1-5eed-a434-371368b744df | textbox | Sensitivity
5044ea8c-f033-4de5-9990-bfcf77f6b33d | checkpoint | RCD Test (2) - Operational Check (push button test)
4e51852c-50dd-5d16-b98d-2f506e08370f | textbox | ID No.
332be179-c4ed-5245-b63a-b757cfe47806 | textbox | Description
6be65329-e243-5929-969f-e87b3971560f | note | Trip time
880f46e2-583e-5551-8711-4ee5e099ce9d | textbox | 0*
74b807d6-a5b7-54aa-a8a1-bcca46f38ec9 | textbox | 180*
64e3e89e-bfe1-59f3-ae93-a9b74a3b06bb | textbox | Sensitivity
df8e3abe-78ba-4a03-9cef-f8646170440b | checkpoint | RCD Test (3) - Operational Check (push button test)
b76492f2-f4d8-5585-9fb2-73cb589b4659 | textbox | ID No.
ac6258a3-5edd-59dd-b9e3-3e2fe3aa0940 | textbox | Description
7769c9b7-c551-5d2a-b74c-fdf400e04351 | note | Trip time
719e3fe8-def1-5bed-ab45-6239b422a827 | textbox | 0*
1cb1cc26-e604-54b6-bd1f-9b335869e22c | textbox | 180*
5deaf089-23cf-5568-bcd3-715018cccaf9 | textbox | Sensitivity
57b075e2-ef07-441a-bd9d-68d0108f3c61 | checkpoint | RCD Test (4) - Operational Check (push button test)
54ae3209-6796-5171-805f-4609b3f9fcc6 | textbox | ID No.
3672e732-e569-579a-b68f-df8c74f6cc18 | textbox | Description
89d77304-1363-5879-bef1-cb977c503d11 | note | Trip time
381879b5-ab4d-522e-87f8-74354ad90926 | textbox | 0*
30f44e85-fa45-5240-9ec8-1c4276a8d86e | textbox | 180*
99445b87-5bc1-52ef-9f46-3e997e517972 | textbox | Sensitivity
cef93080-0852-422f-8dd3-c82ba20536c6 | checkpoint | RCD Test (5) - Operational Check (push button test)
88371c92-6f94-55b2-bdff-deb2198f1c36 | textbox | ID No.
c006b5db-7e9f-5677-8307-fa1bb9ecab44 | textbox | Description
6e1c22c4-132f-52c6-8940-f38f0d295ebb | note | Trip time
7dddacec-33e5-524a-9e5b-b1a10fe971fb | textbox | 0*
5648f65f-4759-5279-8f59-9a63cd810eff | textbox | 180*
131e8752-9c3e-5cde-81f5-ca8295e12d2d | textbox | Sensitivity
2d3fe0b9-cc30-4f7a-83c8-c6ac14ad107a | checkpoint | RCD Test (6) - Operational Check (push button test)
3e1510a1-f299-5dc7-856b-579588060a00 | textbox | ID No.
c91be62c-49d8-57cc-b312-8e8fdc4ba4b2 | textbox | Description
53cacc86-b572-5ac2-b7dd-f9781f642d9a | note | Trip time
fa26a190-47f1-5fae-83bb-9d9574a8be53 | textbox | 0*
3d2cb026-e654-586c-bdd8-f95ff36243a9 | textbox | 180*
1b4fb14b-c791-538d-b670-a807e3d58eec | textbox | Sensitivity
9a9dfb1a-fdbc-49c1-9d59-c2f7752795a8 | checkpoint-no-value | Comments:
b3e79ce4-0aba-4326-a62f-dafaaa0f93be | checkpoint | The Electricians noted above, working for Grid Electrical Services, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation un der the electrical safety act of that particular state/ territory at the date the test/ inspection was completed, in particular AS3000 & AS3012.
614759c8-88dc-48bf-a79b-10bf77335807 | signoff | Signoff
9d35e101-bad4-427f-a089-3d0e72c1afa2 | checklist | WHS-PRO-041 F-03 Construction Switchboard and Wiring Checklist - Initial |  | WHS-PRO-041 F-03 Construction Switchboard and Wiring Checklist - Initial
d9f23e35-8b82-4c05-87ec-096581f47200 | section | Details
7c982ed7-c680-4d83-815c-32ed1f2e7c66 | checkpoint-no-value | Details
685ec3c5-8b07-59ca-bfa1-bd5b985e667c | textbox | Tag Number
8481ca5f-5db6-5698-ac73-fc80e1f1576f | textbox | Construction Board Location
75c1a410-4019-54e4-ab7d-35311cffebef | textbox | Fed From
b0581125-f233-4271-b2fb-7c27a2857745 | section | Section 1: Switchboard/ Load Centre
afea3652-28b1-493f-818a-e10ee138ed32 | checkpoint-no-value | Construction Switchboards complete ALL check points, Load Centres (lunch shed, site offices etc.) complete noted check points only.
870bb427-b144-4ecb-bc75-f30f3c5201d5 | checkpoint | All electrical equipment and lighting/ power supplied from a 30mA RCBO
1683e46d-2b8f-5c05-ae20-d3a22e3e7c03 | note | Load Centres
ba662b2c-e51c-4c50-9c3f-e4addc1df93a | checkpoint | Readily accessible, i.e. not obstructed in any way
fdbe5176-4b0c-5030-861a-808a3b5ce4b0 | note | Load Centres
33081646-7f3f-4835-813d-0f0488b26198 | checkpoint | Robust construction with a minimum IP23 rating
07f2c440-4c27-498a-867d-d1192a1ec4c9 | checkpoint | Spider boards are not exposed to the weather
46f06815-8533-4aa4-9dd2-315dd69ab571 | checkpoint | Live components are effectively protected (check pole fillers)
26bbf1d6-05d4-5c8c-8671-d7b063481a8c | note | Load Centres
65672bdc-e392-47bb-88ee-e93a07b90c4c | checkpoint | Insulated Tie bar has been fitted for flexible cords
082d8a81-6359-4413-8810-2a73f3550710 | checkpoint | Switchboard/ Load centre door is lockable, non-removable without a tool and fitted with a retention device to stay in the open position
dee52e21-a3a8-5b98-8295-bc91e6b38cb8 | note | Load Centres
469f84ac-691e-43a0-aecd-954dd94e3e53 | checkpoint | Mounting is secure and stable including secured to the floor
3c6e9f6e-ec40-56a8-b24c-24248e66e3a5 | note | Load Centres
c9b13606-30d9-488c-9d56-6162d1bb908a | checkpoint | Where there is more than one breaker, marking provided by means of number, letters or both to distinguish one from the other (unique ID)
5170efcf-4815-5f5a-8a40-eafe876d1bb9 | note | Load Centres
2b3cc5eb-0316-41aa-8126-8818ea582777 | checkpoint | Marked with appropriate signage such as “danger 240V / 415V”, “lightning bolt”, “source of supply is identified” and” Keep Closed- Run all leads through the bottom”.
8ee77d53-53ae-5727-b2e7-0a602deda7f2 | note | Load Centres
dbccb1ab-c997-4c2e-b507-b33a2e1b6c80 | checkpoint | Main isolator installed capable of isolating all downstream circuits, is labelled appropriately i.e. MAIN SWITCH and is capable of being locked or within a lockable space.
1a681fbb-9c8e-577e-bd84-eff07f65dc1c | note | Load Centres
5967afd8-d789-4827-aae3-878f00a8a97d | checkpoint | Visual indicator of periodic test, i.e. current test tag installed
9cf426fa-b9ae-5714-8b64-d59fcf741e7d | note | Load Centres
184fcacb-2489-4054-bb36-ecd93c0075cd | checkpoint | Construction DB Register complete
ed9e8b7c-4a86-5430-b264-4e7c11bf7dbc | note | Load Centres
59f4a58f-95dc-484e-b9a7-632170398d4c | section | Construction Wiring
ecc11752-1962-46d7-93cd-fa6989a3188b | checkpoint | Confirm wiring is not tied or bundled with permanent wiring system
1dd827b2-dbbb-4900-b461-762c2f1d4914 | checkpoint | Marker tape (yellow “construction wiring”) installed at intervals not exceeding 5 meters (unless cable is readily distinguishable colour from permanent installation)
db2dbc85-5c5e-4fd2-8bac-f3aee65fc22c | checkpoint | Permanent wiring in vicinity to be marked “live wiring”
1a689aad-f3ed-4b3d-bf5e-d70aad11b747 | checkpoint | Mechanical protection installed as required including the use of plain screw adaptors (glands are not to be used)
7620b00b-f07e-4783-b316-15ad5b7741f4 | checkpoint | Visually inspect each circuit or sub mains entire route length to verify integrity of the installation as is practicable and safe
adca6b87-f695-4f25-8afc-066bd7aacadb | section | Lighting
d87808ba-5f59-4027-8c25-0ef0957923cd | checkpoint | Adequate access lighting provided, minimum 40 lux
f05ec93d-424f-4f03-b66f-b6c6586540ed | checkpoint | Emergency Lighting over switchboard installed
2e2bd78f-321e-4229-b55b-a900c17903df | checkpoint | Lamps protected from mechanical damage
7d909056-629d-4c80-805d-f02211c3e82b | checkpoint | Emergency lighting (when required) adequate for safe egress – minimum 20 lux average
7c9391ef-015a-442c-965a-2d014935f753 | checkpoint | Emergency Lighting Register complete, site plan marked up accordingly
4a5a2f8d-78c6-42e9-814b-f4449eb3fa47 | checkpoint | Visually inspect each circuit entire route length to verify integrity of the installation as practicable
88e0fe83-17fa-484f-8f8d-19a96208c1e2 | section | Testing Equipment
64d2c7e3-0b41-427d-ae87-036bb46fcede | checkpoint-no-value | Testing Equipment:
51bbaf92-dd21-5b8d-8ddb-cc8a527d60b9 | textbox | Serial Number:
79f81cc1-1b75-5136-a236-24f6dad6e7c9 | textbox | Cert Number:
f2aa67d0-18aa-57ca-87e7-1b50ce5c62f0 | date | Calibrated Date:
7e61f093-2d1f-5c5e-885f-0b523e4a1207 | date | Calibrated Due Date:
ada828cb-b9c2-45c6-994c-0ec809e75eef | section | Test Report - to be completed on initial installation of Construction Board and visually inspected every six months after
ffbf03bb-4f09-468b-a9ec-a7e77516f233 | checkpoint-no-value | Details
407bf833-bc78-52bb-963a-47c4a3b176bc | textbox | Earthing system integrity (Ohms)
03b1331c-a6b7-573d-9d8b-80079e66cfe7 | note | Insulation resistance (Meg Ohms)
537689ff-487b-551c-954e-c2e14baa5597 | textbox | A-B
a97efc88-92c6-578f-af33-7560bb29d98f | textbox | A-C
ba4dafc6-0da6-5845-a1c6-e709c98ffd6c | textbox | A-N
6ce5cb3b-12a3-55ce-8706-a25250bfffff | textbox | B-C
5d9c4c62-acd5-56e7-9372-45b3a8aae458 | textbox | B-N
b10f6a97-03b6-5df7-b7ed-b596c4196c94 | textbox | C-N
f0f9e5ad-2042-4f43-b856-d8a1a6684e38 | checkpoint | Polarity
2beae974-b46a-4550-8a2c-685c64456344 | checkpoint | Correct Circuit Connections
0d74ac86-ed9e-4e3b-bcae-35a336049833 | checkpoint | Suitable for connection to supply
91347b9b-2a25-4793-bfc8-ede377902396 | section | Emergency Lighting Battery Test – to be completed every six months
14d7729b-ed4d-4295-9502-c674a751c79b | checkpoint-no-value | Circuit Breaker Number
08e900fd-29b5-5d73-8204-ebcbbe76a9a8 | textbox | Circuit Breaker Number:
7c17f6e7-7493-49d6-989a-146b5a9d4f06 | checkpoint | LED charge indicator is working
ed9e4fd7-c287-4d39-8e5a-97673cd1e7b9 | checkpoint | Battery Operates for 1 hour
5e3b3cd0-0e7c-4a4a-93b0-ed967b92eed7 | section | RCD Test – trip time and operational check to be completed on initial installation
8c7529e9-0d20-447a-b7cd-c253324b515d | checkpoint | RCD Test (1) - Operational Check (push button test)
e327fbd3-da70-5e68-be3f-39d60d0918b6 | textbox | ID No.
b67f9e99-1361-5021-9de2-426c8d6513d3 | textbox | Description
2e2a50c6-bf8c-59c0-9486-d0e47ff910a6 | note | Trip time
639257e9-5e8d-5a42-894e-a6a7f3274e3f | textbox | 0*
35ec1ec3-7f9d-53df-ba92-650b21e6cb07 | textbox | 180*
75d161dd-967d-5d41-8199-1a89b30565bb | textbox | Sensitivity
647d7272-afe9-460a-89a0-f97ac06b19a6 | checkpoint | RCD Test (2) - Operational Check (push button test)
f1ba9d6f-dec3-5bc9-ba78-42393883142a | textbox | ID No.
ddf08d7f-8303-5829-bca8-b90de0f35619 | textbox | Description
8f56cb48-ee01-5f46-a761-88b57f18bdb5 | note | Trip time
2c998828-6fb3-59eb-9be8-7d69ae4922fa | textbox | 0*
67497834-8b04-5279-80bf-c14a324f5e1f | textbox | 180*
ff6b143a-a270-5b11-ba08-5c2ae79cf626 | textbox | Sensitivity
05183182-3aec-44b7-9e8f-469ac4e4b885 | checkpoint | RCD Test (3) - Operational Check (push button test)
a8e6305c-0628-58ca-909b-9f93b90ef96d | textbox | ID No.
6d22dc80-1312-5142-93b9-0dfa9fb77edd | textbox | Description
bd0305b8-717e-57b5-89b9-43544d6e9233 | note | Trip time
42fd1383-662f-58b8-93ee-cee08f02d964 | textbox | 0*
b09925e8-ed77-5afd-a981-f4220f004914 | textbox | 180*
b31a5a22-c5a7-52d8-9c73-661b3a0df495 | textbox | Sensitivity
a1e1ff3c-e5aa-4ec4-8c72-3aa529a811b7 | checkpoint | RCD Test (4) - Operational Check (push button test)
5052cfdd-647f-5385-b4ff-35bdd2e1f589 | textbox | ID No.
8007d0d2-4dcc-5e55-9f87-57223af0f651 | textbox | Description
dc0345b5-cd01-55e1-bf5d-f76d47dfea7c | note | Trip time
2139f2cf-5c6d-5fe2-86f0-9bff163a25f7 | textbox | 0*
f48b0cf0-3317-5159-8edd-2b08ba21bf56 | textbox | 180*
5917e8fe-a540-5816-b606-d8b5cebc8630 | textbox | Sensitivity
1b04ca9d-a3d7-46b6-b475-48c376bf8d3e | checkpoint | RCD Test (5) - Operational Check (push button test)
dff3afa7-9b33-5760-a9d2-ef51de339961 | textbox | ID No.
cb62cfa9-d531-52c4-9d87-a0a1c4d0ddd4 | textbox | Description
10bfee9b-4ab1-5f45-97c1-c12c93cfe9a6 | note | Trip time
8421a4e2-23a6-5127-8fae-54ced11e661c | textbox | 0*
98b76b3f-72c8-5cd2-9a8b-e042e2ee9340 | textbox | 180*
336ad746-ad60-54ba-ba72-86a98ecde03a | textbox | Sensitivity
48d75f7a-a98d-421c-9842-a9f0f6097bcb | checkpoint | RCD Test (6) - Operational Check (push button test)
c7cf8967-68c8-515a-9298-13ffa03a4480 | textbox | ID No.
f657c80b-1704-50d7-b11c-44f829356d0d | textbox | Description
30fe2aaf-849f-50cb-8ca6-58189585f61a | note | Trip time
f18bf110-5b3a-54b9-9f38-656cb5f6160d | textbox | 0*
9d76aa74-22a7-59c3-9b92-849c590024e6 | textbox | 180*
c355bad8-e083-5a01-afdd-b8ccdc856dcf | textbox | Sensitivity
36c76084-a242-4a2d-b4e5-a22c3d90d936 | checkpoint-no-value | Comments:
b98b8088-bc2b-41ad-b027-51e5b1d28f10 | checkpoint | The Electricians noted above, working for Grid Electrical Services, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation un der the electrical safety act of that particular state/ territory at the date the test/ inspection was completed, in particular AS3000 & AS3012.
d3a19844-914f-446a-ba0e-cdfc7ee607f9 | signoff | Signoff
181243b9-fadd-4e1f-896f-e750217a8043 | checklist | WHS-PRO-041 F-03 Construction Switchboard and Wiring Checklist - Monthly |  | WHS-PRO-041 F-03 Construction Switchboard and Wiring Checklist - Monthly
b9c22620-1a9d-463a-ae56-6a3757338e3b | section | Details
756b6be8-c9e6-4093-9d79-7ac6a6b233ec | checkpoint-no-value | Details
1352dcbc-bd16-5d69-b735-ae1cec9abd3c | textbox | Tag Number
8bdb1288-b0b3-5617-9971-7eff878ac099 | textbox | Construction Board Location
170112f2-f439-5737-bfb1-ed4bd528b0b6 | textbox | Fed From
bc601785-c32b-41c0-9611-7897f70fab2c | section | Section 1: Switchboard/ Load Centre
82d4138c-feff-4db1-8729-c88eb58fa3c0 | checkpoint | All electrical equipment and lighting/ power supplied from a 30mA RCBO
600b307e-b7e6-5b61-a14b-b9ad6762e890 | note | Load Centres
1fc2ae85-663b-4f3a-8d61-d8446d0cf7b5 | checkpoint | Readily accessible, i.e. not obstructed in any way
7d557bba-a26e-5f12-9532-0d8f3c2bd23c | note | Load Centres
4782e95e-26d3-407e-9f2e-4e9db00ab092 | checkpoint | Robust construction with a minimum IP23 rating
3e9cee53-7802-43bc-86cb-8c964d9cae59 | checkpoint | Complete operational checks of all RCD’s i.e. push the test button
8a378df8-0845-5166-8f96-ae2ca5403df5 | note | Load Centres
27b1aa15-0e5d-4cfe-8c3b-2df7ab924469 | checkpoint | Spider boards are not exposed to the weather
fb3954b3-1644-4b3f-8797-4815dc5399ff | checkpoint | Live components are effectively protected (check pole fillers)
860da1a4-8c2e-5173-ac95-b081adb2df36 | note | Load Centres
fd5f1563-3aae-4d9e-ac07-d761e53d4d2e | checkpoint | Insulated Tie bar has been fitted for flexible cords
659fed77-3c24-497a-ae5b-35631b90f7b0 | checkpoint | Switchboard/ Load centre door is lockable, non-removable without a tool and fitted with a retention device to stay in the open position
04efc631-f470-5f44-aaf2-ef99620ad9ce | note | Load Centres
c3bd4ad8-cc47-41e6-bb3e-4acd60eddc50 | checkpoint | Mounting is secure and stable including secured to the floor
ee81fb31-ddd1-5763-b8f7-b817c6ed8387 | note | Load Centres
d276bea3-8163-4c49-9bb1-6a778b31538c | checkpoint | Where there is more than one breaker, marking provided by means of number, letters or both to distinguish one from the other (unique ID)
2693df93-f880-5be4-90e2-e57301e7d0e5 | note | Load Centres
6c554058-9474-4587-9af0-e57290efe5d8 | checkpoint | Marked with appropriate signage such as “danger 240V / 415V”, “lightning bolt”, “source of supply is identified” and” Keep Closed- Run all leads through the bottom”.
4dc3bbf0-9bd6-56af-b638-5f3fc0205e80 | note | Load Centres
4b9170aa-585d-434e-a55f-9f2fb5b8345a | checkpoint | Main isolator installed capable of isolating all downstream circuits, is labelled appropriately i.e. MAIN SWITCH and is capable of being locked or within a lockable space.
85549398-326c-59f8-81c7-474a6a5eb94e | note | Load Centres
21dc8563-adbf-4f42-a9b9-53e9cd7acf03 | checkpoint | Visual indicator of periodic test, i.e. current test tag installed
4b487965-74a1-5613-a7e3-86983a31c115 | note | Load Centres
cbc5584e-a385-4fc7-a5af-685273804681 | checkpoint | Construction DB Register complete
a65f9fa0-bb14-5457-afcf-0262dcb6f83d | note | Load Centres
93aa566a-973a-4e68-99ee-37ac88d96ec2 | section | Construction Wiring
650245c3-9d88-44a7-ba87-125d68855cbc | checkpoint | Confirm wiring is not tied or bundled with permanent wiring system
39e199c9-3747-4643-9f77-338a97de9140 | checkpoint | Marker tape (yellow “construction wiring”) installed at intervals not exceeding 5 meters (unless cable is readily distinguishable colour from permanent installation)
10ffcc39-ab01-4478-9773-db6a5cc24cd0 | checkpoint | Permanent wiring in vicinity to be marked “live wiring”
3211f8fc-1a0d-42b7-8c98-43bd04811d6a | checkpoint | Mechanical protection installed as required including the use of plain screw adaptors (glands are not to be used)
4df9ca44-9ff6-4b57-88b6-cbe250624a97 | checkpoint | Visually inspect each circuit and/ or sub mains entire route length to verify integrity of the installation as is practicable and safe
e143c8d6-3158-4918-ab0c-a483e8dc04fc | section | Lighting
31583f1d-e451-4207-bba6-fb801c2ac6d4 | checkpoint | Adequate access lighting provided, minimum 40 lux
c5be621f-3df5-450d-8329-98e911281391 | checkpoint | Emergency Lighting over switchboard installed
08274758-8ae5-41c7-8fc9-31973adec25d | checkpoint | Lamps protected from mechanical damage
d087601e-4c96-4bac-9fe3-b7668639f7da | checkpoint | Emergency lighting (when required) adequate for safe egress – minimum 20 lux average
ba31f921-360a-4a66-9534-dbca22739028 | checkpoint | Emergency Lighting Register complete, site plan marked up accordingly
ed9aa8f1-e359-4462-aa7f-acafc61c8cd3 | checkpoint | Visually inspect each circuit entire route length to verify integrity of the installation as practicable and safe.
7219db24-285a-44a3-a93d-d475fad1f58d | checkpoint | The Electricians noted above, working for Grid Electrical Services, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation un der the electrical safety act of that particular state/ territory at the date the test/ inspection was completed, in particular AS3000 & AS3012.
76d438df-b1c8-4d0b-9b73-901e21c28966 | signoff | Signoff