## Sheet1
checklist | ITC 010 - Inground Conduits
section | Referenced Drawings and Revision Number
checkpoint-no-value | Details
textbox | Referenced Drawings and Revision Number
section | INGROUND CONDUITS AND UNDERGROUND SERVICES INSPECTIONS
checkpoint-no-value | Description of Work Area
textbox | Description:
checkpoint-no-value | Attach mark-up of work area
checkpoint | Investigation of Existing Services Completed, including review of existing services documentation & BYDA drawings and service scan
checkpoint-no-value | Validation of Imported Material undertaken as per RAP requirements. Upload material validation certificate.
checkpoint | Set-out inground conduits, pits and any other items in accordance with the IFC documentation ahead of commencing excavation
checkpoint | Excavate to design levels. Check that minimum cover requirements are achieved (650mm minimum cover for LV & 300 for comms).
checkpoint | Inspect trench and ensure it is free from sharp materials
checkpoint | Place bedding sand in bottom of trench. Check that 50mm bedding sand is achieved.
checkpoint | Place conduits, glue and pull through draw wire
checkpoint | Verification of correct conduit sizeas per IFC documentation.
checkpoint | Take photos of conduits prior to backfill.
checkpoint | Surveyor to survey conduits prior to backfill.
signoff | HOLD POINT
checkpoint | Principle contractor to inspect conduits prior to backfill.
signoff | HOLD POINT
checkpoint | Place and compact sand to 300mm above the top of conduits.
checkpoint | Place warning tape.
checkpoint | Place and compact suitable material to remaining depth of trench.
checkpoint | Undertake compaction testing per the civil documentation.
checkpoint | Pits cleaned and free of holes. Refer to ITC 10A
checkpoint-no-value | Attach as-built survey
checkpoint-no-value | Attach any other relevant items (optional)
checkpoint | Grid final acceptance - Foreman or higher
signoff | HOLD POINT
checkpoint | Client to review completed ITC and confirm acceptance
signoff | HOLD POINT
checklist | ITC 010A - Inground Pits
section | Referenced Drawings and Revision Number
checkpoint-no-value | Details
textbox | Drawing and revision number
section | INSPECTION AND TEST RECORD FOR: INGROUND PITS
checkpoint-no-value | Description of Work Area
textbox | Description:
checkpoint-no-value | Attach mark-up of work area
checkpoint | Set-out pits and any other items in accordance with the IFC documentation ahead of commencing excavation
checkpoint | Excavate to design levels.
checkpoint | Ensure Drainage Holes are provided on bottom of pit
checkpoint | Ensure connected connection to Stormwater System where applicable.
checkpoint | Place bedding sand in bottom of trench.
note | Check that 100mm bedding sand is achieved.
checkpoint | Place Hessian Underlay above
checkpoint | Place Gravel above Hessian Underlay .
note | Check that 150mm gravel is achieved.
checkpoint | Install Pit ensure levelled to correct RL
checkpoint | Take photos of pits prior to backfill.
note | (Upload separately below).
checkpoint | Client to inspect pits prior to backfill.
signoff | HOLD POINT
checkpoint | Place and compact suitable material to remaining depth around pits inline with manufactures data sheet.
signoff | Request Sign Off
checkpoint | Pits cleaned & sealed
checkpoint | Ensure Pit Lids are clearly labelled with service type
checkpoint-no-value | Attach photos of conduits
checkpoint-no-value | Attach as-built survey
checkpoint-no-value | Attach any other relevant items (optional)
checkpoint-no-value | Client to review completed ITC and confirm acceptance - final acceptance
signoff | Client Final Acceptance