## ITP-008
ConQA Team Notes:
Document Title: |  | ITP-135-CIV-SSB-Stormwater Pits and Pipe Installation
ITP Description: |  | SSB-Stormwater Pits and Pipe Installation
Discipline (e.g. CIV/STR/RAIL): |  | 135-CIV
Revision Number: |  | 0
Revision Date: |  | 2023-01-30
ITP created by: |  | Hiruni Wickramarathne
ITP approved for use by: |  | Victor Mira
Special Notes to ConQA Team : |  | ITP for Beaconsfield Station
Inspection & Test Plan - Stormwater DrainagePits and pipes installation
[9 empty] | Revision: | 0
[9 empty] | Date: | 2023-01-30
Legend: HP: Hold Point, HP* Internal Hold Point, WP: Witness Point, IP: Inspection Point, SP: Surveillance Point
Item | Task/Activity Description | Reference | Acceptance Criteria | Inspection / Test |  |  | Responsibility | Verifying Documents | Date Completed | Sign-off
|  |  |  | Method | Frequency | Category
1 | Referenced Documentation
1.1 | Non Dependent | VicRoads Section 701 (May 2020) | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.2 | Non Dependent | VicRoads Section 705 (June 2021) | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.3 | Non Dependent | IFC Drawings | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
2 | Preliminaries-Materials
2.1 | Materials | Respective separable package Materials and CCTV ITP | Materials are as approved in the main ITP Enter: Separable package Lot number:[Textbox] | Document Review | Each lot | HP | Nominated Authority | Teambinder Material Approval
4 | Pre-Construction Activities
4.1 | Survey Set Out - Pits & Pipes | IFC Drawings Section 701.10 | Prior to commencement of excavation for the culverts the Contractor shall confirm the position of all culverts with the Superintendent. Survey activities undertaken to ensure and validate the plan location, height and line of pits and location, invert level, plan of pipes in accordance with design documentation and 701.10 | Survey | Each Lot | HP* | PE | CHK-001-CIV-Stormwater Drainage Pipes Installation CHK-002-CIV-Stormwater Drainage Pits Installation
5 | Construction / Installation Activities
5.1 | Pits - Excavation | IFC Drawings Section 705.05 | Excavation shall be to the depth indicated on the IFC drawings or as necessary to secure a satisfactory foundation. Precast pits shall have min of 400mm clearance from all external faces of the pit to each face of the excavation. | Visual inspection Measure | Each Lot | IP | SE | This ITP
5.2 | Pits - Placement of Bedding Material | IFC Drawings Section 705.05 | Bedding conforming to to 701.09 shall be supplied, placed and compacted to a thickness: > 80mm for clay foundations > 150mm for rock foundations | Visual inspection Measure | Each Lot | IP | SE | This ITP
5.4 | Pits - Placement of Precast Drainage Pit | IFC Drawings Section 701.10 | Survey pick-up to verify: - Plan location of pits, other than offsets to kerb line or barriers, to be +/- 100mm - Offset of entry pits required to match lines of kerbs or barriers ±20 mm | Visual inspection Measure | Each Lot | IP | SE | This ITP
5.5 | Pits - Cast in Place Drainage Pit | IFC Drawings Section 705.06 Section 610 Section 611 | Cast in place drainage pits shall be constructed at the locations and to the dimensions shown on the drawings and in accordance with the requirements of Section 610 and 611. Cast in place drainage pits shall not be constructed with fibre reinforced concrete (FRC). | Survey Measure | Each Lot | IP | SE | This ITP
5.6 | Pits - Jointing & Drainage Connections | Section 705.11 | All connections to drainage pits shall be neatly made in accordance with Section 705.11. Openings into drainage pit walls to facilitate drainage connections shall be neatly saw cut to the required size not more than 50mm greater than pipe diameter. Breaking out of holes is not permitted. Drainage pits shall be replaced if circumferential or longitudinal cracking occurs as a result of installing holes or if the hole exceeds the pipe diameter by more than 50 mm. Exposed reinforcement shall be coated with an approved epoxy treatment to prevent corrosion prior to rendering around the pipes. | Visual inspection Measure | Each Lot | IP | SE | This ITP
5.7 | Pits - Shaping of Floor | Section 705.13 | Drainage pit floors shall be smoothly shaped from the inlets to the outlet for a height of one‑third of the diameter of the outlet pipe with cementitious mortar in accordance with Section 705.13. | Visual inspection Measure | Each Lot | IP | SE | This ITP
5.8 | Pits - Step Irons | IFC Drawings Section 705.12 | Drainage pits greater than 1.0m deep shall be fitted with step irons in accordance with 705.12. Ladder rungs shall not opbstruct openings and that water does not discharge on them. Step rungs do not come within 50mm of the top of the riser. Step irons of an approved proprietary type shall be installed in accordance with the manufacturer's instructions. | Visual inspection Measure | Each Lot | IP | SE | This ITP
5.9 | Pits - Fitting of Covers | IFC Drawings Section 705.17 | Frames for drainage pit covers shall be cast into the top of the drainage pit or bedded on fresh mortar, 5 mm thick, consisting of two parts of sand, one part of cement and sufficient water to produce a mix of suitable consistency. Height shall be within 10mm of the design level. | Visual inspection Measure | Each Lot | IP | SE | This ITP
5.10 | Pits - Pit Lids | IFC Drawings | All stormwater pits shall be provided with a locakable pit lid minimum Class D with in-fill material or fibre glass Terra Firm Enduro or similar. | Visual inspection | Each Lot | IP | SE | This ITP
5.11 | Pits - Backfilling Around Drainage Pits | Section 705.18 | Backfilling around drainage pits shall be placed in layers not exceeding 300 mm loose thickness and compacted to refusal using hand held mechanical equipment. | Visual inspection Measure | Each Lot | IP | SE | This ITP
5.12 | Pipes - Trench Excavation | IFC Drawings Section 701.15 | Excavation for pipe shall have a horizontal clearance between the pipe and the excavation wall of: > 300mm, < 600mm for RCP > 150mm for Flexible Pipe The base of the trench shall be compacted to refusal using mechanical plant. | Visual inspection Measure | Each Lot | IP | SE | This ITP
5.13 | Pipes - Bedding Placement | IFC Drawings Section 701.16 | Bedding material shall be provided and placed in the full width of the trench to the below minimum: > 100mm where D<1500mm > 200mmwhwere D≥1500mm Bedding material shall be placed and compacted in layers <150mm loose thickness | Visual inspection Measure | Each Lot | IP | SE | This ITP
5.14 | Pipes - Bedding Testting | IFC Drawings Section 701.20 | Test a minimum of 20% of all lots for each culvert. (Lot = 1 layer of bedding or backfill). The number of tests per lot shall be three Bedding shall be compacted to refusal using hand held mechanical equipment and material (Swell ≥ 2.5%) and mean moisture ratio of 92% between the completion of rolling and the placement of overlaying layer | Compaction Test | Each Lot | IP | SE | This ITP
5.15 | Pipes-Placement of Pipe - Flexible Pipe | IFC Drawings Section 701.17 Section 701.22 | All buried flexible pipe sections supplied shall be assembled in accordance with the manufacturers specifications. Before proceeding to install the next length of pipe, the conformity of the assembled joint shall be verified by checking that the position of the rubber ring on the spigot, and the clearance and overlap between the spigot and socket, are within the values specified by the manufacturer. | Visual inspection | Each Lot | IP | SE | This ITP
5.16 | Pipes - Lifting Holes | Section 701.18 | Lifting holes shall be plugged off in accordance with the manufacturers specifications after the pipe is installed. | Visual inspection | Each Lot | IP | SE | This ITP
5.17 | Pipes - As-built survey pick-up | IFC Drawings Section 710.10 | Each run of underground drainage shall be Survey verified prior to backfilling. - Offset pits to kerb +/- 20mm - Plan location pits not adjacent to kerb +/- 100mm - Invert level of pipes at pits +/- 50mm - departure from design grade +/- 10mm in 10m, provided minimum grade is not less than 1:250 | Survey | Each Lot | IP | SE | This ITP
5.18 | Pipes - Backfill Placement | IFC Drawings Section 701.16 | Backfill material shall be placed the full width of the bedding material and compacted in layers <150mm loose thickness. Filling shall not be placed within 2.0m of the open end of the pipe where a further section is to be placed. | Visual inspection Measure | Each Lot | IP | SE | This ITP
5.19 | Pipes - Backfill Testing | IFC Drawings Section 701.20 Section 701.29 | Test a minimum of 20% of all lots for each culvert. (Lot = 1 layer of bedding or backfill) Backfill material shall be compacted to a density ratio > 97%. Material which has a swell equal or greater than 2.5% shall be maintained at a mean moisture ratio of 92% between the completion of rolling and the placement of overlaying layer | Visual inspection | Each Lot | HP* | PE | This ITP
6 | Post-construction / Post-installation Activities
6.1 | Flushing & CCTV | Section 701.28 Section 701.30 | Refer to Respective CCTV and Material approval Lot Enter CCTV and Material approval Lot number: [Text Box] | Record Review | Each lot | HP | Nominated Authority | This ITP CCTV Reports
6.2 | As Built Survey | Section 701.10 | Provide record of dimensional measurements to demonstrate the drainage lines are installed within the tolerances specified in Section 701.10 Attache: Survey conformance Report | Document Review | Each lot | IP | SE | This ITP As Built Survey Report
6.3 | Repairs to Damaged Pipes | Section 701.31 | Where inspections after backfilling identify any of the following defects they shall be notified as a non-conformance: • cracks wider than 0.5 mm • spalling of concrete • exposed reinforcement • joints that are not fully engaged. Any pipes with defects greater than the following limits shall be removed and replaced: • longitudinal cracks greater than 2 mm • circumferential cracks around the full circumference with width greater than 3 mm or with lateral displacement of the cracked sections exceeding 3 mm • circumferential cracks around part of the circumference with width greater than 4 mm • penetrations with area greater than 400 mm2 • pipe joints that are separated. The Superintendent may agree to accept pipes with defects as noted above subject to demonstration that repairs will ensure that pipes will operate effectively for their design life. Consideration will only be given to products and procedures with proven performance and to the following types of treatments: • hot sprayed epoxy coatings for cracks not wider than 4 mm with no lateral displacement • fibre glass reinforced epoxy sleeving for cracks not wider than 4 mm with lateral displacements up to 3 mm • spalled concrete, exposed steel reinforcement and penetrations shall be treated as patch repairs and repaired with polymer modified cementitious repair materials in accordance with the requirements of Section 689. The Contractor shall submit details of proposed rectification treatments including manufacturer’s product specifications and warranties, the area and thickness of repair treatment, detailed repair procedures, and inspection and test plans. No repairs shall be undertaken without the Superintendent’s approval of the repair materials and procedures. All repairs shall be inspected using CCTV to verify compliance with the repair specifications. | Document Review for Repair Procedure CCTV Report Review Visul Inspection | Where applicable | HP | Nominated Authority | This ITP Approved Repair Procedure Post Repair CCTV Report
6.4 | Non-conformance Report (NCR) Closure | MRPA Quality Management Plan | Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed in Teambinder. | Document Review | Once, prior to closure of this lot / element / Work area | HP* | PE | This ITP
Final Inspection
On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
Print Name: Position: Signature: Date:
Note on D45: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm the compaction method for backfill, standard or modified?