## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Rough In / Fit Off Checklist |  |  |  |  | Yes | Rough In / Fit Off Checklist | 66efcd27-c362-46a5-9a59-e85e283c53e1
checkpoint-status |  |  | checkpoint | Rough In completed
text | 6bbd850a-24b9-5ec8-b4fb-fe26384c4e7e |  | textbox | IQ Terminal
checkpoint-status |  |  | checkpoint | Cable Fit Off completed
text | 233db7c5-2ec9-5660-9fb8-9e881610ce3f |  | textbox | Controller Terminal
checkpoint-status |  |  | checkpoint | Device Fit Off completed
text | 7dada32f-63ba-52d1-8062-c2cc2d375b75 |  | textbox | Fire alarm status
checklist-flat |  |  | checklist | ITP 4 - Monitored Door |  |  |  |  | Yes | ITP 4 - Monitored Door | 6970b6e2-0b85-4c84-85d0-8941988430e5
checkpoint-status |  |  | checkpoint | Check No. 1
boolean | f95773e9-9fc5-5284-98d2-4fb78dfd8918 |  | tickbox | Check that the door is closed.
boolean | 54d9f498-d469-5c71-b48b-0074957ddfd0 |  | tickbox | Ensure that the door is in “Secure” mode on the EBI workstation.
boolean | 52dca58e-757b-50e4-83fa-fe2f1300affb |  | tickbox | Open the door with a key and verify that a door alarm is logged at the EBI alarm summary.
boolean | e0b4ad8a-62e6-53d5-86fd-adf500f400db |  | tickbox | Right click the point and select “associated page” to confirm the right floor plan has been linked.
boolean | ed8561e0-d62c-51ab-a164-317f2b031ec6 |  | tickbox | Check colour of door icon on floor plan.
checkpoint-status |  |  | checkpoint | Check No. 2
boolean | f277ee0c-ba54-5631-80cc-9919a6a61044 |  | tickbox | Close the door & reset to secure mode and verify that the alarms clear.
checkpoint-status |  |  | checkpoint | Check No. 3
boolean | 804c3338-aac4-53fe-87f5-6a9ff585b74e |  | tickbox | Switch door to “Access” mode.
boolean | 666cb30b-b79b-5c11-94af-642c4edc2362 |  | tickbox | Open the door with a key and verify that NO door alarm is logged at the EBI alarm summary.
boolean | e7fbb3ad-c771-5c5e-93fd-78bf3db9f385 |  | tickbox | Check colour of door Icon on floor plan.
checkpoint-status |  |  | checkpoint | Check No. 4
boolean | 45a816a0-c4d6-53ce-8089-020e7227c3aa |  | tickbox | In the security panel disconnect one input wire.
boolean | 48d68dc9-d122-5ed2-a1ef-52f260eec09d |  | tickbox | Confirm a high priority tamper open alarm is raised in the EBI alarm summary.
boolean | dbb09914-4ec7-5429-9a5b-639fddde2fea |  | tickbox | Put wire back and now short the input with a piece of wire.
boolean | 5df8796e-0e9e-51e1-8d38-f51bbf9b0213 |  | tickbox | Confirm a high priority tamper short alarm is raised in the EBI alarm summary. right click the alarm, select “associated display” , and check icon colour on the floor plan.
checkpoint-status |  |  | checkpoint | Honeywell Sign Off
holdpoint |  |  | signoff | Multiplex Sign Off
checklist-flat |  |  | checklist | BMS Checklist |  |  |  |  | Yes | BMS Checklist | ef9bf8c3-b780-4bab-af1a-33d9ae30b967
checkpoint-status |  |  | checkpoint | All information completed below
text | c434d61c-64a3-5f2a-8ffc-539558ebf055 |  | textbox | Terminal Address:
text | 72ebe48f-f7e5-5e79-b07b-a8dd16e942fc |  | textbox | Plant Name:
select | a268edf4-0e65-570e-b4ca-f09581614b59 |  | dropdown | Point Type | Analog Input, Analog Output, Binary Input
text | 8fa10512-a579-563d-9aec-b99ff4fa2bbb |  | textbox | Additional comments if applicable
checkpoint-status |  |  | checkpoint | Installation complete