## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | ITP007 - Precast Drainage Structures | itp |  |  |  | Yes | FH-ZU2-QU-ITP007 - Precast Drainage Structures - Rev 0 | 402839a9-e811-488c-99cd-5670e095de16
checkpoint-group |  |  | section | 1.0 - Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | 5db1b43a-1481-53e1-8de3-6d2f2dc31855 |  | note | Frequency - Prior to commencing activity
label | 1a76d17f-abc3-50a3-b63a-504f13b3a613 |  | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
label | 0d8d158f-73f0-5a63-b5b1-81123ed6bfe9 |  | note | ○ using the correct and complete set of drawings.
label | bbdc7d62-c614-531d-9e87-93061dcfdf4b |  | note | ○ all drawings are the latest revision.
label | 2cceb0a1-7ceb-5f46-90ba-44ce40a286b7 |  | note | Reference Documents - IFC Drawings
label | 57e73c5b-8753-5f96-9e6b-7503760b523e |  | note | Inspection/Test Method - Document Review
label | 3453148d-86f9-55d1-9874-e84456f23411 |  | note | Record of conformity - This ITP Signed
label | f2aebf2b-e43a-5cb6-b55f-8253f262294f |  | note | HP*
label | 31f3edd6-0a74-5ffd-994f-63f47528d216 |  | note | Responsibility - Project/Site Engineer
date | 9b90ffe2-5c62-5bad-b57d-2238a6456e16 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 7db392a2-fa21-5236-8c16-e9900da3e150 |  | note | Frequency - Prior to commencing activity
label | f4083910-855f-57c0-9147-6a80de365aa0 |  | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: CEMP, TMP, SWMS & WP.
label | 06f95c10-fae3-5fe3-ab27-fe120bb891db |  | note | Reference Documents - CEMP, TMP, SWMS & WP
label | 8a3feeb6-5bce-57be-b8e7-c3078292fad6 |  | note | Inspection/Test Method - Visual Inspection
label | 016a468e-f575-5630-a16d-5dfbd4f4075a |  | note | Record of conformity - Site and Office Inspection
label | a0e8ae7d-3b8c-58c4-9d58-ac3382dc190e |  | note | HP*
label | bb752f86-d03a-511d-84ff-723e46cdeb21 |  | note | Responsibility - Project/Site Engineer/Supervisor
date | dba43527-ddff-57f6-bb82-05b51bf52559 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Excavation Permit
label | b22648d9-7d02-580d-85cd-cdbdcad4c8ac |  | note | Frequency - Prior to commencing activity
label | 191cd235-416b-56c4-ae45-ba847c9b457a |  | note | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
label | 3fd46ef3-909e-574d-bc0a-517872f8ebd0 |  | note | Reference Documents - Approved Permits
label | aed208a1-ac7a-596e-9042-0a061c81d802 |  | note | Inspection/Test Method - Verify
label | 83a18917-fc0f-5b77-80ab-116c9821c0b8 |  | note | Record of conformity - Proof of permit & ITP signed
label | 5d722d91-8a36-5933-b731-3c1675a16b46 |  | note | HP*
label | 2368bad9-cb75-5cf3-a8ba-657e6c725e1b |  | note | Responsibility - Project/Site Engineer
date | 70234546-ef16-5344-83b2-265b140986d3 |  | date | Date Completed:
checkpoint-group |  |  | section | 2.0 - Material Approvals
checkpoint-status |  |  | checkpoint | 2.1 - Precast Structures
label | ab58fa24-f116-51e1-bb56-2a5a9c8ec0a2 |  | note | Frequency - Prior to commencing activity
label | cf5ed991-6585-57b3-b911-3d0f86fa22e2 |  | note | Acceptance Criteria - Details of the proposed precast drainage pits, headwalls, and culverts to be as specified on the IFC Drawings.
label | bdd411b2-4986-53fb-b73b-7e7c7000d1e2 |  | note | ○ Approval of the shop drawings constitutes a Hold Point.
label | dc249841-c08f-5a5f-af73-76dbf53cd354 |  | note | ○ Outline of sampling and test program
label | fed5492d-1da5-53b7-a7cf-795b5d8a04cc |  | note | Reference Documents - Cl16.6.1 & Manufacturer’s documents
label | 1301e68d-a0a5-5b05-bcea-f42d62c4a43f |  | note | Inspection/Test Method - Document Review
label | 727e61f8-7fd4-50b5-a15d-86daf5052d56 |  | note | Record of conformity - Aconex Correspondence
label | 0599f0ff-d4c6-5ff8-8896-4d09cc6f8ea3 |  | note | HP
label | 60e01000-b791-57e5-bb2f-4f7d4d1ff2ac |  | note | Responsibility - Project/Site Engineer
date | 2794c579-9153-5731-8224-ae2a4141554f |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.2 - Access Cover and Grates
label | ee79c773-1a56-5fe8-899f-c58377ade254 |  | note | Frequency - Prior to commencing activity
label | 738d9405-acdd-56c8-ba83-7a8e734ab43c |  | note | Acceptance Criteria - All Pit covers to conform to AS 3996 and the applicable load class to be as noted on the Drawings. For all drainage pits, pit lids are to be Class D.
label | fa10de75-6a4c-5fb4-a5fb-5874320a4794 |  | note | Reference Documents - Cl16.5.7.1 & IFC Drawings
label | e579fe7a-accd-5bed-91df-d69f754eb26c |  | note | Inspection/Test Method - Verify
label | ec5278a1-6e0e-5f5b-b066-f574f2cc1a35 |  | note | Record of conformity - This ITP Signed
label | 26f47815-84b6-555e-8d46-79bb5eaf571e |  | note | HP*
label | 01dc8e7e-e7f0-55ad-8db3-4ececbf30b27 |  | note | Responsibility - Project/Site Engineer
date | bd40906a-f0ca-51cc-ad66-83ab99c6018f |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Box Culverts Bedding, Side, Overlay and Backfill Zone Materials.
label | 688061a6-81b0-559a-8250-397751cc1678 |  | note | Frequency - Prior to commencing activity
label | f4a418bf-6ffb-5a9d-aba5-c09c320a74ba |  | note | Acceptance Criteria - Materials are to be compliant with the requirements detailed in Cl.16.5.6. Material submission approval.
label | 38053ff1-cd39-5fdf-8ce8-f5930d7b639e |  | note | Reference Documents - Cl16.5.6 & 16.6.2.2
label | 16451f44-84f4-5e7c-9a14-7a0da0f8e1d3 |  | note | Inspection/Test Method - Document Review
label | 30b99241-d916-525a-bfc3-2d08052484b7 |  | note | Record of conformity - Aconex Correspondence
label | 2eb85dda-ae6a-50fa-bbfb-e924fb5d65de |  | note | HP
label | bb4d22c6-594e-5e4e-a331-0681ccdd570c |  | note | Responsibility - Project/Site Engineer, Beca
date | 7fcdd18b-5de0-57e4-9b71-aaa4a4660761 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.4 - Blinding for Drainage Pits and Headwalls
label | 2cdc4b40-de5a-5ded-8076-77119d0265f3 |  | note | Frequency - Prior to commencing activity
label | a24482b1-7c81-59d4-a748-46579e1d29c8 |  | note | Acceptance Criteria - Approved bedding material as per IFC Drawings.
label | 783bb8e2-be87-5037-9220-8c38c2c4dd3c |  | note | Reference Documents - IFC Drawings
label | f44ffccd-5943-5302-aed5-53db29ae97ce |  | note | Inspection/Test Method - Document Review
label | 63f4a899-fbd9-5678-a97e-10b5d6ed1165 |  | note | Record of conformity - Aconex Correspondence
label | e90d6749-9565-5df0-b4c1-b94133094ae9 |  | note | HP*
label | 930504cd-e750-5cfb-b16e-1becd7073c2d |  | note | Responsibility - Project/Site Engineer
date | 11bca55f-d813-5454-a26b-d1954d7f4432 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.5 - Geotextile Fabric
label | 0951a30d-bcd5-5f82-bef2-ba9a2aad8644 |  | note | Frequency - Prior to commencing work
label | f891fcef-102e-5a05-8555-ad08670e8ccb |  | note | Acceptance Criteria - Non-woven type complying with the requirements of VicRoads for first stage filter.
label | 24b2885c-192f-549e-802c-228765e85054 |  | note | Reference Documents - Cl.16.5.8 & VicRoads Section 702
label | c630faca-13d4-560f-830e-3f4aa85bed97 |  | note | Inspection/Test Method - Verify
label | 1294c6fe-f4d9-590b-9f86-0f6f852ba88a |  | note | Record of conformity - Visual Inspection & Delivery Docket
label | c0d53522-9130-5af2-a8d7-de0dc81e3b98 |  | note | IP
label | 4dba0165-a49b-5344-86bc-0d5dd9ac3264 |  | note | Responsibility - Project/Site Engineer
date | b2b17873-ad3d-59da-a630-c012a3d50118 |  | date | Date Completed:
checkpoint-group |  |  | section | 3.0 - Material Receival
checkpoint-status |  |  | checkpoint | 3.1 - Precast Structure Delivery
label | 510d066f-aaad-521c-acd0-6ab33d93d77d |  | note | Frequency - Each Lot
label | dd9eb527-123d-5ff3-8a1d-3dc9615eb7ee |  | note | Acceptance Criteria - Ensure each precast component is inspected upon arrival ensuring:
label | 07b2c205-7888-5b47-92a6-db01e80e6c1d |  | note | ○ Dimensions are as shown on manufacturer drawings.
label | 7cc21e09-88cc-50a3-9e6f-0ca3fb4973b0 |  | note | ○ All blockouts in correct positions and to dimensions.
label | 135c1ef7-713d-5cc5-ba69-8ad6e14a1ce1 |  | note | ○ No damage to any precast structure component to the satisfaction of FH Engineer
label | 8d9ffef1-ea02-531e-8f73-963f781550bf |  | note | ○ No modifications to the pits are to be made without written approval from manufacturer.
label | 5074dbb4-fe4f-5a86-8c38-d55d527c200c |  | note | ○ Manufacturer’s conformance report
label | 6d2e38b7-5e7a-579b-98aa-27efa490fb76 |  | note | Reference Documents - Cl16.6.1 & IFC Drawings
label | 16726ebd-142c-5e2d-94c3-c144f08e5ef2 |  | note | Inspection/Test Method - Visual Inspection
label | 315da72d-1ceb-58aa-8eff-c1fd0d60823b |  | note | Record of conformity - Order Acceptance Form
label | 59a9abc0-badd-59c7-8e34-ca95cacf72b3 |  | note | HP*
label | 0f267815-5dc3-5586-9e6c-2588f0be04e8 |  | note | Responsibility - Project/Site Engineer
date | 9b599835-4289-5d69-b59b-6d98ad2786ab |  | date | Date Completed:
checkpoint-group |  |  | section | 4.0 - Drainage Pit, Headwall and Culvert Installation
checkpoint-status |  |  | checkpoint | 4.1 - Survey Setout
label | 96f73f4c-1ddb-5ecf-8655-9ec86c40c259 |  | note | Frequency - Prior to construction and each lot
label | 80120edb-cad5-57b6-b432-a9dfba621b6a |  | note | Acceptance Criteria - Set out the drainage structures as shown on the Drawings to identify the locations, lengths and levels:
label | eaaa0d90-e5de-575a-bd91-aeb0a7373072 |  | note | ○ All pits, and inlet and outlet structures.
label | c40a009b-6410-5c62-97aa-7dbe26d35a79 |  | note | ○ Ends of wing walls and headwalls.
label | 15456013-b6fe-5a16-8b34-9444a9a3f601 |  | note | ○ At outlets and inlets of box culvert structures.
label | 739131ea-764e-5029-b752-a70fa5c75714 |  | note | – Setout of each drainage system to constitute a Hold Point.
label | 6c41b77b-65df-5b8e-9a67-f535ee05e9e9 |  | note | Reference Documents - Cl16.7.1
label | 1f07cdb5-abfd-522c-b9e8-564f84f66c66 |  | note | Inspection/Test Method - Survey
label | 16a01d25-681e-5993-bc13-59adf1d5e086 |  | note | Record of conformity - This ITP Signed
label | 219b5388-f45e-56f4-a1df-a87748de4426 |  | note | HP
label | 14944d7e-92c0-52a4-bacf-e90676402f30 |  | note | Responsibility - Project/Site Engineer, Beca
date | fa7a906f-cd3c-519d-84f4-67963423f62e |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.2 - Excavation
label | 1176e267-a531-5cdd-b74e-306ee86a5a72 |  | note | Frequency - Each Lot
label | e374136f-55f7-5a35-86e5-f75d59b8c3a4 |  | note | Acceptance Criteria - Excavation to be performed to the minimum depths, widths and batter slopes as shown on the Drawings, regardless of the type of material.
label | 1a9ec8b6-abbe-5c22-9433-db8811c2a6dd |  | note | Inspection of completed excavation works to constitute a Hold Point.
label | d8d48fdc-af48-5f58-80f8-c3a8dd8d7a41 |  | note | Pits:
label | dde9fb29-d00c-5e0f-80d9-470fd164b600 |  | note | ○ The shape of the excavation to be as required and the size sufficient to enable construction of the structure.
label | ccdb8dbb-6936-568e-baa8-372a04b9834d |  | note | Box Culverts:
label | c5d4529e-db4c-5d84-959d-20a5f2f5efb7 |  | note | ○ The width of trench to be not less than the exterior width of the culvert plus 400mm, and not greater than that required for satisfactory backfilling.
label | d9f522df-c5ed-5ac9-9d83-0fa5b613c708 |  | note | Reference Documents - Cl16.8 & Cl 16.6.2.2
label | 571c1da6-a91a-5fa3-a70c-66ec3ae68a74 |  | note | Inspection/Test Method - Verify
label | c6c80ad7-00a7-5073-908c-c069c67ae74c |  | note | Record of conformity - This ITP Signed
label | 94484256-bf2c-5fd8-b6dc-a6317e71bd2a |  | note | HP
label | 8fe370bf-550c-5878-b7d3-9a205bf1b3bb |  | note | Responsibility - Project/Site Engineer, Beca
date | e6b7dcc7-0c07-58c8-8026-1f909adc8449 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.3 - Confirm Ground Conditions
label | b8d350c1-8ff5-5b96-973a-67f22efdb856 |  | note | Frequency - Each Structure
label | 20e25821-d580-5c2e-b669-b1ad3bb75e5f |  | note | Acceptance Criteria - 1 x DCP test to be undertaken per drainage structure to confirm ground conditions.
label | 36164437-c5cf-56ae-9d48-c40a20b3ed9a |  | note | ○ Contractor to notify the Contract Administrator of any area of the foundation with inadequate material to support the proposed drainage structure. Inadequate material is deemed to have a bearing pressure less than 130kPa, equivalent to 4 DCP blows per 100mm, as per note 4 on drawing ZULU-BECA-012- DWG-07102.
label | 2f1f7b49-708c-5f8c-a252-fe31b08cae2d |  | note | ○ Inadequate foundation material is to be replaced with a layer of coarse crushed aggregate compacted to 95% relative standard compaction to AS1289 Section 5.5.1 over a geotextile Bidim A29 or approved equivalent.
label | 2350b2d8-7113-5a27-a640-aeecc9cfcaee |  | note | Reference Documents - Cl16.8.2 & Tender Clarification #38
label | ea4ce89e-4f55-53c5-bd51-7609dc2a8f82 |  | note | Inspection/Test Method - Site Inspection
label | 2423809a-6b01-53b2-8e5b-8dd890b86fdd |  | note | Record of conformity - DCP, Test Results
label | 06e8b35d-cbaa-523b-9400-83dc0bda6785 |  | note | TP
label | 6c53e3f2-cb75-566e-aa85-9477e2f68835 |  | note | Responsibility - Project/Site Engineer
date | 0414f3d0-9444-5ffb-b0fa-d989cc17b6be |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.4 - Blinding for Drainage Pits and Headwalls
label | bcad1afe-016b-5246-927e-c5f03a90f683 |  | note | Frequency - Each Lot
label | b55575d8-14b3-5e3f-8751-50467135ca28 |  | note | Acceptance Criteria - Blinding to be installed as per the depths and widths shown on the Drawings.
label | 45ac2b98-d9a1-5003-b229-0a8f31ab2df2 |  | note | ○ Pits: 50mm Crushed Rock bedding
label | 89a61e11-443b-50b1-8d5a-9700e1abaa68 |  | note | ○ Headwalls: 100mm 15MPa Concrete blinding and 600x150mm apron cut off wall
label | ebd7362e-49bf-5a7b-9ffb-9e0d8661adbc |  | note | Reference Documents - IFC Drawings & VicRoads SD
label | 0e10937e-f79f-5a21-a6a5-a510f354efb2 |  | note | Inspection/Test Method - Verify and Visual Inspection
label | 7f27ad83-67f0-59e9-b805-d75ab259c9b1 |  | note | Record of conformity - Delivery Docket & This ITP Signed
label | dc4048a4-91fe-5f55-ada0-70be55bd2a52 |  | note | HP*
label | d9ac6299-f974-558c-b572-02ef9cc116d3 |  | note | Responsibility - Project/Site Engineer
date | f8ec5fdd-ff5b-5701-9419-f7ff43c7b7ef |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.5 - Bedding for Box Culverts
label | f6104982-9dea-5959-98f6-70237c3d3dd8 |  | note | Frequency - Each Lot
label | 4fa34d6c-f014-5a38-beb1-1c3e335ffd31 |  | note | Acceptance Criteria - Bedding material to comprise of approved select fill and to be placed for the full width of the trench.
label | 42c26375-9a6c-569e-9359-fb0c5cfd5717 |  | note | ○ Upon completion, the bedding is to provide a uniform firm foundation with the top surface of the bedding shaped to the details shown on the drawings. This to constitute a Witness Point.
label | 14025ba8-9afd-54e8-be08-4d2e8e8a27af |  | note | Reference Documents - CL16.5.6. 1
label | 20d97cde-028a-5067-846d-c4bcc652d396 |  | note | Inspection/Test Method - Verify and Visual Inspection
label | 18606999-4387-52e4-a1c1-37ccd808471b |  | note | Record of conformity - Delivery Docket & This ITP Signed
label | f52e261e-1bef-5aa7-8741-0bb3dabc2c2b |  | note | WP
label | 61c2e6db-e12f-5367-ad8e-43d826fcc22d |  | note | Responsibility - Project/Site Engineer, Beca
date | 34b4a718-4ed3-563b-bec5-2a949aab05dd |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.6 - Positioning of Precast Structures
label | 11f1ce0f-933d-5c66-b10d-8ca75e1a0230 |  | note | Frequency - Each Lot
label | cc95c182-f51a-5dd3-8794-6c3a70be63aa |  | note | Acceptance Criteria - Precast structures installed as per survey set out points marked on blinding / bedding layer
label | df1710e5-23d8-5ac6-b0a9-32a51a5dfb01 |  | note | Reference Documents - Cl.16.8.1 & IFC Drawings
label | 52618993-76b4-5fe0-b5ec-760dd3780ed4 |  | note | Inspection/Test Method - Verify
label | d0e4ca64-9106-55b0-a47a-48a846c16bf7 |  | note | Record of conformity - This ITP Signed
label | 62ffd668-108d-5f05-a822-06fac03094e8 |  | note | IP
label | 5ef51f22-b49d-5375-87c3-b02487c59eac |  | note | Responsibility - Project/Site Engineer
date | ac26066b-3fa6-50e3-bf9c-b1f302782640 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.7 - Backfill Materials for Box Culverts
label | f797f376-3caa-58b0-bd53-dfce5ebb7902 |  | note | Frequency - Each Lot
label | 4fa89b10-99b2-50e1-818a-1cb940c0473e |  | note | Acceptance Criteria - Side Zone, Overlay Zone and Backfill Zone Subject to Vehicle Loads
label | d2e1e579-fd48-5bdc-aee0-64eb6b1073a6 |  | note | ○ Approved Select fill material.
label | 068414fc-e61e-512c-b7b3-bd93288de40b |  | note | ○ Completed in layers with maximum thickness of Cl200mm loose material.
label | 29ef28c6-caad-5e95-a851-4720cb916273 |  | note | Overlay and Backfill Zone – Not Subject to Vehicle Loads
label | 39bc908f-7787-552e-9edc-bcd4afe87479 |  | note | ○ Ordinary fill material compliant with Cl.16.5.6.3 of Beca’s specification
label | 5f59707d-fbdf-5d92-aa4c-011a03990d19 |  | note | Reference Documents - Cl.16.5.6 & IFC Drawings
label | 04391806-868e-55c2-967c-a5a34dd0621a |  | note | Inspection/Test Method - Verify and Site Inspection
label | f87b33fe-04c5-5d60-8d00-8d73cafd1cb8 |  | note | Record of conformity - This ITP Signed
label | 32827412-ef03-5eae-97ff-c2b0e931a375 |  | note | IP
label | 23df4aec-6efa-5a2b-bcf0-63d5419c08b5 |  | note | Responsibility - Project/Site Engineer
date | 3d43666e-c673-5375-aaad-1c98ed6901b8 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.8 - Compaction Requirements (Box Culvert)
label | 98400f66-d4ff-57da-81dd-2aa44bd1cdbf |  | note | Frequency - 1 test per lot.
label | e82ad8bb-5d63-55ba-b493-617779f660fa |  | note | ○ "1 test per layer of bedding for bedding materials and every 2nd layer for side, overlay and backfill zone materials."
label | 6505258c-50fe-5498-909a-6ec23215c323 |  | note | Acceptance Criteria - Bed Zone – Minimum 90% SMDD
label | cdbf78aa-742b-5d44-acd4-73ad8c9d8c0a |  | note | ○ Side Zone Not Subject to Vehicle Loads – Minimum RD of 95% SMDD
label | 224642d9-8551-5dfa-9f37-38db447150ec |  | note | ○ Side Zone Subject to Vehicle Loads – Minimum of 95% SMDD
label | 7185abd0-f6b6-5e6d-9992-fe193d868633 |  | note | ○ Overlay and Backfill Zone Not Subject to Vehicle Loads – Minimum 90% SMDD
label | 20b777a5-0948-5cab-a93d-a92f0a9be3d4 |  | note | ○ Overlay and Backfill Zone Subject to Vehicle Loads – Minimum 95% SMDD
label | a6406e74-85d9-50e7-bb1f-e5c15ddfa32d |  | note | Reference Documents - Cl.16.5.6. 1 (b) (iv)
label | c3136cf7-8b38-5165-872c-2c5d937abe76 |  | note | Inspection/Test Method - Site Inspection
label | db9b4411-efa6-5856-af78-2ea2b9335782 |  | note | Record of conformity - Test Records
label | f82995cc-38b0-5b15-a358-a96ca9566be0 |  | note | TP
label | 473aac9c-b16d-5edb-bb4d-33375d1f8a79 |  | note | Responsibility - Project/Site Engineer
date | d5d91f95-4800-5240-bfec-fc3ad1f31973 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | 4bfba408-c2c7-5b13-a5b6-2aac8afb6c80 |  | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
text | bd8aa650-6082-5eb0-9fb1-0784fb190a53 |  | textbox | Print Name:
text | 07933e25-3d1e-5871-b20e-a61376c04a4e |  | textbox | Position:
date | 94923ded-cd73-539a-81ee-c1c46804e037 |  | date | Work Completed On:
date | 9c06ea5a-c74f-5bfa-9993-ce5fe6ee7f38 |  | date | Date:
checklist-sectioned |  |  | checklist | ITP003 - Stripping Top Soil and Bulk Excavation | itp |  |  |  | Yes | FH-ZU2-QU-ITP003 - Stripping Topsoil and Bulk Excavation - Rev 0 | 5645e9f5-3660-4c90-a71c-b1ba3bd279a6
checkpoint-group |  |  | section | 1.0 - Preliminary Activities
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | b0bf35cf-bf6c-5dcc-bc41-0235c9052364 |  | note | Frequency - Prior to works
label | e04509c7-936f-53e0-8fb6-f7bcc1a327ea |  | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
label | fdc5d8e3-669e-5553-b761-b07e1a397496 |  | note | ○ Using the correct and complete set of drawings.
label | 48eb929d-4aad-5b25-ae8d-1d7116fe3a1a |  | note | ○ All drawings are the latest revision
label | 6ca6d629-4784-5861-a79c-4c0ba3d6f4eb |  | note | Reference Documents - Aconex
label | dd16b1cc-ab12-505c-a2b7-7bb53fe3bd1d |  | note | Inspection/Test Method - Visual inspection
label | 2d9a6b90-f30a-5624-8211-191e8989370d |  | note | Record of conformity - This ITP signed
label | cc09c387-0c2f-5dda-adea-a8ef80176672 |  | note | IP
label | ea4975d0-50ea-5d69-bb76-c1968543b9ce |  | note | Responsibility - Project/Site Engineer
date | cf4ecca4-eaeb-5bec-9d03-95e47a4cca08 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | a1c6b7af-0051-5b47-adee-2ba83b1e11a9 |  | note | Frequency - Prior to works
label | 0fbcefe2-64ad-51a3-9613-d315fef28308 |  | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS and WP.
label | e4c9d16e-a953-5b9b-9a45-8877156edfba |  | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
label | 7d8cb712-2e8a-5a0d-a8b0-c44a5c45ec04 |  | note | Inspection/Test Method - Visual inspection
label | d25d94ff-7601-53b0-919b-c613f70f2323 |  | note | Record of conformity - This ITP signed
label | b7a0ec80-5f8e-587f-834b-1d098369588f |  | note | IP
label | 0a63dfdf-bbf5-580e-a8d0-ae9bf172ca29 |  | note | Responsibility - Project/Site Engineer
date | 72eda7e5-1afb-5c67-acd8-196c3e10781d |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Survey
label | b28ddb15-dca5-55f8-87fa-e72f19e92a7a |  | note | Frequency - Prior to works
label | 8f6fc471-c5ab-56c6-92c3-cdc17da61ba1 |  | note | Acceptance Criteria - Area has been surveyed, highlighting any areas where excavations should not occur (e.g. exclusion zone).
label | 895ea11a-326a-5b69-9652-f24fcd91fd48 |  | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
label | d8337aa2-37fe-515d-b4f3-1bacfc84dc3c |  | note | Inspection/Test Method - Visual inspection
label | 7717e169-d754-5552-bb9d-d4f6f8d10b45 |  | note | Record of conformity - This ITP signed
label | eb0c37fb-eed5-5944-85a7-b335db33ccc5 |  | note | IP
label | fd3a1bf8-2181-59f0-ac7e-d79f06a26e54 |  | note | Responsibility - Project/Site Engineer Surveyor
date | bf4564b4-0f61-503c-bcf3-02eccb92fc4f |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.4 - APAM permits
label | f25c9f2a-2ac1-560f-9017-7b5a7084fae8 |  | note | Frequency - Prior to works
label | 24dd5cb6-1f04-5f82-a4dd-46e652983d3d |  | note | Acceptance Criteria - Excavation permit issued. If working near HV electrical, an Electricity supply Isolation form and cabling permit has been issued from Melbourne Airport.
label | 9212205d-6ac3-54ab-8fc9-fee1a896df2e |  | note | Reference Documents - Excavation permit
label | c8d42d6b-eab7-5cb6-8755-e20453f295ab |  | note | Inspection/Test Method - Approved permits
label | cd6b0421-3dd9-5c4c-b73a-de6b1c4ef85c |  | note | Record of conformity - This ITP signed
label | 8c0fd384-a553-5a21-86d2-9c2ae1ecfe59 |  | note | HP*
label | d444af54-ebc2-5cb7-8451-2ffc6d07021f |  | note | Responsibility - Project/Site Engineer
date | 8be9d07d-a5ae-5841-b757-795c9b56f251 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.5 - Fulton Hogan Permits
label | 46947f88-5c71-5c7e-b717-22cd2b1a7fc2 |  | note | Frequency - Prior to works
label | 71e0ef47-8be4-5ac0-962e-604e87161e84 |  | note | Acceptance Criteria - Fulton Hogan Excavation permit issued to plant operators prior to excavation works. Native Grass heatmap issued and boundary of working area has been set out.
label | 6f1796c9-4d05-53e0-bdde-821c5592e2a9 |  | note | Reference Documents - Excavation permit
label | d8325656-3f12-56e1-b210-0d4b6ceac6e5 |  | note | Inspection/Test Method - Approved permits
label | 4967b778-ff83-52d9-ba59-8cdfef0f275f |  | note | Record of conformity - This ITP signed
label | 286d6d2b-0311-53eb-ab23-9f4d05737f61 |  | note | HP*
label | e52bf27e-db56-57ab-bf83-dafe2c698d6d |  | note | Responsibility - Project/Site Engineer
date | eee46c57-60e0-571e-a3f7-97999f76db52 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.8 - Plant and Equipment
label | 725e528d-8b52-5ff5-85fb-0ada1e94e3c8 |  | note | Frequency - Prior to works
label | 85884f2f-55a6-5be8-9305-0ab219e520c7 |  | note | Acceptance Criteria - Plant and Equipment used in the works are appropriate to achieve specifications requirements. All plant inducted and inspected as per Fulton Hogan’s plant safety guidelines.
label | 0c019c51-0614-53a0-a154-a2497f8f1c0a |  | note | Reference Documents - WMS - 003
label | 49aa4a47-fa8b-5fc8-9e34-53bd8059363b |  | note | Inspection/Test Method - Visual Inspection
label | 6f0ef1fb-f190-53d8-bb13-c894ce09a267 |  | note | Record of conformity - This ITP signed
label | 1200834b-44a9-5646-b802-8fb932cef07a |  | note | HP*
label | acb14978-a615-5ab1-b64f-c6ca52037d13 |  | note | Responsibility - Project/Site Engineer
date | d2181fa4-4cd9-5c12-8779-31f6d7c56cc6 |  | date | Date Completed:
checkpoint-group |  |  | section | 2.0 - Stripping / Bulk Excavation
checkpoint-status |  |  | checkpoint | 2.1 - Site Preparation
label | e27a247b-1e88-5f51-a280-e8299a920aef |  | note | Frequency - Each lot
label | 0a25fe0f-b005-5d68-9994-e63d04d72117 |  | note | Acceptance Criteria - All excavation and filling will be free draining to low points clear of the Works. Sufficient pumps, well-points or other equipment for work area de-watered during the works shall be provided where required. Existing drainage lines and water mains found to be traversing the site must be removed as shown on drawings. Contractor must provide temporary pollution control devices or ponds in existing drainage systems and receiving waters.
label | fb794ab0-50c9-5a06-9d65-96021ddcebff |  | note | Reference Documents - ZULU- BECA-001- DWG-00001 to ZULU- BECA-005- DWG-01119
label | 57f65844-de94-507d-8927-bfcd2dc9e32f |  | note | Inspection/Test Method - Visual Inspection
label | de7135f9-ef45-53c4-a19f-d3aee6734303 |  | note | Record of conformity - This signed ITP
label | 1e268370-06e4-51b0-93f7-5fe806d0e603 |  | note | IP
label | fdf1cd7f-ee62-5ff2-92da-3766f85b1d48 |  | note | Responsibility - Project/Site Engineer
date | a585c59e-e787-55aa-92e0-4d29ff87e6d7 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Dust & FOD control
label | 4d67a5f8-2cd4-5cd9-9125-ce8a13c6a8e4 |  | note | Frequency - Each Lot
label | 9d8de3bf-fc2b-5dc9-a674-f8c8cc422829 |  | note | Acceptance Criteria - Prevention of dust during earthworks and subgrade preparation. Sweeper onsite at all times to manage dust / FOD.
label | 4ad3cfa1-c539-5aed-8a56-1a9ecdfb9de9 |  | note | Reference Documents - Site ECP
label | c801db41-4373-5367-9606-050abb383544 |  | note | Inspection/Test Method - Visual Inspection
label | ffd00528-9efe-5abc-885c-e0a0693ef0cd |  | note | Record of conformity - This signed ITP
label | 191ac37f-fb65-59aa-9cf7-0486937f3484 |  | note | IP
label | 8e80ef2a-479d-5ee0-bfd4-90df9d4824b1 |  | note | Responsibility - Project/Site Engineer
date | 58934db1-aab0-59e1-af23-b9571dc42add |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Stripping Top Soil
label | a2cb99da-1e4a-5761-888c-818826c7f6f0 |  | note | Frequency - Each Lot
label | 795111e8-641b-57d4-817c-253a3653277c |  | note | Acceptance Criteria - Prior to bulk excavation, site shall be stripped of all topsoil and organic matter as shown on the drawings. Spoil to be taken to Gate 11.
label | e90c0149-9f06-5f8a-befe-fb458a02b66b |  | note | Reference Documents - WMS - 003
label | 58244c20-c81e-55b3-810d-ca191ccd8952 |  | note | Inspection/Test Method - Inspection Point
label | 544ed1e8-6d34-59ab-93b7-0c67e29edcbe |  | note | Record of conformity - This signed ITP
label | b8aec92e-8e8a-5dac-95b4-9a205065a43a |  | note | IP
label | b77161e9-7ad9-5ed9-bb01-df12fda98a3b |  | note | Responsibility - Project/Site Engineer
date | f8d6de4d-e30d-5464-bfc8-fdf096736fcf |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Excavation
label | 655ef21e-d583-540b-b0e8-1ae4f87f9ef6 |  | note | Frequency - Each Lot
label | fd71f423-e2b8-53ba-bbee-19f9db30e125 |  | note | Acceptance Criteria - Bulk out subgrade to 100mm of subgrade. If rain is imminent, ensure subgrade is left 100mm high prior to trimming.
label | c7cc11d3-553d-5d81-b8f0-0f6f1407a670 |  | note | ○ Rocks Under <800mm can be taken as mixed fill to Gate 11
label | 623c6037-b637-5187-982a-aec791a42130 |  | note | ○ Rocks >800mm to be sorted and taken to Vic Civil
label | 00c8d2f8-9d2e-5735-9cec-8d01d06b07aa |  | note | Reference Documents - WMS – 003 Spec 001 - Cl8.5.3
label | 14dccc02-a646-50f9-8f6d-32f24959c516 |  | note | Inspection/Test Method - Inspection Point
label | 5d396ef6-eb80-5b2a-b64b-d36b8ef0cd6f |  | note | Record of conformity - This signed ITP
label | f0aa852a-6306-543b-81bf-7bb4fe5f8563 |  | note | IP
label | 5d0cec04-02dc-5c0f-8bfd-6084f48216a9 |  | note | Responsibility - Project/Site Engineer
date | 55143d0a-4292-5671-8588-0096dd2b279b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.5 - Batters & Temporary Support
label | 0078066f-7ff2-5a7e-8bd0-f096e2d634ee |  | note | Frequency - Each Lot
label | a9d660c2-8e06-58b0-819c-137e62261509 |  | note | Acceptance Criteria - All batters to be kept at 1:1. If not, temporary support will need to be designed, engineer and approved for use. Temporary support will remain in place until it is no longer required.
label | 29b426b8-1462-5593-8f23-9614a99f34eb |  | note | Reference Documents - WMS – 003 Spec 001 - Cl8.5.3
label | 126bb257-8287-5830-aac8-804f9eb9a3ce |  | note | Inspection/Test Method - Inspection Point
label | 2c813702-c8eb-5da1-a4cc-6123c2135816 |  | note | Record of conformity - This signed ITP
label | 087bd442-d3ce-5bd3-a28d-e96e359893d3 |  | note | IP / HP* (if required)
label | 391bd648-17fe-558b-a9e4-f3742978176b |  | note | Responsibility - Project/Site Engineer
date | 5b4b410e-8682-530d-bb89-ffc8cee3cc2a |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.6 - Excavation – Detailed Trim
label | 409c906c-8df3-5ce5-baed-d2848aa53b27 |  | note | Frequency - Each Lot
label | 6c4e7036-00b5-55de-ae66-e0e7d66c0a00 |  | note | Acceptance Criteria - Detail trim Subgrade with excavator / dozer
label | 261f738f-711f-58c1-9b34-cd5f799091d7 |  | note | Reference Documents - WMS - 003
label | c48ff060-151e-56f8-8dbd-337de1a3b9d6 |  | note | Inspection/Test Method - Inspection Point
label | 857f60cb-c4f5-52c7-a914-3d2c5f25ef5e |  | note | Record of conformity - This signed ITP
label | d00655ce-58a8-571d-a4f0-17a5c069092c |  | note | IP
label | 2e518698-e4ba-51be-a036-130fbe55bbbe |  | note | Responsibility - Project/Site Engineer
date | b7c1f4d5-948f-56cc-8b7f-1d61781f5e30 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.6 - Contaminated Materials (if found)
label | 67d60ac1-c767-5cea-b33a-9c957fe6607c |  | note | Frequency - Each Lot
label | 7449cf1a-8fdd-5cbe-ae73-f35efccbcd1c |  | note | Acceptance Criteria - If contaminated or hazardous materials are found, immediate notice is to be given to the Principal’s Representative. These include the following;
label | 18a1b02f-fa5f-5c4b-b29e-8f690d0c20a9 |  | note | ○ Asbestos or material containing asbestos;
label | 0e601b8e-85e3-5a48-a95a-ce16b3c42b43 |  | note | ○ Flammable or explosive liquids or gases;
label | 2ffaae20-313d-56b8-af17-0013db1ffe64 |  | note | ○ Toxic, infective or contaminated materials;
label | 62627aff-bf7a-5503-aaa0-559e22ae8235 |  | note | ○ Radiation or radioactive materials;
label | 07a861b9-fcc3-52fa-867a-fdd1a56a7642 |  | note | ○ Noxious or explosive chemicals; and
label | ea990217-0df6-564d-b132-aaf6c7ce482c |  | note | ○ Tanks or other containers which have been used for storage of explosive, toxic, infective or contaminated substances.
label | 37992f1d-ea50-5adf-8ffe-baa1ff457dd3 |  | note | ○ High levels of PFAS
label | 2b53e1b2-cddd-5f0b-ad08-820e0dc38a18 |  | note | – Agreed removal location to be confirmed with Principles Representative.
label | 9480a3e7-6a36-5ce4-ae96-c773283c46a8 |  | note | Reference Documents - WMS - 003
label | c114f601-e3b3-5150-891f-fd79140ee62f |  | note | Inspection/Test Method - Inspection Point
label | 544d69e3-e333-556a-a981-ea4bfb155186 |  | note | Record of conformity - This signed ITP
label | a5480ed3-09c5-55d5-9668-ff3b1e52ce26 |  | note | HP*
label | 1ec73940-2fe9-55e5-ae19-877a013ce1a4 |  | note | Responsibility - Project/Site Engineer
date | cae0531d-97c9-55cc-8a76-caf2995f702c |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | b663b21c-3dfa-536b-b178-91b4f1c37e18 |  | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
text | ee31d79b-0f59-5a23-82d1-8fe5dd6ec31c |  | textbox | Print Name:
text | 664f83e7-742d-544a-9d95-9b5f459e4f81 |  | textbox | Position:
date | b8ae34f3-9bd9-5e79-9bd4-5cef927f9b58 |  | date | Work Completed On:
date | 3fe6fc4e-f7a1-5d0e-aa19-8fd21eac62dd |  | date | Date:
checklist-sectioned |  |  | checklist | ITP008 - Lime Stabilisation Works | itp |  |  |  | Yes | FH-ZU2-QU-ITP008 - Lime Stabilisation / Subgrade Improvement - Rev A | 5944a9b8-0892-4aee-a2d9-d710cab1086d
checkpoint-group |  |  | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Materials and Trials
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | f80ad63e-e054-58a6-a576-5a5156f8f8f3 |  | note | Frequency - Prior to commencing works
label | 34372137-72c1-5b78-8857-0f4f56117113 |  | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy. Current Revision to be obtained via Aconex
label | 580de26a-94ed-5a77-9d34-68c0de8454b4 |  | note | Reference Documents - Aconex
label | 5884289d-b391-508f-8f26-6eb97aee0dc9 |  | note | Inspection/Test Method - Visual Inspection
label | 2221d813-5b0e-555c-b17a-b06903a82588 |  | note | Record of conformity - This signed ITP
label | 1641ee97-6204-5c83-9048-3a8b6c09dcc5 |  | note | HP*
label | 0916181f-7bd9-570f-ba06-450763029d6b |  | note | Responsibility - Project/Site Engineer
date | 3a82f130-c2e3-5900-9703-54d723e73696 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 2c1d7258-8000-5b31-8f79-226a154efb79 |  | note | Frequency - Prior to commencing works
label | 417cbc72-d3c4-5e70-9d6b-6d7fd9543fa3 |  | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
label | f58b910f-8b97-58b0-9ec4-8d835fad21a5 |  | note | Reference Documents - PSP, EMP, TMP, WP, SWMS
label | 16c2ed29-62a0-56d2-a6bd-dcc04d5066c9 |  | note | Inspection/Test Method - Visual Inspection
label | c098280e-eab5-5450-82a7-3064d0f70f3f |  | note | Record of conformity - This signed ITP
label | 4a2d40a3-38c1-5039-a5f4-dd646da1fe9c |  | note | HP*
label | cc8e0828-610c-5047-af96-86a758dd60ef |  | note | Responsibility - Project/Site Site Supervisor
date | 17c04995-8757-5c6f-82eb-4b3d59be076c |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Current excavation permit
label | 48755452-95f8-5c14-a233-f2e1cf26d6fc |  | note | Frequency - Prior to commencing works
label | b01f95de-178b-54ed-aeb7-b45562fdd472 |  | note | Acceptance Criteria - An Excavation Permit and an Isolation permit issued by Melbourne Airport. Fulton Hogan Excavation permit issued to plant operators.
label | fbbb0ee7-a34f-5610-bf1a-f5a488b2f235 |  | note | Reference Documents - Excavation Permit
label | d7fb0750-fc55-58dc-9eed-a9c56f8dc487 |  | note | Inspection/Test Method - Visual Inspection
label | 4d53328b-f3e0-5e07-9229-c4368426e0b3 |  | note | Record of conformity - Permits
label | a28cb457-3300-5049-a9dc-6df79138d9f1 |  | note | HP*
label | 16159f6c-a4d3-5c8a-9ff3-26033da1286f |  | note | Responsibility - Project/Site Foreman
date | b1e6b55d-eb1d-59ed-94ef-517a38151dd1 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.4 - Preceding Lots Satisfactory
label | 7b4d2be7-586c-5c08-92ec-a97afa14a7d4 |  | note | Frequency - Prior to commencing works
label | 5a0cab34-2cd9-5151-83c4-bffc7a581e96 |  | note | Acceptance Criteria - Review ITP004 (Select Fill placement) and ITP003 (Stripping and bulk out) has been completed to a satisfactory level
label | d8e0fc77-3146-5441-a683-eca1b40121a0 |  | note | Reference Documents - ITP004, ITP003
label | 11225a67-461e-574a-a52e-67f98e2149e9 |  | note | Inspection/Test Method - Visual Inspection
label | a50494c7-dc42-5d61-9716-1ad5c838a926 |  | note | Record of conformity - This signed ITP
label | c01588dc-e681-5eb9-ac50-cf96b17b44ea |  | note | HP*
label | 947156b6-065d-5acf-b73c-792903b506a4 |  | note | Responsibility - Project/Site Engineer
date | 2a7c5747-5127-549f-967b-707955a736f5 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.5 - Test Pits
label | 7c8519cf-ff0c-5c02-aa96-9b158f5e6e29 |  | note | Frequency - Prior to commencing works
label | 41a79849-3252-57fd-b30f-d4a68214ffbb |  | note | Acceptance Criteria - Test Pits have taken for the works area and suitable lime content parameters have been established. Test Pits should be taken at least one month prior to works beginning
label | 71daa2cc-6103-565b-b46c-98841bbca874 |  | note | Reference Documents - WMS003 – cl3.1.9
label | 57acbe24-3046-54bd-bb53-a17a9127cecb |  | note | Inspection/Test Method - Visual Inspection
label | 64134581-a21c-506b-99a9-d0d1c880f2a9 |  | note | Record of conformity - This signed ITP
label | ea9433d0-78af-51f7-94a0-b0b613798d59 |  | note | HP*
label | f22378cc-3fca-5bf0-b859-26e4d26a13d4 |  | note | Responsibility - Project/Site Engineer
date | 545db90f-ab5b-53d7-bea8-b422883bd1d6 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.6 - Stabilised Lime Content
label | f2f31c7f-52ce-57ee-9395-40c354934c6f |  | note | Frequency - Prior to commencing
label | 0e307209-0378-5981-9057-c4b66b6e204d |  | note | Acceptance Criteria - Stabilised Lime subgrade material shall have a minimum of lime content of 4% and a specified minimum strength of 20% CBR after 7 days of curing.
label | 0ad1c593-f993-5554-b867-61a4f26394a8 |  | note | Reference Documents - Spec cl. 3.3
label | dfe53d81-bbca-5d9e-8f62-4e024c45e26c |  | note | Inspection/Test Method - Testing
label | 21a7fda0-7769-5e6f-9181-6b849c545dfd |  | note | Record of conformity - Test results & This ITP signed
label | 083f471c-d4f2-5af5-aaf9-70e82188470f |  | note | HP
label | cea4568a-f969-58c2-b43b-f9e846f19f75 |  | note | Responsibility - Project/Site Engineer Principal’s Representative
date | d0ac1f16-ef5b-5c04-b294-6e28176e1e57 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.7 - Stabilised Soil Trial
label | e3d0b6f7-6262-5ae7-a116-cdf8203cc42b |  | note | Frequency - Prior to commencing
label | 2e2fcecc-d65e-5881-8a0f-c4e3d62082c6 |  | note | Acceptance Criteria - Trial of the Lime Stabilised Subgrade is greater than 500m2 to demonstrate that the Subgrade is able to meet the required specification. If trial is approved and accepted by Principal’s Representative. Tried Lime Stabilised Subgrade will form the completed Works. Principal’s Representative to approve trial before commencing Lime Stabilised Subgrade placing.
label | d9320f77-f9cf-5415-aeee-ad3e50d4eeb0 |  | note | Reference Documents - Spec cl. 3.6
label | 764a3254-a6cd-5bb3-8d96-1553077c9681 |  | note | Inspection/Test Method - Verify
label | c74c4ef1-a31a-5983-b31f-08be016efe25 |  | note | Record of conformity - This ITP signed
label | ee59310b-da9b-5b45-944b-c2caf07af9ba |  | note | HP
label | 97a2130d-f4a2-5239-b27e-9e5f00e946b7 |  | note | Responsibility - Project/Site Engineer Principal’s Representative
date | f0486ae8-36d6-593f-af18-abc1300c6ef1 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 2.0 - Subgrade Preparation & Replacement
checkpoint-status |  |  | checkpoint | 2.0 - Pre-treatment of earthworks
label | 62101956-cfd2-56c5-a143-4fcaba515afd |  | note | Frequency - Each Lot
label | ca2ab39e-38b8-5645-8e8e-460eeec59cf4 |  | note | Acceptance Criteria - Inspect subgrade that will require lime stabilisation.
label | f7698896-93d5-5474-af2c-25a6768a2d96 |  | note | ○ Subgrade that is excessively wet and/or contains rocks greater than 60mm to 100mm, subgrade will need to be removed and replaced with site won material.
label | 449ef220-c86c-57a5-9b93-86589310e7a8 |  | note | ○ No testing or proof rolls required on replaced subgrade
label | e925ddb6-f95f-555d-bd8a-84e3a6919e3e |  | note | ○ Survey to for any excessive high and/or low spots. Fill / excavate spots as required.
label | 6574d0fc-589f-501c-b9e6-d4e591f900c9 |  | note | Reference Documents - WMS008 – cl 3.2.1
label | d934765e-d9f6-599e-85ab-b2db351f6738 |  | note | Inspection/Test Method - Verify
label | 2d74c1c7-55a6-5095-a646-e3a7e197179d |  | note | Record of conformity - This signed ITP
label | 9c64b3e9-bc04-5d0a-b882-244b2a0eb039 |  | note | IP
label | 6198c2fc-43cc-59eb-be6f-1ed67fefda31 |  | note | Responsibility - Project/Site Engineer
date | fc7a943e-af06-5ce0-ad19-febd7032786d |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.1 - Rip Subgrade
label | 0ed5f65f-3dd4-572f-b3f2-fc4a6da3a75f |  | note | Frequency - Each Lot
label | 289ff85d-0e0f-52af-a6c4-b533252d1c95 |  | note | Acceptance Criteria - Prior to spreading lime, the subgrade is to be ripped and pulverised to at least 300mm to 400mm
label | 78a69a18-ef9f-5a5f-b19f-44f9a9e27cfa |  | note | Reference Documents - Cl3.7
label | 07a86b6f-2f5c-53df-9cd7-e2343a34de4f |  | note | Inspection/Test Method - Verify
label | 8ebee48c-0faa-5a95-8e7a-c814d37c73e5 |  | note | Record of conformity - This signed ITP
label | 8987659c-3dd4-56df-8cee-3eafa73c79e0 |  | note | IP
label | 0978e5f5-b066-569d-8337-01eadd85b626 |  | note | Responsibility - Project/Site Engineer
date | e412f8a9-a9a1-5572-a8f5-fca294ade8de |  | date | Date Completed:
checkpoint-group |  |  | section | 3.0 - Layer Placement
checkpoint-status |  |  | checkpoint | 3.1 - Layer Parameters
label | 99e44411-a4ad-5fcb-830f-e0d514ee55f7 |  | note | Frequency - Each Lot
label | 9668753c-07fd-5ae3-9a2d-500b9dad8b2d |  | note | Acceptance Criteria - Summary of Layer Parameters:
label | e7987681-aecf-5adf-9e89-02b191d8bde4 |  | note | ○ A Lot is defined as one days production
label | fddf2ea4-53ad-52e6-9b97-31c9a6cd1f6a |  | note | ○ Min depth of 300mm for PT01, PT03, PT08
label | 0b2f3865-99cd-5ea6-a77a-5b4f53aada8e |  | note | ○ Min Depth of 400mm PT02
label | a12d4f6f-4b99-52bd-a159-699b10b67c91 |  | note | ○ Shape: <12mm over a 3m straight edge
label | 042cf666-81dc-5ef0-a900-b9ebf2205b1a |  | note | ○ Surface Level: -25mm to +0mm
label | d55ac57e-4ef5-53a8-a429-8559b87327f8 |  | note | Reference Documents - Cl 3.16
label | f37964be-4804-592f-8472-6ac8abb7c365 |  | note | Inspection/Test Method - Verify
label | b6018f76-a667-5ba2-857f-b65ce20ea6e5 |  | note | Record of conformity - This signed ITP
label | 4244dc42-aa65-5ad0-b98b-0e643ce23f76 |  | note | IP
label | ee8912da-58a6-5c54-a045-2dcd5397f24e |  | note | Responsibility - Project/Site Engineer
date | 70f4e856-2faf-59ca-9345-bdf1a240d1f2 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Prior to Works Starting
label | f09b7eeb-84a5-5d2c-a892-80da7ab3a55c |  | note | Frequency - Each Lot
label | 8c0af34f-fa40-554b-af73-418ad7d50957 |  | note | Acceptance Criteria - Check weather forecast for rain and wind. Works to not beginning if rain is imminent. Works must not start or cease if wind increase over 15 knots
label | e886f363-b2b7-5d65-a0d3-74b740221ef7 |  | note | Reference Documents - Cl3.7
label | 428c7c0b-bcd8-5ef4-b124-ab659e25d26b |  | note | Inspection/Test Method - Verify
label | edea983b-1021-5459-87af-07fad8ad33ea |  | note | Record of conformity - This signed ITP
label | 40298fdd-eece-5a4d-bf52-24aa79d1721d |  | note | IP
label | 840a110e-9bae-54b5-b7b6-7aa8312005d7 |  | note | Responsibility - Project/Site Engineer
date | 2097ba3d-a9c1-5756-a462-013f70a97ea0 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.3 - Spreading of Lime
label | 78e2769e-331f-565f-ac61-b2172501c3a3 |  | note | Frequency - Each Lot
label | ee78259e-b187-553c-a8f8-a39f8b65891d |  | note | Acceptance Criteria - Lime to be spread uniformly over the prepared surface at the Lime spreading rate calculated.
label | 33187a45-846e-52b6-ab6a-5d438b34c101 |  | note | Reference Documents - Cl3.7
label | ca0f43a1-fc2a-5041-9c08-4906d7047af9 |  | note | Inspection/Test Method - Verify
label | d8bc3daf-9fff-5d39-a2f3-3270cfd3f663 |  | note | Record of conformity - This signed ITP
label | 0976379c-eeb2-55c7-91f8-d74f1929eb49 |  | note | IP
label | 4ee44097-ec15-5b67-b8c6-59ed3780f975 |  | note | Responsibility - Project/Site Engineer
date | 420033b4-467d-50e9-a35e-c3d53789f22b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.4 - Spreading of Lime
label | a75badb0-eb77-5a41-8fd7-57d54ba88ce7 |  | note | Frequency - Once Per Hour
label | b74e3e83-f0f3-54a3-affc-686b1d414fcc |  | note | Acceptance Criteria - Lime spread to be checked every hour and shall be with +/- 5% of the specified amount. An area to be checked is required to be 1x1m2.
label | 3390d410-7f7c-5242-8e9f-d6a14c96a9d9 |  | note | Reference Documents - Cl3.7
label | 94907931-d99d-5f4a-9ed1-72a7bd40a53c |  | note | Inspection/Test Method - Verify
label | 1d6bc099-7de6-521e-a53b-c1dc33af1031 |  | note | Record of conformity - TP
label | 6bce729d-7697-5a49-bed7-d09bba0b0fdb |  | note | IP
label | ad236bae-a6ed-5aed-89d2-cbd80ce624e7 |  | note | Responsibility - Project/Site Engineer
date | 704bcd53-dd10-5f8e-abf6-1d85f6e1e264 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.5 - Mixing
label | 342dc891-c403-5f90-b824-bbf8f7a88c87 |  | note | Frequency - Each Lot
label | 390ce6f2-6e8b-5b9c-af40-e7318e0b4f9e |  | note | Acceptance Criteria - All lime to be mixed to the specified depth within 8 hours of spreading. Mixing passes to overlap to ensure subgrade is mixed twice as a minimum.
label | cc5e43e5-aeea-5ebe-89e0-150f5c893321 |  | note | Reference Documents - Cl3.8
label | 1dffa4ef-977c-5200-9704-d4057650e30f |  | note | Inspection/Test Method - Verify
label | 6bfe17ce-16bc-52bb-a1c0-3e907940d531 |  | note | Record of conformity - This signed ITP
label | e0aabdf2-0f0c-51bd-855e-f54daab64e09 |  | note | IP
label | d0540783-c182-5522-b955-56420d6d484a |  | note | Responsibility - Project/Site Engineer
date | 994e21c9-ca3a-5509-a5a3-0cf0d1059d7e |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.6 - Mixing
label | c562766c-54bc-512f-8f72-d70eadefc4f0 |  | note | Frequency - Once Per Hour
label | c1f928cf-02bb-562e-8be8-3b04caaf0ac3 |  | note | Acceptance Criteria - Approximately every hour, mixing plant will record the depth of application to check compliance with the specification (300mm or 400mm).
label | ce08e854-5a2e-5f75-a0ce-ee62a04c30b8 |  | note | Reference Documents - Cl3.8
label | fddc46ec-5c36-548c-9341-af9ba77c9e32 |  | note | Inspection/Test Method - Verify
label | 3718af78-1a8b-57a9-a532-0dea2ad1f0fc |  | note | Record of conformity - TP
label | 6e7b5fd0-bb87-52f0-8aa3-de05d6a89a6a |  | note | IP
label | 604b6d97-13ba-5a6c-a11c-15e0afee918b |  | note | Responsibility - Project/Site Engineer
date | 9911afd3-d0e0-521b-bea9-867e1aa90967 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.7 - Joints
label | d260d097-aab9-5437-a478-470276285dfb |  | note | Frequency - Each Lot
label | 87275da8-6c25-52f9-a6f7-98b66d093217 |  | note | Acceptance Criteria - Construction Joints when required, will be placed to ensure no single plane of weakness. Construction joints of adjacent lots will:
label | 56b137d2-41f8-5edb-9b14-5cb2bf5b70bf |  | note | ○ Longitudinal Joints – Will be avoided by overlapping adjacent lime stabilisation mixing runs.
label | 3ff60da7-8cef-5b45-aac3-88eb76284fb9 |  | note | ○ Traverse Joints – Will be staggered to avoid forming a single joint.
label | 09fc5b76-e89a-55e9-91a1-304745c6f012 |  | note | Reference Documents - Cl3.13
label | 4f5cf043-d1a6-5402-9422-ec3286759824 |  | note | Inspection/Test Method - Verify
label | 0f8796f9-0f68-5d9d-911c-4dd0df554f39 |  | note | Record of conformity - This signed ITP
label | 91fc4eb7-572e-5e1d-b5bb-73b2d8d06491 |  | note | IP
label | 59a162e2-9def-5e63-800f-f58f1cd41a8f |  | note | Responsibility - Project/Site Engineer Foreman
date | 71be9b34-2f3f-51e8-96e1-c87052da0403 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.8 - Compaction
label | 98edc022-ce50-597f-a49e-fd5f9cd8f64f |  | note | Frequency - Each Lot
label | a802c0d7-976b-507a-82ab-78328487457b |  | note | Acceptance Criteria - After satisfactory mixing, compaction shall commence within two hours and be finished within eight hours of mixing completion. Additional moisture may be added if required.
label | 4c8d3682-ad1a-5729-9c6f-2e04e34da9f8 |  | note | Reference Documents - Cl3.11
label | e5693786-39f2-5aae-81e9-a3617205b081 |  | note | Inspection/Test Method - Verify
label | e15bc505-3a49-52dd-9b7c-9ed1054f2c30 |  | note | Record of conformity - This signed ITP
label | 43fc5fae-6188-59b1-82a8-c5d0d4f56eeb |  | note | IP
label | a7256504-2d31-5e6a-bb32-f6b1487cad93 |  | note | Responsibility - Project/Site Engineer
date | 813850de-8025-5607-84f0-7cdf4c1621ec |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.9 - Trimming
label | b2c11689-93f9-520e-b751-4b92349a7772 |  | note | Frequency - Each Lot
label | 70ccdfdc-aa8b-545f-9f9d-36c5789170e9 |  | note | Acceptance Criteria - Surface to be trimmed to +0mm, -25mm
label | a4867d15-b3ab-57ac-b389-76f5f082326a |  | note | Reference Documents - Cl3.11
label | 2c8e1993-e02f-5023-82c6-ff4971f7b99f |  | note | Inspection/Test Method - Verify
label | 21f15f9a-1bae-52d8-9b6c-b7f6cf06e552 |  | note | Record of conformity - This signed ITP
label | e4704b06-5569-5e33-a586-8cc50ab7f1c9 |  | note | IP
label | 1357d1c2-2430-5df4-85a6-b9c7d2652ddd |  | note | Responsibility - Project/Site Engineer
date | e44933a5-f7c7-5f2c-a310-b86a294811e4 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.10 - Protection
label | 3a917592-6749-5df9-b2e0-1e85c23e2f6f |  | note | Frequency - Each Lot
label | e2b99457-d65b-54d8-8fef-e7c361627566 |  | note | Acceptance Criteria - As soon as lime stabilisation activities start, no construction plant to travel across works zone (other than those involved in the operation for 48 hours minimum.
label | 2dd506ec-22c9-5e37-a1bf-fc4acf1eedc7 |  | note | Reference Documents - Cl3.15
label | 17f9f7c3-91cc-5b6c-8462-621aa1bfd5a8 |  | note | Inspection/Test Method - Verify
label | a3d5d5de-4b52-5924-9d24-2c0b71b05c48 |  | note | Record of conformity - This signed ITP
label | e7639432-5a5f-5ccc-88ff-b79580bbf1c5 |  | note | IP
label | 7e023d29-6b28-5d62-b994-407b63ef41fd |  | note | Responsibility - Project/Site Engineer
date | eb4df604-5d71-5666-8157-65e62f99e767 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.11 - Curing
label | f5d664e1-3302-5239-b31b-bb3d32877dae |  | note | Frequency - Each Lot
label | 3634ecf6-60c9-5eb9-9428-1f7e010dcc54 |  | note | Acceptance Criteria - Curing shall commence as soon as practical. The curing period is 48 hours or until the succeeding layer is placed.
label | 61592bc7-ee26-52a2-a062-6e051423a52d |  | note | Reference Documents - Cl3.15
label | 7180bd48-55d1-52eb-bc1a-3e79860497ec |  | note | Inspection/Test Method - Verify
label | 17d9e9eb-a333-5f92-a309-9d214f33daa2 |  | note | Record of conformity - This signed ITP
label | 2ec1438f-9013-52d1-822b-308c154d145f |  | note | IP
label | 02640a26-aa0f-5092-8fb2-64afa27ad078 |  | note | Responsibility - Project/Site Engineer
date | 77d43f30-4dbf-58d2-86f2-a8ea53be2978 |  | date | Date Completed:
checkpoint-group |  |  | section | 4.0 - Acceptance – Lime Stabilisation
checkpoint-status |  |  | checkpoint | 4.1 - Proof Roll
label | 2f9353b6-e54c-554e-8c1b-d099c954ad0a |  | note | Frequency - Each Lot
label | 36368a93-d957-5fdf-89b4-f9e013b6bb09 |  | note | Acceptance Criteria - Following completion of the curing period, detailed trim and survey conformance, the Principle’s Representative will be invited to a proof roll (24 hours notice). Proof roll will be accepted if no rutting greater than 25mm is observed. Proof roll will involve using a heavy vibrating roller (in static mode)
label | c68d0f35-ea92-50b2-a8f9-67e617c28a42 |  | note | Reference Documents - 3.12
label | 01c1e634-186b-5a82-a4b8-b45d73df62b1 |  | note | Inspection/Test Method - Verify
label | 87be2623-dfbd-595f-891c-8be21e24dbf4 |  | note | Record of conformity - This signed ITP
label | 18dcd2dc-0dc5-50c3-9665-7cd0923ebd3a |  | note | HP, WP, HP
label | 6fc411fb-3ae7-5906-8a89-562298867e11 |  | note | Responsibility - Project/Site Engineer Principle’s Representative
date | d1fa4d52-e8b4-590a-968e-cf95e9142cce |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.2 - Surface Smoothness
label | 837b0e22-2d8b-5699-84c5-515f36d75e55 |  | note | Frequency - Each Lot every 10m
label | de08aee8-f886-5796-a501-5eabd7247879 |  | note | Acceptance Criteria - Long straight edge surface not to deviate by more than 12mm over a 3m long straight edge, following subgrade treatment
label | 55319a9f-9797-5e69-859e-50134128725b |  | note | Reference Documents - 3.16
label | 16184e99-8bbd-5666-ad3a-1593c7749c5b |  | note | Inspection/Test Method - Verify
label | b9fa94eb-211f-52da-8503-97c347b9b63e |  | note | Record of conformity - This signed ITP Results Attached
label | badb7c5b-c62c-5b51-9f76-70912fae58ac |  | note | TP
label | 0789e41b-dcac-5f88-996d-89e182908747 |  | note | Responsibility - Project/Site Engineer
date | b79112a3-6ced-57fa-b89d-fddd9e664d09 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.3 - Strength Testing (CBR)
label | d85a453c-5089-51ed-954f-8e86db541710 |  | note | Frequency - Each Lot
label | f5a104ee-3f30-5158-8fbb-ace6a4d16cbf |  | note | Acceptance Criteria - To exceed 20% CBR after 7 days. Test every 1500m2 for first 3 consecutive conforming Lots; then every 3,000m2 or part there of. Maximum 3 tests per lot.
label | dcfc4b1e-0919-542f-b37d-11d9d298b83c |  | note | Reference Documents - 3.16
label | 9aafccc7-b587-5e41-9e41-508f824c8f8e |  | note | Inspection/Test Method - Verify
label | 7d77674a-c72a-53e8-8a83-e1b6063b07ef |  | note | Record of conformity - This signed ITP Results Attached
label | da13dbcc-c9e4-57d0-8957-1788082fb56b |  | note | TP
label | d639452d-ccd1-5669-8883-d3a580538630 |  | note | Responsibility - Project/Site Engineer
date | a45fc774-3ef6-57c2-b1f7-690c9bddcf71 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.4 - Field Dry Density
label | 5b50c56a-2fb2-56de-a1a9-589bcd9b2868 |  | note | Frequency - Each Lot
label | 13f56cac-10c3-5539-9859-e527e2da735f |  | note | Acceptance Criteria - Maximum Dry Density used is lime stabilised subgrade 90%. 500m2 for first 3 consecutive conforming Lots; then every 1000m2 or part there of. Maximum 4 test per Lot
label | f62b5305-d129-5dbc-bf9c-8ff4bafc6a11 |  | note | Reference Documents - 3.16
label | 92188a49-9e45-5703-b6e1-72394050c8e9 |  | note | Inspection/Test Method - Verify
label | 458eb129-b3d5-54be-9309-1a51f9e67403 |  | note | Record of conformity - This signed ITP Results Attached
label | f5b3e371-e308-5ab0-b6ae-b1becb453e47 |  | note | TP
label | a6ee8b2b-41ec-5e59-a54f-86f1f31451df |  | note | Responsibility - Project/Site Engineer
date | 7fb847a3-e1dd-5c9b-871a-e52592ada559 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.5 - Surface Level
label | f264f4f4-7d4f-54d0-8b2f-52a809c0980a |  | note | Frequency - Each Lot
label | a9239d3b-556d-58a1-9f60-bb446b8a5ee5 |  | note | Acceptance Criteria - Stabilised and compacted subgrade surface layer to comply within -25mm to +0mm from specified levels.
label | dd91c709-302e-59a4-9b57-787abfb44091 |  | note | Reference Documents - 3.16
label | 5c788dd4-2a4d-591d-bc3d-cf3bd5319e8d |  | note | Inspection/Test Method - Verify Report
label | 03035fda-fbdf-5aca-9ea7-6a19bf79a240 |  | note | Record of conformity - This signed ITP Results Attached
label | a3606e88-472f-5d9d-8a9b-d3aa27803cec |  | note | SCP
label | 22446a72-33e9-53a1-a9d8-daa4db972c79 |  | note | Responsibility - Project/Site Engineer
date | 8536f0c4-4dcf-5494-a569-c3e75eed94ca |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | 77834e6f-6574-54f0-b03c-6bcabe6cb4dc |  | note | On behalf of Fulton Hogan, it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
text | e9b4af31-26aa-5a17-b1c7-baaf6919ffd1 |  | textbox | Print Name:
text | a304cf96-b429-5255-a2df-662eb05d02a4 |  | textbox | Position:
date | 7de9a745-74e3-5528-8e04-9e99c94961b2 |  | date | Work Completed On:
date | fb9de0d3-dd9f-5aff-9a96-ab452a1610b2 |  | date | Date:
checklist-sectioned |  |  | checklist | ITP006 - Subsoil Drainage | itp |  |  |  | Yes | FH-ZU2-QU-ITP006 - Subsoil Drainage - Rev 0 | 620efb2d-bb1e-4b7c-bce3-9de8780204a5
checkpoint-group |  |  | section | 1.0 - Preliminary Activities
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | b203efa7-9a22-5926-bd73-8de13b415a22 |  | note | Frequency - Prior to commencing activity
label | bbc090e4-5691-53ff-8630-4771d69f82b0 |  | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
label | 0bd51d55-9b65-50b8-b133-094970bffa42 |  | note | ○ using the correct and complete set of drawings.
label | 2796cb7c-8938-5ce3-864e-aed637875e7b |  | note | ○ all drawings are the latest revision.
label | 46916086-2b53-5d88-ad5d-4ec4e0b35143 |  | note | Reference Documents - IFC Drawings
label | 2331c893-c1ca-5edd-a5bc-32cd368b8062 |  | note | Inspection/Test Method - Document Review
label | 0c7059cd-7c8d-5927-b2a6-53aeda36e7f6 |  | note | Record of conformity - This ITP Signed
label | 2a4ea12c-0fc8-5bf2-8321-e0e60a39e82b |  | note | HP*
label | 62a43976-e7ef-5bb6-b3c4-d0f251e5ed9b |  | note | Responsibility - Project/Site Engineer
date | babe2d24-e642-593a-b977-cfdd507e634e |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 941dc993-a111-5574-9200-06146195396a |  | note | Frequency - Prior to commencing activity
label | 40f86d52-0a66-57a8-890a-0408cd16eb95 |  | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: CEMP, TMP, SWMS & WP.
label | 2e4953e3-5ca0-5ad7-8b53-475ec0eb0254 |  | note | Reference Documents - CEMP, TMP, SWMS & WP
label | c9883755-8c08-5007-a533-cc805d703693 |  | note | Inspection/Test Method - Verify
label | 9f40c57f-8d81-5fbc-97cc-5cc438a222b3 |  | note | Record of conformity - Site and Office Inspection
label | d456838d-d521-5f5e-9814-6ebab7e168ba |  | note | HP*
label | 13a3a736-2da8-5338-9439-c66cf07d0f9e |  | note | Responsibility - Project/Site Engineer/Supervisor
date | 8d3617a0-ff7a-589c-97a6-7746d94759b0 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Excavation Permit
label | 4621e442-d233-5395-83bc-ce811358abeb |  | note | Frequency - Prior to commencing activity
label | c10cec44-4414-5d8f-adad-794206ee4cef |  | note | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
label | 6a9c7f96-9941-5267-b05e-e17eaf8ad66d |  | note | Reference Documents - Approved Permits
label | b7759b67-f929-5676-a29c-9f2d90988101 |  | note | Inspection/Test Method - Verify
label | f39f1bfc-9cd3-5716-a541-b40dbc723cf1 |  | note | Record of conformity - Proof of permit & ITP signed
label | 7a6a615a-ed94-53da-aa6d-817b63f120c6 |  | note | HP*
label | 178bd2a1-3ba0-50c6-afce-5996683f0817 |  | note | Responsibility - Project/Site Engineer
date | 99112c83-d7a5-59d9-aef3-fc94599fd70f |  | date | Date Completed:
checkpoint-group |  |  | section | 2.0 - Subsoil Materials
checkpoint-status |  |  | checkpoint | 2.1 - Subsoil Drainage Pipes
label | 5b646d98-aa7a-5836-ae73-381d8ebf1b62 |  | note | Frequency - Prior to commencing work
label | bcaec0c9-9031-5295-9942-dbf72084364d |  | note | Acceptance Criteria - Pavement Subsoils:
label | b7359a8d-0550-508d-8b02-ed66b1b36fc1 |  | note | ○ 100mm Dia slotted with filter fabric (sock) CL1000 SN20.
label | d5a93f8c-7cf5-5dd9-ac9b-3357d03174ae |  | note | Subsoil Collector Pipes:
label | b092e40d-b547-5be0-99d7-08a0a40cc028 |  | note | ○ AGL Carrier Pipe: 80mm Dia PN12 uPVC Non-Perforated Pipe.
label | c71454fc-b17e-5349-9e45-7aa67f16c22d |  | note | ○ SSD Carrier Pipe: 150mm Dia PN12 uPVC Non-Perforated Pipe.
label | 0fe68566-15e7-5f87-ac33-ea7c86b3cb4d |  | note | Reference Documents - Cl.16.5.3, Cl.16.5.4 & IFC Drawings
label | 7db0c490-ad5b-577f-af6c-8253694d2b26 |  | note | Inspection/Test Method - Verify
label | 7b19fdb1-45b4-5c3e-8438-1738fb265c3e |  | note | Record of conformity - Order Inspection Checklist
label | 5a52b1f3-475b-5840-a3fe-5ad3d836fb4e |  | note | IP
label | 6a41afaf-d4b0-56ae-9cde-29297e7b2dbc |  | note | Responsibility - Project/Site Engineer
date | 7e10c348-b168-547c-b344-2948e99a3363 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Bedding and Backfill
label | 0a65b798-f2a0-50d4-8a54-048370d7f9e6 |  | note | Frequency - Prior to commencing work
label | 65490841-89f8-52b9-a6c8-0e6ade8c75c5 |  | note | Acceptance Criteria - Subsoil Drain Pipes Under Pavement
label | 8d673ba2-f482-50d9-8e8d-01e35ea81db5 |  | note | ○ 100% recycled crushed glass (sand) meeting VicRoads (Section 702) Grade A2 or A3 material or approved equivalent.
label | ea074592-f6e0-5276-8ecf-09e2aa464e5e |  | note | Subsoil Collector Pipes – Under Pavement
label | 90d57a37-66c0-5a63-9a00-37a0d5ea31cb |  | note | ○ Approved 15MPa lean mix.
label | 0a750720-2d3c-5829-b0b1-43f7a714381f |  | note | Subsoil Collector Pipes In Grass
label | f6feccc3-2a5b-5c58-8c91-7bc66bc2ac4e |  | note | ○ 100% recycled crushed glass (sand) meeting VicRoads (Section 702) Grade A2 or A3 material or approved equivalent.
label | a375508d-7a04-5b79-a062-dd33308b9ec0 |  | note | ○ Excavated Soil
label | 0be3036b-e5c3-5cd3-94d1-82069d58357c |  | note | Reference Documents - IFC Drawings & VicRoads Section 702
label | 192a4443-013d-5350-bee7-1ced123affd2 |  | note | Inspection/Test Method - Verify
label | 04805040-cf54-5fbd-ab74-74d27943c596 |  | note | Record of conformity - Visual Inspection & Delivery Docket
label | 12a91005-a1ce-5115-9639-3ff57f494a39 |  | note | IP
label | 75b3b35e-138d-55f3-86be-0386538781c7 |  | note | Responsibility - Project/Site Engineer
date | 977a00fc-306d-59b1-9a0a-2ac71d410998 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Geotextile Fabric
label | 1f00f2b1-23ff-5d29-ad30-843835eca1db |  | note | Frequency - Prior to commencing work
label | 3654a3b6-f2a4-5ef2-a001-4d0b5aca6d9b |  | note | Acceptance Criteria - Non-woven type complying with the requirements of VicRoads for first stage filter.
label | e7938520-5e9f-54bc-91a5-5d8faeca7148 |  | note | Reference Documents - Cl.16.5.8 & VicRoads Section 702
label | cbdc78d0-0722-54da-8205-b90cc9af3622 |  | note | Inspection/Test Method - Verify
label | 447ec906-7210-5a3a-a5f3-6f908f3d604c |  | note | Record of conformity - Visual Inspection & Delivery Docket
label | 0c6a5fea-3afd-512c-8368-a5417aef9492 |  | note | IP
label | f8fe6ab3-b47f-56cd-a396-18119f9ec08b |  | note | Responsibility - Project/Site Engineer
date | d3362b11-23dc-5195-9144-10052d55416a |  | date | Date Completed:
checkpoint-group |  |  | section | 3.0 - Excavation and Installation
checkpoint-status |  |  | checkpoint | 3.1 - Trench Excavation
label | 93bdb9fc-556e-5244-9d83-f6783c956641 |  | note | Frequency - Each Lot
label | 8c640fb9-21ba-520b-a95f-471abad2330d |  | note | Acceptance Criteria - Trenches shall be excavated to the minimum depths, widths and batter slopes as shown on the drawings.
label | 56f6e280-b7f1-5fd9-a677-7c644276b746 |  | note | Minimum Trench Widths: Subsoil Drain Pipes
label | 43759727-e5da-57a1-af50-b01cf3d394bb |  | note | ○ 300mm total width for the subsoil drain pipe (DN100).
label | 43e28dc1-5a6a-5792-b73e-e85f01e8c46f |  | note | Subsoil Collector Pipes
label | af2bffd1-df6b-5b82-83e6-861c7441d94c |  | note | ○ Horizontal clearance from the outside of the pipe to the wall of the trench to be minimum of 150mm for all collector pipes (DN80 & DN150 both under pavement and in grassed areas).
label | 02934fcd-64ef-573a-95a1-a5782919ad2c |  | note | – Excavated material disposed per approved CEMP.
label | c83e1bc1-a23f-50ea-a791-ee6fee052881 |  | note | – Completed excavation works shall constitute a Hold Point.
label | d35269e0-0384-5008-8156-7ca76583fce3 |  | note | Reference Documents - Cl.16.8.1 & IFC Drawings
label | 30c8a41b-bf2d-5399-81fb-af8d6620b1df |  | note | Inspection/Test Method - Verify
label | 84ef1c63-e86c-5e80-8a4a-3617827e4c3e |  | note | Record of conformity - This ITP Signed
label | 20ae350c-40fc-5b50-9d8f-19f392727a14 |  | note | HP
label | 2579ceae-223e-5bc5-813e-452564241e37 |  | note | Responsibility - Project/Site Engineer, Beca
date | bc954475-f8de-599e-8749-faa5b05ffb8a |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - Geotextile Placement
label | ef9802b5-3e5f-5715-a88b-5cb5dc0ff26f |  | note | Frequency - Each Lot
label | deb9c76e-c3ed-54e6-b14d-4668eeb6639b |  | note | Acceptance Criteria - Geotextiles in trench drains shall be placed to conform loosely to the shape of the trenches. The approved geotextile must fully envelope the drainage material in the trench with a minimum 150mm lap.
label | 21d2eb47-3873-541e-b2c9-79d7673f0a3e |  | note | ○ Site trial to be undertaken to evaluate the proposed construction process and compaction method, Hold Point.
label | dab879b0-1f17-5774-8e0f-6117afa132ea |  | note | Reference Documents - Cl.16.9.4.2, Cl.16.9.4.5 & IFC Drawings
label | 82e70949-388e-58e4-a299-eb94ab7b8933 |  | note | Inspection/Test Method - Visual Inspection
label | 71db4eed-f250-532a-bb94-bd3a828c4158 |  | note | Record of conformity - This ITP Signed
label | e5f82998-cc61-5ce3-93b0-24d850879a9b |  | note | HP
label | 705d94a8-4029-58fe-a8b9-780793c31bca |  | note | Responsibility - Project/Site Engineer, Beca
date | 860b8d14-7b9e-506a-a000-6954dab63e0c |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3 - Bedding
label | edf8c917-c28c-5c70-b565-3e2d432fd2dd |  | note | Frequency - Each Lot
label | 62421231-2c6d-5eca-9810-3473afb30050 |  | note | Acceptance Criteria - Bedding for Subsoil Drain Pipes Under Pavement and Subsoil Collector Pipes in Grass
label | bc12892a-da80-540e-8469-0dfa293e3156 |  | note | ○ Bedding of granular filter material:
label | 9ef781b3-6406-5d7a-b1e3-c4c4d0ffd4bb |  | note | ○ 100mm for subsoil drain pipes.
label | 8739fd5d-84f9-595e-bd56-eb792fcc829d |  | note | ○ 75mm for subsoil collector pipes
label | 4a1d56be-0e72-559e-8a13-4adfe3968569 |  | note | ○ Filter material shall be placed and compacted with minimum disturbance to pipes and in layers no greater than 200mm uncompacted.
label | f7bbff52-7368-5ad4-ac3a-16b9fd15f9eb |  | note | Reference Documents - Cl.16.9.2 & IFC Drawings
label | a1ff3c14-5b58-56dd-9b30-9a770d99dedc |  | note | Inspection/Test Method - Visual Inspection
label | edbf6be4-9c0b-5c1e-8e98-001ed939039e |  | note | Record of conformity - This ITP Signed
label | 11b14a64-c51f-50ef-a675-66ea99711356 |  | note | IP
label | 60facb07-3d1a-5dc6-9896-76c918e4279c |  | note | Responsibility - Project/Site Engineer
date | b6e19c2b-861b-5e35-aa57-f3dfa61fcc93 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.4 - Laying and Jointing of Pipes
label | acc63919-1859-5956-accd-4338e7a69607 |  | note | Frequency - Each Lot
label | 982dab69-d0d8-5ee3-9b07-5a9200f9ad52 |  | note | Acceptance Criteria - Pipes laid at the depths and lines indicated on the drawings. Where grades are not specified, the bottom of the trenches shall be trimmed to provide no less than 0.5% longitudinal fall.
label | 43ca6168-124c-5106-916f-7f05a8f1181f |  | note | Reference Documents - Cl.16.9.2 & VicRoads Section 702.03, 702.09
label | f30b24eb-069d-52f8-9c80-00edf093fa0c |  | note | Inspection/Test Method - Visual Inspection
label | 8d17080c-d48d-5c25-8294-368a7b2b11f5 |  | note | Record of conformity - This ITP Signed
label | 12ccdfeb-6447-5b5f-9c90-89d12c8e5783 |  | note | IP
label | 5af6caf2-1f5c-55ba-9bda-dd7a686406ea |  | note | Responsibility - Project/Site Engineer
date | 5fed5454-4550-5138-823f-625274cf1e2e |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.5 - Backfill
label | 82e0d72f-b673-55f3-a373-a8ea5a346c9c |  | note | Frequency - Each Lot
label | 782fda5e-a891-560b-a090-0d895cc5246e |  | note | Acceptance Criteria - Backfill for Subsoil Drain Pipe (⌀100mm pipe)
label | 16f6de95-850c-54e9-9cda-8db3e3234d8a |  | note | ○ Granular filter material backfill is to be placed to the underside of the CTB layer.
label | c65b7a80-90b6-58d2-b607-783ba0e61707 |  | note | Backfill for Subsoil Collector pipe ⌀150mm Under Pavement
label | db90f132-f0d7-53d9-8eae-ea8a81b12ea0 |  | note | ○ 15 MPa lean mix backfill is to be placed to a minimum of 150mm above the pipe crown to underside of pavement formation.
label | 7815479a-a64b-514a-a8ac-c710635bff3e |  | note | ○ Backfill to be completed in two stages to avoid pipe floatation.
label | 52e3cb2e-51b0-5ed2-a80d-117db9ebcc0a |  | note | Backfill for Subsoil Collector pipe ⌀150mm In Grassed Areas
label | e01eaf9d-2a64-523d-b88e-eaba57882e10 |  | note | ○ Granular filter material is to be placed to a minimum of 150mm above the pipe crown.
label | 04f9a45d-67aa-5f3a-9cf6-d80049db9353 |  | note | ○ Excavated soil recompacted in layers not exceeding 200mm loose thickness to underside of topsoil.
label | 7a5f02a3-76eb-5822-a496-80137de680ef |  | note | Backfill for Subsoil Collector pipe ⌀80mm
label | 3d708b91-b862-571a-bd20-879a1ca722a2 |  | note | ○ 15MPa lean mix backfill to be placed to be placed to top of 150mm FCR subbase layer
label | d63fb179-d759-5832-859e-dff393f317ce |  | note | ○ Backfill to be completed in two stages to avoid pipe floatation.
label | e2f44423-fabd-5fc4-a2bd-d2019986ed13 |  | note | Reference Documents - Cl.16.9.2, IFC Drawings & Tender Clarification #38
label | 2c3a2b19-1ecf-55da-b4cc-23359d952d5d |  | note | Inspection/Test Method - Visual Inspection
label | c359ccd0-b0bf-56ed-9d34-2103b9b83abc |  | note | Record of conformity - This ITP Signed
label | 89d9dfb0-fe82-54a4-b618-7d17b9f3ecf1 |  | note | Responsibility - Project/Site Engineer
date | 5a6ddc48-3b75-5b34-a0cc-51ff2e6bbcdb |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.6 - Subsoil Drain Outlet
label | 2729af9d-76e7-5b4f-b482-22072c7b5378 |  | note | Frequency - Each Lot
label | 93d4d9f0-a715-5621-902f-6b616213da84 |  | note | Acceptance Criteria - Subsoil outlet point to be located at a drainage pit, pipe end wall or outlet in a fill batter or drain. All subsoil drain outlets shall be fitted with Vermin Guards.
label | 43351c17-7eda-5104-ba99-610b06d2a88b |  | note | Reference Documents - IFC Drawings
label | f54cbdc1-b074-5ceb-b237-b304e63b3eca |  | note | Inspection/Test Method - Verify
label | 118f5f81-1efc-52a1-88c9-a445cb2c84c2 |  | note | Record of conformity - This ITP Signed
label | dc0e6d00-83df-50ea-81de-bb9fbdfead91 |  | note | IP
label | 02300ae5-d391-51c9-a516-b20c5ddd137f |  | note | Responsibility - Project/Site Engineer
date | cc3b74dc-e10e-501a-a4f7-2f5006fa8096 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.7 - Flushout Risers
label | 4ce793d0-4b56-55ae-bbda-0be872c461e9 |  | note | Frequency - As applicable
label | 160fda7a-f329-55cf-b8ba-fdf84ab370a6 |  | note | Acceptance Criteria - Cleanouts shall be located at the heads of all subsoil drains and as specified on the Drawings.
label | 59bd5fb0-e432-5242-b273-7bf5b9e311ed |  | note | Reference Documents - Cl.16.9.2 & IFC Drawings
label | 7b40b719-15b4-5402-93d8-59527c560432 |  | note | Inspection/Test Method - Visual Inspection
label | f3ef272f-cdec-523a-903c-f3f96bd94df1 |  | note | Record of conformity - This ITP Signed
label | 4717fb7b-5e44-5540-b72d-1c7a289ab715 |  | note | IP
label | c6899f67-80fc-5df1-80cf-fe23901deb0d |  | note | Responsibility - Project/Site Engineer
date | 47d5459c-6674-578c-9823-3add99fab108 |  | date | Date Completed:
checkpoint-group |  |  | section | 4.0 - Post Construction
checkpoint-status |  |  | checkpoint | 4.1 - Flushing Test
label | ac2cde80-3d01-529a-812e-aef469bf814a |  | note | Frequency - Each Lot
label | 33817df8-516a-506f-bf30-2f709891d88f |  | note | Acceptance Criteria - Flushing test to be carried out for subsoil pipes to remove material that has entered the pipes during construction and to ensure that the drainage line is free from obstruction. This constitutes a Witness Point.
label | 9b875275-a4ca-5915-bdf5-2499e12fbd6d |  | note | Reference Documents - Tender Clarificati on #33
label | eee59dc7-f9c7-5a81-8506-01615d50d95b |  | note | Inspection/Test Method - Visual Inspection
label | 02293552-747a-5fd4-866a-94f45d6e5a3e |  | note | Record of conformity - This ITP Signed
label | 62c6cda1-4101-52c8-9adf-97edc1fddbc1 |  | note | IP
label | 67f67238-bbbc-5e97-b0ec-911c93b51479 |  | note | Responsibility - Project/Site Engineer
date | c6604951-a6da-5fa5-a47e-d47d5f6087bd |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.2 - Records
label | 265d3813-d435-55c9-8a25-0b3901c43330 |  | note | Frequency - Each Lot
label | a5ebcd79-d827-530b-81ad-26bce792df85 |  | note | Acceptance Criteria - Levels and alignment recorded in as built documentation.
label | 5a5215f2-64c1-573e-ae61-0cbce602f745 |  | note | Reference Documents - As built Data
label | 4c686766-1525-5f55-bbeb-013432f0beb7 |  | note | Inspection/Test Method - Verify
label | 0d197c67-89f3-5a1e-b1ae-c8ebc5c7e02f |  | note | Record of conformity - Aconex Correspondence/Asbuilts
label | 287c6857-e310-5e63-8b19-69f7316bccd1 |  | note | SCP
label | 5b6a66e7-a082-5f5d-b2a2-fea9a80aa612 |  | note | Responsibility - Project/Site Engineer
date | 5ebdc4ef-343c-5375-8a19-e6b25236d540 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | 61331d75-b3c7-5352-8079-414b603e3db6 |  | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
text | 5572ef30-e932-5a08-a991-e4f08674c94b |  | textbox | Print Name:
text | f6667217-4fcf-50bd-b2bf-6f44ca637a42 |  | textbox | Position:
date | f259472e-32a8-5470-b3b9-9487c05a4eb7 |  | date | Work Completed On:
date | 933ef43f-f06a-5888-ba35-78c4fb61c965 |  | date | Date:
checklist-sectioned |  |  | checklist | ITP001 - Demolition of Existing Pavements | itp |  |  |  | Yes | FH-ZU2-QU-ITP001 - Demolition of Existing Pavements - Rev 0 | 6c81ad99-728e-449a-9e5f-10150372d498
checkpoint-group |  |  | section | 1.0 - Preliminary Activities
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | de6ba418-2f03-5955-aff5-5e2c470d39b5 |  | note | Frequency - Prior to works
label | bb451165-5268-54e3-b4b3-8cbe6e9d37fa |  | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
label | 6ed2bb77-45d4-5333-a0a1-cce4e1527cc8 |  | note | ○ Using the correct and complete set of drawings.
label | cff6e110-a38b-51b6-a6e5-0e28d19fe499 |  | note | ○ All drawings are the latest revision
label | 33fc753a-477a-5f83-a6b1-be5cbddefd25 |  | note | Reference Documents - Aconex
label | 869252e6-5f03-5a03-a27c-06d6aa13de5b |  | note | Inspection/Test Method - Visual inspection
label | e10801c6-67d0-59d2-a960-52a5b2a6237d |  | note | Record of conformity - This ITP signed
label | 98e00363-1acd-579f-aa9e-b465cfc1d60d |  | note | IP
label | 2e60b1e9-7e3d-5aca-850f-c29ad54093ee |  | note | Responsibility - Project/Site Engineer
date | a181c36b-ae14-5c86-a20a-ba915d3c521c |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Demolition Work Plan
label | bb0d47e1-b70f-5be4-86bc-6d0d37693a4d |  | note | Frequency - 2-weeks prior to start of works
label | e1c9a3bf-226c-5123-9338-2edf778f750e |  | note | Acceptance Criteria - Prepared and submit Demolition Work Plan in accordance with AS 2601 to Contract Administrator two weeks prior to start of works.
label | c758a3bb-d8ed-5e95-a947-289dfedf1fac |  | note | Reference Documents - Spec cl. 8.4 AS2601 WMS-001
label | 4ca45db9-8b0c-593f-854a-70f9c91cca6c |  | note | Inspection/Test Method - Verify
label | c8cd80e1-5dc0-5e39-a4bd-8395ab627af1 |  | note | Record of conformity - This ITP signed
label | e2077523-4d37-50e2-a1f7-236a89c4a6fb |  | note | HP
label | 7d84c665-a967-530f-8433-c484bfb0d278 |  | note | Responsibility - Project/Site Engineer, Principal’s Representative
date | 5db4d83c-29fd-5cdf-960c-ed9c12482e50 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.3 - Dilapidation Report
label | 7bd5b0c6-ba17-5187-adc3-e6a326a32eb2 |  | note | Frequency - Prior to works
label | 35695348-166d-5426-94a1-37f22be6a12e |  | note | Acceptance Criteria - A dilapidation report is to be completed and submitted prior to works on site. Dilapidation report to include photos and recordings of the condition of the pavement prior to demolition works.
label | 218d6988-09da-5982-a2e4-909d172da817 |  | note | Reference Documents - Dilapidation Report
label | 0b41a501-7016-5af3-988e-a6311d817726 |  | note | Inspection/Test Method - Visual inspection & Verify
label | 405be92c-0e43-50e6-8944-d5e211f5759f |  | note | Record of conformity - Aconex & This ITP signed
label | 74a7bfa7-7423-5826-abb8-adebfeae7f9a |  | note | HP*
label | 023533ff-1616-5d33-a2b8-30bef7b7486b |  | note | Responsibility - Project/Site Engineer
date | c2e3814f-1ccd-534b-a013-4d4f743f21dd |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.4 - Existing Service Identification & Protection
label | 45f1702d-5b43-575b-9667-75048355810b |  | note | Frequency - Prior to works
label | 4522f48d-9bdf-5866-8d04-f661277673a2 |  | note | Acceptance Criteria - Existing services information gathered from APAM prior to works. Area to be demolished has current BYD plans, service scanned, and existing services has been proved. Services have been identified and protected prior to demolition.
label | 58dd54e3-03e1-5fb7-849e-d8f22fa07fbe |  | note | Reference Documents - Spec cl. 8.5.1 Drawings, BYDA, Survey Maps
label | 97297616-c88e-5eb6-99ed-b539126ae022 |  | note | Inspection/Test Method - Verify
label | e5c985f5-f458-58aa-a10f-f5e7346a67d4 |  | note | Record of conformity - This ITP signed
label | f276c259-8c21-5cca-a78f-49100e7c9402 |  | note | IP
label | 5907faef-fe05-5530-81d6-24ed30a1b715 |  | note | Responsibility - Surveyor, Project/Site Engineer
date | 4f9c2daa-fa7b-5ede-9e45-eefa43fd675d |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.5 - Execution of Demolition works
label | b9f49108-0177-5ea0-a0db-0e2301b5389a |  | note | Frequency - 2-weeks prior to start of works
label | e6729bde-b9d0-5217-9282-8cc785387ff1 |  | note | Acceptance Criteria - If working within the existing vicinity of AGL services, Fulton Hogan to give APAM a two-week written notice to work in the vicinity of existing AGL cables and transformers, to provide notice for APAM to assist in isolating services.
label | 8c4ca2a2-bc2a-51a5-89eb-197856cb2a8e |  | note | Reference Documents - Spec cl. 8.5.1
label | 2705b2d5-423f-5299-9b17-ff18479d6236 |  | note | Inspection/Test Method - Verify
label | f6a5a2d9-aa00-55c5-af5b-02517ffb42e5 |  | note | Record of conformity - This ITP signed
label | 9b05a6b9-21b7-5a6d-94f2-aac152dfdcfe |  | note | IP
label | 6769e4c8-2210-5634-bd56-691fabf8e714 |  | note | Responsibility - Project/Site Engineer
date | 2ec735ad-f8dd-51ad-a7d0-bdab91a4efac |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.6 - Implementation of all measures and controls
label | 0288d473-5da7-580d-bb77-dd34ac13a7f6 |  | note | Frequency - Prior to works
label | 5b133118-4d35-573b-806b-23778d780fd9 |  | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, ECP, TMP, SWMS and WP. Existing areas that are not part of the demolition will be delineated with bollards or similar to ensure that it is not disturbed during demolition.
label | 34224c36-7f04-5aef-8886-f22b446426a1 |  | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
label | f22f7a72-5027-5553-b48d-c50f459710fb |  | note | Inspection/Test Method - Visual Inspection
label | 00819a04-f5a1-5f8f-a38e-4a4f6fa7092b |  | note | Record of conformity - This ITP signed
label | a3cd1da0-3c74-5829-81b8-79d9cb39a0f3 |  | note | IP
label | b88747a5-0950-5069-8d91-33c9885de087 |  | note | Responsibility - Project/Site Engineer
date | 05a68ad6-76b3-58df-93c1-dd9252a94a11 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.7 - Testing of Demolition Materials
label | d7fd890f-720a-5d4d-9d5e-fff65772b3c3 |  | note | Frequency - Prior to works
label | eb55cd7b-dcfa-5434-8639-c55e87603b0a |  | note | Acceptance Criteria - Ensure PFAS testing has been completed. The results of the testing will be used to determine the appropriate disposal or re-use of the demolished materials. Offsite disposal of material has been approved by APAM and comply with regulatory requirements.
label | e07c9c66-19b8-53e8-ae70-ef8968bfec0a |  | note | Reference Documents - Spec cl. 8.5.5
label | 50f7461a-2b7e-5d7d-9c84-ffedd2400d90 |  | note | Inspection/Test Method - Verify
label | 8bdecf34-d91f-5805-b803-d4e50f3f66b2 |  | note | Record of conformity - This ITP signed
label | de5775e5-cd56-550e-8333-79a2f2215f3f |  | note | HP*
label | c9bfbcd4-75a8-59e6-8fe8-974782b93305 |  | note | Responsibility - Project/Site Engineer
date | 9f4b5e74-2c21-5070-a5c6-40e28d21b6bd |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.8 - Excavation Permits
label | be982e0d-451d-5990-b371-14bd6a185547 |  | note | Frequency - Prior to works
label | 31b23bba-6ec6-56fd-a149-0b62d29a0b33 |  | note | Acceptance Criteria - Prior to works, check that excavation permit has been gathered from APAM prior to any demolition works. Internal Fulton Hogan permit has been issues to excavation works and plant operators.
label | b7c27170-a1ca-5d0d-b0b8-cb64a43d841e |  | note | Reference Documents - APAM Excavation permit, FH Permit, Go- Cards
label | 10f5a5af-1690-5b5a-9bda-dee7d4bdb2d8 |  | note | Inspection/Test Method - Verify
label | 1b9c1d85-945d-5cd5-87df-b56aa0eeb97e |  | note | Record of conformity - Excavation Permit
label | 2e86c833-d897-5663-8392-742befa2a4f6 |  | note | HP*
label | 08f2e4dd-49c9-5a1d-b705-b46fe3ed0ad2 |  | note | Responsibility - Project/Site Engineer
date | f80a5894-3af3-507f-a3c4-605e3111fde8 |  | date | Date Completed:
checkpoint-group |  |  | section | 2.0 - Demolition of Existing Pavement Works
checkpoint-status |  |  | checkpoint | 2.1 - Definition of a works area (survey)
label | aae52969-45d2-503e-adc2-d30ba1dd9d2d |  | note | Frequency - Each Lot
label | b4adfc7f-599d-5b8d-8cd3-e661d18ab14f |  | note | Acceptance Criteria - Work area has been cleaned and surveyed (marked on site). Limits of demolition are clearly marked.
label | ef12fdfe-1564-5ea2-b5f6-2d7d56fe5e0c |  | note | Reference Documents - Drawings
label | e867c56c-9d76-5a56-bb23-b85897312423 |  | note | Inspection/Test Method - Verify
label | 17d31cd7-172a-5a27-b550-5cef99ad77ce |  | note | Record of conformity - This ITP signed
label | 4d590bf8-5081-5894-a2b4-5b161ed967fb |  | note | IP
label | 53d97e94-87e1-5ed2-b6ab-66f519b380ae |  | note | Responsibility - Project/Site Engineer, Surveyor
date | 9dfd43f7-e8ef-503e-bd0b-4685d0cc6190 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Temporary Supports
label | 284bf415-c66d-52fc-87f8-f1d3317cd3e5 |  | note | Frequency - Each Lot
label | c5a0bfd9-acef-5e79-9960-d1bba05f5585 |  | note | Acceptance Criteria - Check demolition will not affect any structural or service supports, if so, temporary supports will be provided until it is no longer required.
label | 25fd1501-6624-532a-8618-4460e259eb3a |  | note | Reference Documents - Spec cl. 8.5.3
label | 4527299f-b244-5799-ba2a-31ec22a6e6f8 |  | note | Inspection/Test Method - Verify
label | bff6d09d-e026-51bf-8796-48ecd81b755d |  | note | Record of conformity - This ITP signed
label | 26408a23-98a8-529a-8c69-e60a9c256fc1 |  | note | IP
label | 9cb94ee1-978c-577c-a441-c9a96ac698b7 |  | note | Responsibility - Project/Site Engineer, Superintendent, Foreman
date | c6fd8ad7-c9a7-519e-bb7f-7215c1ca0594 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Disposal of Material
label | edeeb9de-8f1d-5408-948d-f170556aefb9 |  | note | Frequency - Each Lot
label | 62348367-a089-5ff2-965a-d5b97f1490d5 |  | note | Acceptance Criteria - Demolished clean concrete material will be taken to Vic Civils at Gate 8, for concrete recycling. Contaminated or PFAS material are to be taken to Gate 11 to be stockpiled into their dedicated category and contaminant. Any discovered contaminated material found on site, that are not already known, will be notified to the client immediately.
label | d51bfb7b-fb2b-5e85-bb31-102f96a844ab |  | note | Reference Documents - Spec cl. 8.5.5
label | 628bdfa2-776a-56b3-ad7f-2c6f15db31a7 |  | note | Inspection/Test Method - Verify
label | 34eb3d96-c6e2-5c48-a27e-e66ecd8623f7 |  | note | Record of conformity - This ITP signed
label | eab19740-24a5-5057-b0a7-4656c968481d |  | note | IP
label | 6ef59242-739d-584c-9780-6332e3011149 |  | note | Responsibility - Project/Site Engineer, Foreman
date | 4d348c96-f5be-5a9b-a86f-4c97db7f50b6 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Asbestos Materials
label | 4973ee8e-e824-5621-8769-1660434f041c |  | note | Frequency - Each Lot
label | 50401d4f-5850-55fc-867d-33e4e17c44a6 |  | note | Acceptance Criteria - If asbestos material is identified, works are to be stopped until test is conducted to verify the asbestos. If asbestos is confirmed, licensed subcontractors are to remove and dispose the asbestos out of site.
label | c8338bbf-c5cd-5c6d-8560-17ec9a11dcf2 |  | note | Reference Documents - Spec cl. 8.5.6
label | 63eac01c-1285-511f-9009-807a05066da4 |  | note | Inspection/Test Method - Verify
label | deb03700-7275-57e9-8b52-ec1baaf14c47 |  | note | Record of conformity - This ITP signed
label | 1919a9ee-a3fc-5a1d-a43f-206f21f2ed84 |  | note | HP*
label | 2660f46f-ffde-5d8d-ba2b-1fe0c70f3c7f |  | note | Responsibility - Project/Site Engineer, Foreman
date | f9a21230-85e8-5c8a-8766-654ec65b288f |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.5 - Made Good
label | 2e649beb-1249-56e7-bdf6-b2a3358aed94 |  | note | Frequency - Each Lot
label | 72cb9da6-7592-566c-a0c5-7bad14187df7 |  | note | Acceptance Criteria - Removed and demolished pits and/or cavities are backfilled and compacted. Backfilled areas match adjacent existing surfaces.
label | a122d8df-a5a6-5039-abe3-45ddf042b566 |  | note | Reference Documents - Spec Cl. 8.5.7
label | 032378c0-9e5f-5fe6-9c7c-a7a25c0cc35f |  | note | Inspection/Test Method - Verify
label | de1d9087-ec08-57fa-9c3b-a8e2f082dd8a |  | note | Record of conformity - This ITP signed
label | 753bd93d-d588-5243-bb18-80ffc50e8cb1 |  | note | HP*
label | 95172b46-6943-5d2b-b5b9-60aef6f9cecb |  | note | Responsibility - Project/Site Engineer, Foreman
date | 0d69e2a8-438f-5fbd-be52-ebd47e1cc6e7 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | 2e649beb-1249-56e7-bdf6-b2a3358aed94 |  | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
text | 72cb9da6-7592-566c-a0c5-7bad14187df7 |  | textbox | Print Name:
text | a122d8df-a5a6-5039-abe3-45ddf042b566 |  | textbox | Position:
date | 032378c0-9e5f-5fe6-9c7c-a7a25c0cc35f |  | date | Work Completed On:
date | de1d9087-ec08-57fa-9c3b-a8e2f082dd8a |  | date | Date:
checklist-sectioned |  |  | checklist | ITP004 - Select Fill Placement | itp |  |  |  | Yes | FH-ZU2-QU-ITP004 - Select Fill Placement - Rev 0 | 7b74922b-d98b-4973-8d9b-f42b3f6a3132
checkpoint-group |  |  | section | 1.0 - Preliminary Activities
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | 08c4b17e-a29e-56a5-be50-2ab69afd4d71 |  | note | Frequency - Prior to works
label | ec07a3cb-c1f0-5188-bcf9-00a8a0a7c914 |  | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
label | 0afb9d20-3984-59f9-afad-cbce551ff055 |  | note | ○ Using the correct and complete set of drawings.
label | 9934483f-2306-58cc-9494-554d12355379 |  | note | ○ All drawings are the latest revision
label | ffc9abf8-4d0f-5d97-bd9f-25c82ca3379e |  | note | Reference Documents - Aconex
label | ab0c1193-80ea-588b-943d-7498f0b43bae |  | note | Inspection/Test Method - Verify
label | 9190310b-61ff-55e1-b585-7c6deddfd16d |  | note | Record of conformity - This ITP signed
label | d5d4dd88-73b5-5173-aa38-2d4c061b361e |  | note | IP
label | f1a09c02-c144-573f-9bf1-fc6e921e59dc |  | note | Responsibility - Project/Site Engineer
date | 5582b486-373d-5a50-a97b-1b17f5be5c85 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | b26f041a-9e1a-53f5-a2a7-ae357fb1b158 |  | note | Frequency - Prior to works
label | 5f736424-2c68-5813-9f3e-9938bc60e9e0 |  | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS and WP.
label | f2c2258a-099b-5a2d-bbb8-405e99612b87 |  | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
label | 2a982293-b48a-53b5-9ab5-3e0ad4ffa560 |  | note | Inspection/Test Method - Visual inspection
label | 4651ff39-7b00-5362-9150-e2db58cfff0d |  | note | Record of conformity - This ITP signed
label | 2f29ce51-e199-555a-98f0-058275729f9f |  | note | IP
label | 2f332fd5-58f8-54ee-b8b4-6bcfbdb45e3b |  | note | Responsibility - Project/Site Engineer
date | 847d413e-f5a2-5801-bdce-d489bf57302a |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Survey
label | b94c6f79-9487-5050-adc7-6028f0f7816c |  | note | Frequency - Prior to works
label | bb4e26e8-aa42-5610-aa37-25d1a70889db |  | note | Acceptance Criteria - Area has been surveyed, highlighting any areas where excavations should not occur (e.g. exclusion zone).
label | d71e8c39-5636-59d4-aeb9-34f2bc826c1b |  | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
label | a5158671-8dd3-51d0-8cea-a932a5e0b6ce |  | note | Inspection/Test Method - Visual inspection
label | 5e36ac1e-3494-5b2b-8bbe-78c39bdf135f |  | note | Record of conformity - This ITP signed
label | 09f23b99-26a6-52f7-a317-f1e4add963d3 |  | note | IP
label | 2bb97587-0580-57bc-8c47-320a24478bc9 |  | note | Responsibility - Project/Site Engineer Surveyor
date | 43a2c40b-d1a0-5c47-a992-6064ca6125ff |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.4 - Select Fill Material Source (Under Pavements, Imported)
label | daaba572-1025-5653-afd5-9bf625b59ef9 |  | note | Frequency - Prior to works
label | cbb4fed3-7ecd-5ef1-9d34-d585415b842c |  | note | Acceptance Criteria - Material to meet the following the properties:
label | be36a13f-2979-5221-b8a4-81124970ae9a |  | note | – – – – – – – – –
label | 00897eec-50ef-56f5-b303-a4a67d250bfb |  | note | Wet strength ¦¦ Not less than 125 kN wet/dry strength variation less than 40%
label | 49dcfc3f-2abb-5459-8068-e575a930b0fe |  | note | – – – – – – – – –
label | 2c356531-e24e-5bfe-a5ed-558c7e48cfbf |  | note | Linear Shrinkage ¦¦ < 6%
label | 1e1a2f50-b31b-599f-b1b8-b6cedf70dba4 |  | note | Organic Matter Content ¦¦ < 0.2%
label | 4dec1663-fb29-55bd-95db-83504927c099 |  | note | Maximum Particle Size ¦¦ 75 mm
label | 28ecf767-cd52-5370-a3ff-72d6443e29f1 |  | note | % Passing 0.075 mm sieve ¦¦ 0-12%
label | 476e4531-4980-5b57-a950-4372438293d5 |  | note | Soaked CBR ¦¦ > 20%
label | b265c9d2-38af-59c4-8e30-d0393ed05e4d |  | note | CBR swell % ¦¦ ≤ 1.5%
label | c9074b6f-1d34-594b-b824-102bd68533e0 |  | note | Permeability ¦¦ < 5 x 10-9 m/s
label | d8ecc50e-bce7-5f79-8a5c-a4b2dc1bfc3f |  | note | – – – – – – – – –
label | d8e6513b-c0b9-52ee-bf6c-8f331b0195b6 |  | note | Material Property:
label | 814c752b-bb60-50f1-96f9-edf0e7c737d7 |  | note | – – – – – – – – –
label | c0a6959d-2e3d-5fb8-ac12-ff1d57863ae2 |  | note | Material Property ¦¦ Requirement
label | f2a02c5d-7e16-43b5-bb11-24639f86353b |  | note | Liquid limit ¦¦ < 35%
label | 6023c1d1-dc64-42b9-b566-66672555818b |  | note | Plasticity Index ¦¦ < 12%
label | cf82e18b-2dd1-4b6c-af80-f76a73ba9eb2 |  | note | Wet Strength ¦¦ Not less than 125 kN Wet/dry strength variation of less than 40%
label | a6256b04-31e1-4c46-bb8b-be1963b43002 |  | note | Linear Shrinkage ¦¦ < 6%
label | c25f9859-1f75-4146-8214-12162e402f21 |  | note | Organic Matter Content ¦¦ < 0.2%
label | 28a6fc05-a96f-400f-9a83-f665e36487fe |  | note | Maximum Particle Size ¦¦ 75 mm
label | 18e70ce3-cd41-4e80-b2e7-cdecd621e86f |  | note | % Passing 0.075 mm sieve ¦¦ 0-12%
label | 426ddf19-4a19-428c-81d9-a0976b6ba863 |  | note | Soaked CBR ¦¦ > 20%
label | 56b31f61-ec77-4a26-9c02-193aec6fd96f |  | note | CBR Swell % ¦¦ ≤ 1.5%
label | 3c76cdd8-3729-43ea-9684-809f18ec2000 |  | note | Permeability ¦¦ < 5 x 10^-9 m/s
label | 279ea369-5031-4f1b-91e8-626b863153c5 |  | note | – – – – – – – – –
label | d5283e63-ac96-4ffb-8466-b3b6a9038e9a |  | note | Gradings:
label | c2e5e53a-5d01-4f32-a8cb-c9d3eec343f1 |  | note | – – – – – – – – –
label | e962e5c9-1583-517a-8479-ab3ac3cd2746 |  | note | AS1152 Sieve Size (mm) ¦¦ Percentage of mass passing sieve size
label | cfe1cd19-1284-5aa2-9cf8-91fea8545b4f |  | note | – – – – – – – – –
label | bed041fd-d001-5108-af09-ef0e9711b9e0 |  | note | 75.0 ¦¦ 100 to 100
label | f320a33c-f6e6-5e94-99ea-c648d595de8b |  | note | 37.5 ¦¦ 67 to 100
label | 2f304236-d42e-550f-bb74-14664bc6880a |  | note | 26.5 ¦¦ 54 to 100
label | 1c1acd2b-5d4c-5220-9478-f62ad2876162 |  | note | 19.0 ¦¦ 44 to 85
label | 6d8636bc-a42b-5f14-9b5f-c72cb8ab9d44 |  | note | 9.5 ¦¦ 31 to 65
label | 31e3bec9-ba20-56cd-8c5a-6f576fda8073 |  | note | 4.75 ¦¦ 21 to 50
label | 0faee927-3dcf-5944-91aa-5c5917c5dccd |  | note | 2.36 ¦¦ 13 to 38
label | c568518d-b7e3-533f-a9a7-bc6383d1fb15 |  | note | 1.18 ¦¦ 9 to 30
label | b3f56a11-f6f1-5983-937f-1d114c23c723 |  | note | 0.425 ¦¦ 4 to 23
label | 0d6d1251-8dbd-5410-b46f-a3b6e67d4b61 |  | note | 0.075 ¦¦ 0 to 12
label | d6ae7631-afe6-5798-9b1a-d28144e937a3 |  | note | – – – – – – – – –
label | 040eeceb-01be-5cb7-acbf-c3f57fee68c1 |  | note | ○ Production testing if supplied select fill will be: 1 per 1,000t for first 5,000t, increase to 1 per 2,000t following conforming 5,000t of conforming results. If material source changes, testing to be re-conducted from start.
label | 04ffc556-268c-52b6-b721-d92339b742b2 |  | note | Reference Documents - Spec 002 – CL2.5 Cl2.7.5
label | 3ca23b7d-514d-5470-97a3-39d41093fa60 |  | note | Inspection/Test Method - Test Report
label | 9c5f393c-f175-51db-9434-fda4147480d2 |  | note | Record of conformity - This ITP signed
label | 8a63c909-49de-5436-b4b5-575aefd813ac |  | note | HP
label | 02927e97-19f7-5fbe-a3b4-eee1b7c62d58 |  | note | Responsibility - Project/Site Engineer Principles Rep
text | da34b4ca-7a9f-578d-9c02-d4fabb27fd31 |  | textbox | Checked by: Principles Representative - Aconex:
date | 071c1a9c-2607-5e67-a29d-6a65f01f5cb8 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.5 - Select Fill Material Source (Other Locations, Site Won)
label | 063b6ae1-0810-55a7-b6a7-6b5db22bfcbb |  | note | Frequency - Prior to works
label | 258f4ebc-f34d-5d30-bd3f-22d86510d714 |  | note | Acceptance Criteria - Each source of select fill shall be approved by the Principles Representative.
label | ac6389cc-17e2-595b-b34b-dd88ffe8864e |  | note | Reference Documents - Spec Cl 2.6.2
label | 719895c5-7f3e-5091-ba15-8a37bcc0b054 |  | note | Inspection/Test Method - Test Report
label | b178ae95-a6a8-5f30-a71e-77c3180b179a |  | note | Record of conformity - This ITP signed
label | 5fea5191-b455-5379-a562-341e47f23a5c |  | note | HP
label | 1b1175c9-563b-5f66-9a51-8150698498ab |  | note | Responsibility - Project/Site Engineer Principles Rep
text | e3e36edf-af24-4dfa-9403-05f346394d44 |  | textbox | Checked by: Principles Representative - Aconex:
date | 51923049-c02d-5ec6-b16f-c5aea6323641 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.6 - Submission of Select Fill Methodology Plan
label | d005a128-0585-5c5f-a4ed-dc6cd7fed680 |  | note | Frequency - 14-days Prior to works
label | 7f0a4f4d-b378-5a12-b0e4-f56352981a2f |  | note | Acceptance Criteria - Principal Contractor to submit a Select Fill Methodology addressing the criteria listed in Spec cl. 2.3.1. Hold Point to be released by Principal’s Representative after acceptance of Select Fill Methodology.
label | 9669e478-dd97-5343-81cd-5199ba8b11fb |  | note | Reference Documents - Spec cl. 2.3.2
label | 9a4f811b-2c81-59e0-bc06-90aeeca2bea8 |  | note | Inspection/Test Method - Select Fill methodology & verify
label | 7ee34b39-a2d3-5e3b-b6b4-d71bab0d7184 |  | note | Record of conformity - Select Fill methodolog y & this ITP signed
label | ab118804-4cfd-581c-a8b2-4173b3f62ba2 |  | note | HP
label | c427744c-00ec-5244-95ee-1968a0a0506d |  | note | Responsibility - Project/Site Engineer Principal’s Rep
date | 3ff59667-9db9-5e0f-af41-a6422fa1c607 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.7 - Starting Works
label | 191a663e-328f-5ce5-a946-a8d013cca794 |  | note | Frequency - Prior to works
label | 6988de33-b3cc-59d5-ab8d-79735df2e94a |  | note | Acceptance Criteria - Principles Representative to approve works starting in each Separable Portion
label | d953518c-4665-5be5-9df4-3b5706752e35 |  | note | Reference Documents - Spec cl. 2.3.1
label | 8da07ef4-0244-55ed-84cb-82af9c176d0f |  | note | Inspection/Test Method - Verify
label | 9c0d8931-832c-56ec-b854-27402cac329e |  | note | Record of conformity - This ITP signed
label | 01cc9dd3-f181-5d4e-b595-c5bddced1061 |  | note | HP
label | 1c0dfe50-17e6-5aec-a644-70f7bd58cd85 |  | note | Responsibility - Project/Site Engineer, Principal’s Rep
text | f8c8d075-b3c2-428c-b172-8159d39d679b |  | textbox | Checked by: Principles Representative - SP8 Aconex:
text | b154fc99-0a6d-550d-b606-cf95d0f9bece |  | textbox | Checked by: Principles Representative - SP9 Aconex:
text | 5e843dd3-b3d2-5eb4-9338-9d3baeddc93d |  | textbox | Checked by: Principles Representative - SP10 Aconex:
date | ed099b5c-abd0-5fc3-bf77-6287326c1569 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.8 - Preparation of Underlying Surface Layer
label | 3fd33117-7eb2-586f-aa85-c38c3a5e3e4e |  | note | Frequency - Each lot
label | d49700fe-80cf-52d1-b05b-5a9dd1b1a079 |  | note | Acceptance Criteria - All excavation and filling are free draining to low points clear of the working area. Sufficient pumps, well-points, or other equipment for work area are de-watered as required.
label | 29337356-89d0-56e5-9ce6-bb65769f6fa6 |  | note | Reference Documents - Spec cl. 2.8.2 ITP003
label | be289948-f406-5e5d-aa09-44a86a08572d |  | note | Inspection/Test Method - Verify
label | 6554c8ee-bac9-53ad-8ac4-0c6a0f9b9336 |  | note | Record of conformity - This ITP signed
label | 509f5b45-e354-5884-871e-a14c5219f88e |  | note | IP
label | a8de60f0-59c1-5c31-8c97-7ab7c45d6531 |  | note | Responsibility - Project/Site Engineer Foreman
date | 843759f7-5dbd-5c16-aced-bd975265065d |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.9 - Cut Floor Level
label | 6c8d8f56-6505-5557-a082-4e1a61cb67ac |  | note | Frequency - Prior to works
label | e41bf1b5-9786-5635-8da4-452b93549516 |  | note | Acceptance Criteria - Cut floor to be inspected for suitability - compacted, firm and dry
label | b5ec83c9-941c-5393-a618-6317d028adb3 |  | note | Reference Documents - WMS003 cl 3.3.3
label | 4d0e6c39-2d95-58d1-8054-9ff4a0c20dc4 |  | note | Inspection/Test Method - Verify
label | 1357443b-4fe8-50f2-bc24-5754a41f44d2 |  | note | Record of conformity - This ITP signed
label | 8ca3c972-2063-5790-8b54-d410a0ba7407 |  | note | HP*
label | 47799b55-8c62-5420-b582-d3bfe6e9728d |  | note | Responsibility - Project/Site Engineer Foreman
date | a61bf0fe-c74c-5468-8b07-734f781a523f |  | date | Date Completed:
checkpoint-group |  |  | section | 2.0 - Select Fill Works – Imported Material - Under Pavements
checkpoint-status |  |  | checkpoint | 2.1 - Select Fill Placement
label | a285683c-8b89-5d00-8ee5-7dd4aed4cce1 |  | note | Frequency - Each Lot
label | 1088eff9-1f90-59a7-b41b-14d0f0ad1908 |  | note | Acceptance Criteria - Each Lot of fill must:
label | 76abb573-0b41-5839-8ab6-8f3a78d19147 |  | note | ○ Not be greater than 200mm in thickness
label | c7e45ad8-2f77-5838-8b90-c5dfcf3d6e79 |  | note | ○ Material is to maintain within 1% of the optimum moisture content during all steps of placement, compaction, and finishing
label | 678a7288-b1b6-53dc-b1f4-3c67e7ce5832 |  | note | ○ Placement of material to commence at the crown or the highest side of the pavement, with each lane spread adjacent to the previously placed lane
text | ae18ee55-133d-4030-a099-fa46d32f59f9 |  | textbox | ○ The first layer of placed material is dropped and spread using a dozer, grader, or similar plant to prevent trafficking 7mm seal
label | af09624f-e3c1-5797-9314-8274a1c59ed7 |  | note | ○ Material to not be contaminated by foreign materials and other contaminants
text | 90c3fdc8-a923-4e70-8403-04a9ffc41923 |  | textbox | ○ Plant and equipment does not traffic 7mm Aggregate Seal
label | 3dbc7cb7-6509-580f-91f9-e9a368e88d35 |  | note | Reference Documents - Spec cl. 2.8.4
label | f4e6e6d0-2488-542e-a580-ab6ff313a746 |  | note | Inspection/Test Method - Verify
label | 255c8a3e-d31e-5112-864d-8f0b1a95a4c9 |  | note | Record of conformity - This ITP signed
label | cbb35942-afe0-5989-8175-5db882b1f056 |  | note | HP*
label | 5f20e431-67c6-5049-94d6-bf6ddc20f219 |  | note | Responsibility - Project/Site Engineer Foreman
date | d8351717-5829-52da-9630-21fa92547fd8 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Proof Rolling & Compaction
label | f6bcdc13-2b29-5e73-a520-feffb5a5ff4c |  | note | Frequency - Each Lot
label | e256642d-13d3-5932-b4a9-3a0ded3bfdae |  | note | Acceptance Criteria - Each layer of select fill under pavements is to be inspected with the Principles Representative.
label | d7d39b8c-6eb2-537e-8c6f-760b58edb6fe |  | note | ○ A medium size vibrating roller (or larger) is to be used for all proof rolls.
label | ba9f68a4-a645-56b1-abbe-2ce5f7244fd2 |  | note | ○ At least 5m of longitudinal Select Fill and 500mm of lateral overlap of proof rolling between adjacent areas is needed.
label | 4f3eb4f4-7107-5840-9dee-53fc6614bbc9 |  | note | ○ At least one working days’ notice is to be provided to schedule the presence of the Principles Representative.
label | 24ebd48e-de5b-5a02-b3d8-bd75dd473447 |  | note | ○ Maximum allowable rutting of 25mm.
label | 8400133a-8770-5d5c-aa61-6afb25a99e31 |  | note | ○ No heaving to be observed.
label | d47c6d07-a0d7-4b4c-a959-37094aa81598 |  | note | ○ Proof rolling of the select fill will be approval to place Sub-basecourse or Basecourse. If rain falls on select fill prior to placing next layer, a further inspection will be required.
label | aa8ce4a4-dfad-50ae-9679-f4a320171abc |  | note | Reference Documents - Spec cl. 2.10, Spec Cl 4.6
label | 43d9517b-b833-59e1-a928-f0e9191db911 |  | note | Inspection/Test Method - Visual Inspection & Verify
label | 007a5866-30c6-5e94-9f7b-eda3d6be2915 |  | note | Record of conformity - This ITP signed
label | 75d45070-7e38-5e90-be33-a40b6c4d25f9 |  | note | WP, HP, HP
label | 1035b6bc-5313-55a3-89f8-247dc8516c36 |  | note | Responsibility - Project/Site Engineer Principal's Rep
date | e74b8669-4382-5781-a35f-13ab9e7a638b |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Final Trimming and Surface Finishing
label | b969e5f6-98cc-5976-a1db-96e747fccfd0 |  | note | Frequency - Per lot (final layer only)
label | c5073318-1d2b-5d22-8b0a-7bfc85218377 |  | note | Acceptance Criteria - Final layer of Select Fill surface to the required level, grade, and shape with a tolerance of +0mm and -25mm. Intermediate layers of select fill do not require a Survey Conformance Report
label | bbcd9e54-00b8-5001-8b05-4da4db95e2bb |  | note | Reference Documents - Spec cl 2.11 WMS003 – cl3.4.5
label | cb48011c-a1e9-5dfd-ae7d-68851eeacc67 |  | note | Inspection/Test Method - SCP
label | 61bdba24-af61-5bcf-8e88-65004e5e2603 |  | note | Record of conformity - This ITP signed
label | cbc322f2-a319-54e9-95bd-9652bfb5dd3d |  | note | HP
label | d843fe42-ddf3-58e3-b760-959cd61a1cff |  | note | Responsibility - Surveyor, Project/Site Engineer
date | 5f10bc1c-6362-5c7f-b1df-be0007331eb8 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 3.0 - Select Fill Works – Site Won Material – Other Areas (Not Under Pavements)
checkpoint-status |  |  | checkpoint | 3.1 - Select Fill Placement
label | dd600633-1855-5efb-aa7a-b22b1a16b9ad |  | note | Frequency - Each Lot
label | 6cf86ae2-1ebf-5597-a601-ce96a64e12c9 |  | note | Acceptance Criteria - Each Lot of fill must:
label | 5c46b0da-a8eb-525b-805d-7a15fe1ddb17 |  | note | ○ Not be greater than 200mm in thickness.
label | ff7b2559-af03-547a-9188-aff61a7ed3ad |  | note | ○ If required, material to be lightly watered to aid in compaction.
label | 164428fd-9f41-5a84-989b-371e5ef907e5 |  | note | ○ Placement to start on the high side.
label | 606c0f40-6a0a-5a36-a25b-d94b5802f1b9 |  | note | ○ Material to not be contaminated by foreign materials and other contaminants.
label | 595e330f-84d7-5d07-bdd1-f36f30d40394 |  | note | Reference Documents - Spec cl. 2.8.4
label | 261751eb-649e-54fc-858d-2c38f03f9163 |  | note | Inspection/Test Method - Verify
label | 6a4957a0-b9ab-5808-9006-ec62b9ccf935 |  | note | Record of conformity - This ITP signed
label | 84c8b8d1-03dd-59e6-9d99-6c4ff276b04f |  | note | IP
label | 2a1f2666-ba88-513c-b479-bda9af6ebe9e |  | note | Responsibility - Project/Site Engineer Foreman
date | 3cd2359e-478d-5a7c-937b-723ea792aa09 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Proof Rolling & Compaction
label | 61716091-7ff1-53da-be97-6525d3ab0d02 |  | note | Frequency - Each Lot – intermediate layers
label | 0e621325-bc78-538e-9d1c-ad5c898e2500 |  | note | Acceptance Criteria - Intermediate Layers
label | 7eb80e75-eeda-5830-bbf2-877aa402d695 |  | note | ○ Each intermediate layer will be visually inspected for conformance to the specification following compaction.
label | 16d757da-361e-5a78-a738-deaa432d1861 |  | note | ○ No rutting greater than 25mm observed
label | de4e646d-a05c-5dcd-bdaf-e12065b7296b |  | note | Reference Documents - WMS003 – cl3.4.4.1
label | 1121916d-79fd-5972-b23d-a650ab4d24a8 |  | note | Inspection/Test Method - Verify
label | 1c5f4405-0f62-5fb5-8c5f-310627cbe0fb |  | note | Record of conformity - This ITP signed
label | 554a3ed7-20f7-5e35-83f7-6728a552da00 |  | note | HP*
label | e63bbe64-3698-541a-9ae4-d8da7237141a |  | note | Responsibility - Project/Site Engineer Foreman
date | ccaaa446-44ab-5a1a-af6f-eff82876dee0 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Proof Rolling & Compaction
label | c08bae98-5572-5c0f-bc54-6c2e4e967af5 |  | note | Frequency - Each Lot (final layer only)
label | c5d002ec-66be-5b68-8f97-eae95a2aed15 |  | note | Acceptance Criteria - Final layer
label | 546f7143-3279-5d94-9daf-380e3a1eaf5c |  | note | ○ Principles Representative to be invited to visually inspect final layer of Select Fill not under pavements.
label | 333ff332-9e8b-5a29-a97a-d2e1c8e1531e |  | note | ○ At least 5m of longitudinal Select Fill and 500mm of lateral overlap of proof rolling between adjacent areas is needed.
label | 5d380afc-eb96-5670-9bfd-668848f80509 |  | note | ○ If requested, Proof rolling is carried out in the presence of the Principles Representative
label | d960ea35-51db-573f-89d1-ce44c75a5cac |  | note | ○ If requested, at least one working days’ notice is to be provided to schedule the presence of the Contract Administrator.
label | b49298b2-d1ef-5f42-8be4-cf51205e8922 |  | note | ○ Maximum allowable rutting is 25mm.
label | af69c2c0-630e-5064-96fa-814131dd5fee |  | note | ○ No heaving to be observed.
label | b59bcabf-c714-52e2-92ff-fa9244039adc |  | note | Reference Documents - Spec cl. 2.10 WMS003 – cl3.4.4.1
label | 381fbbab-cc3c-5605-9803-bee173c2d21b |  | note | Inspection/Test Method - Visual Inspection & Verify
label | 716b97f9-32ec-58ce-8d4f-8e536b454e40 |  | note | Record of conformity - This ITP signed
label | 93ca3368-b935-5713-9776-0469b8471dbd |  | note | WP, HP, HP
label | 5c34c3a5-4097-5295-a686-eb8106c9fb84 |  | note | Responsibility - Project/Site Engineer Principal's Rep
date | 40dbf905-4676-5e94-ae72-655a8ae24718 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 4.0 - Testing & Acceptance
checkpoint-status |  |  | checkpoint | 4.1 - Classification and Testing (imported material, under pavements only)
label | 497bfaa0-6206-5775-81af-233539a11d92 |  | note | Frequency - Each Lot
label | 271fc17f-30a4-59e8-bbca-65edc4f02acc |  | note | Acceptance Criteria - Imported Material Under Pavements
label | 27355161-24bb-5967-93e9-dda843f4ba98 |  | note | – Dry Density as per AS1289.5.3.1
label | 3179e986-b82b-5056-98ff-4aabbe83c0dc |  | note | ○ 4 test per lot to achieve average
label | e64042f7-dd1c-50be-926d-7c64a5cbf840 |  | note | ○ Minimum average standard dry density ratio of no less than 98.0%.
label | fdb3a14a-9a9e-55d1-ab92-eb781d5eda6f |  | note | ○ No single standard dry density ratio test result being less than 97.0%.
label | 4dfaf25b-ec5f-5a98-b76f-018000e525bb |  | note | Reference Documents - Spec cl. 2.9 AS1289 5.3.1, AS1289 5.4.1, AS1289 5.8.1, Spec tab. 2-3
label | cde87d4d-e124-5808-9805-530b6d47ec39 |  | note | Inspection/Test Method - Verify
label | 20e31860-c7e0-59f1-bbe5-e62b5343e90b |  | note | Record of conformity - Test results & This ITP signed
label | fec63964-1ec3-5c2e-b894-f48a5a9eee1d |  | note | HP
label | befcf3c6-d0dd-5b27-b626-a9a33bf6131f |  | note | Responsibility - Project/Site Engineer, Principles Rep Foreman
date | 57cd6c31-ace6-54db-9b2e-2802c5fd7311 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.2 - Lot Acceptance
label | fd6d64c3-6ffb-527d-8b4b-bcb152ea8af2 |  | note | Frequency - Each Lot
label | 6094e51b-56c8-55be-81e7-ccc9388928af |  | note | Acceptance Criteria - Principles Representative to review acceptance of lot according to table 2-3. Acceptance of lot will not hold up placing succeeding layer of subbase.
label | 2da0f362-8c08-58fe-9a83-451b169eb89d |  | note | Reference Documents - Spec Table 2-3 Cl2.12
label | 5cadbf22-2e7d-5c0b-8f81-bb24150c0f16 |  | note | Inspection/Test Method - Verify
label | 5317b649-84e5-5a25-8ad7-23504448e577 |  | note | Record of conformity - Test results & This ITP signed
label | 565abba3-17d0-5afd-9e87-56fb95d8fbf4 |  | note | HP
label | c23be552-5ce0-5137-bd63-cde77864010b |  | note | Responsibility - Project/Site Engineer, Principles Rep
date | f8286b5b-50b2-5dec-af24-fffc837e80cd |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | Final Inspection
label | c99016f3-cb40-5a62-aebc-b4d7bb465048 |  | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
text | f2bc87cb-c91c-5291-95da-3deaa91d47f1 |  | textbox | Print Name:
text | 997fdfdb-a196-5436-9205-97836b076b0c |  | textbox | Position:
date | 68dcca9c-d28c-529d-b4b1-3ceac23b94e3 |  | date | Work Completed On:
date | 2181d0aa-ae54-5dfc-8386-981fe6cd1902 |  | date | Date:
checklist-sectioned |  |  | checklist | ITP005 - Stormwater Drainage | itp |  |  |  | Yes | FH-ZU2-QU-ITP005 - Stormwater Drainage - Rev 0 | 83f202df-0ed7-499d-abd2-6f7b84d31412
checkpoint-group |  |  | section | 1.0 - Preliminary Activities
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | 54e098fd-2875-533c-ae63-868a90e30081 |  | note | Frequency - Prior to commencing activity
label | 3a9488af-ceef-526d-a9e6-e8a30e966b9f |  | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
label | 471f36d6-b4b4-5388-a9d2-5ae7ece93b5f |  | note | ○ using the correct and complete set of drawings
label | 8f7a1599-66cb-573c-9016-a55fbc589bc8 |  | note | ○ all drawings are the latest revision.
label | c2e5a589-5901-5b02-9701-76e4ce132a9a |  | note | Reference Documents - Drawings and Aconex Register
label | a2ee1067-eb31-532d-8b47-6005b527fbc3 |  | note | Inspection/Test Method - Visual Inspection
label | bfafb1b0-e9c1-591c-b5de-dc2927d5d9b0 |  | note | Record of conformity - Up to date drawing sets & ITP
label | 839ea919-c7d7-547f-a4c5-a127348d8a0e |  | note | HP*
label | 95bf2957-8d71-57ca-98d9-f701505fe279 |  | note | Responsibility - Project/Site Engineer
date | 16f17a8f-429d-5221-b86f-2a3ff34b50bc |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 2b1c2541-a2e3-53ee-acdf-59d7d816963e |  | note | Frequency - Prior to commencing activity
label | 56e020d7-7c16-5716-9b87-daa768345924 |  | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: CEMP, TMP, SWMS & WP.
label | bc2543d4-aa2d-54cf-a7b6-1c651c7eef89 |  | note | Reference Documents - CEMP, TMP, SWMS & WP
label | b2945d35-791b-5282-9eab-f1096aae2e5c |  | note | Inspection/Test Method - Verify
label | 6743976f-a864-5448-8b47-d3bd43ab57a1 |  | note | Record of conformity - Site and Office Inspection
label | f3bde6b2-9eeb-5f16-a6fd-7ab73df5c502 |  | note | HP*
label | 7247c46e-49a4-5101-afd6-c19f89422b74 |  | note | Responsibility - Project/Site Engineer/Supervisor
date | a959ad58-ba7b-515e-934e-cfe533042728 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Excavation Permit
label | 67c58622-d040-5817-8e40-c14ba3c81201 |  | note | Frequency - Prior to commencing activity
label | 858c6e33-5f6d-5f36-b9be-131e6512679b |  | note | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
label | d89748f0-3fe4-5f6e-bd16-db487ca14c10 |  | note | Reference Documents - Excavation Permit
label | 5ac316e1-5683-5604-bf46-2f6aa45e1fe3 |  | note | Inspection/Test Method - Verify
label | 2a3b06da-8a9d-55ae-a1b3-00d7413308e1 |  | note | Record of conformity - Proof of signed permit
label | 62992194-6156-50b2-81f9-ef93471b5596 |  | note | HP*
label | 11702d77-2c52-5332-81a8-f6e2b636d283 |  | note | Responsibility - Project/Site Engineer
date | 5da7027f-4163-53a4-8cf3-0db8251e49d5 |  | date | Date Completed:
checkpoint-group |  |  | section | 2.0 - Stormwater Products and Materials
checkpoint-status |  |  | checkpoint | 2.1 - Drainage Pipes (RCPs)
label | 41d9fad8-a375-534c-a828-f397d7515358 |  | note | Frequency - Prior to commencem ent of works
label | 6f00cc3b-c4a0-5f15-b5f6-bf98b9efe43f |  | note | Acceptance Criteria - Drainage pipes supplied in accordance with AS4058. Material submission approval.
label | bb56e26e-19e7-566c-ba5d-74cdce66240b |  | note | Reference Documents - CL16.6.1
label | b162d0c8-25a1-5911-b3f4-0422cfa98d99 |  | note | Inspection/Test Method - Document Review
label | 8228597f-c73b-526f-af9d-351be9066490 |  | note | Record of conformity - Aconex
label | 25943020-9f4e-5ca1-bb79-37472b1edede |  | note | HP
label | ad6d63b5-fe57-5348-bd57-1d841f377ee4 |  | note | Responsibility - Project/Site Engineer, Beca
date | d8eba816-e46c-541d-aec8-fefd40c15961 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.2 - Pipe Support Cradles
label | 8d618c69-5b5e-5645-817f-836c8e834b02 |  | note | Frequency - Prior to commencem ent of works
label | 9c03adc9-e7de-52a6-993c-ccf61071cfe7 |  | note | Acceptance Criteria - Pipe to sit on firm foundation with pipe support cradles. Material submission/ Shop drawing submission.
label | cea46deb-31cf-5803-af12-5fe92b2db20f |  | note | Reference Documents - Cl16.5.6.1
label | b213bf5e-eb9c-5753-b606-7d40d87cd7e4 |  | note | Inspection/Test Method - Document Review
label | a40cf2e5-0db3-51ea-b1c4-75fbd7cbc6d1 |  | note | Record of conformity - Aconex
label | 076afd1f-35a5-5927-a7fc-edd5de7cec1e |  | note | HP*
label | 3a0220cb-cceb-5803-a539-4a7b71938cac |  | note | Responsibility - Project/Site Engineer
date | 5acb6203-0f4b-5ceb-886a-84cdc070e164 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Encasement Material
label | 046121b9-b4f0-54f0-8a63-31d5a43a9243 |  | note | Frequency - Prior to commencem ent of works
label | cfed6de3-a0e4-56e6-a0f6-bd5a01012fcb |  | note | Acceptance Criteria - Encasement Material to be 5Mpa lean mix concrete for all RCP’s. Material submission approval.
label | 75304e44-4159-53f3-9435-58d198c06a7b |  | note | Reference Documents - Cl16.5.6.1 & 16.6.2.2 & Tender Clarificatio ns #36
label | 549db1d7-fd4a-5eab-b6d1-07156f91fe49 |  | note | Inspection/Test Method - Document Review
label | eb1080aa-021d-5be6-b979-d353ecb13764 |  | note | Record of conformity - Aconex
label | 1ed1078f-fff6-57f8-b1e1-0cf5460b2dd8 |  | note | HP
label | 42d9471f-bd13-5359-b02c-cf38eb141023 |  | note | Responsibility - Project/Site Engineer, Beca
date | be559595-6804-5b57-ac83-af45fe1f80c8 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.4 - Backfill Material
label | fa1e2509-551b-53e2-b3e4-40cc2b17a126 |  | note | Frequency - Prior to commencem ent of works
label | 00ce685d-1629-5606-af60-85e42324d169 |  | note | Acceptance Criteria - Backfill material to be 6% cement stabilised sand to pavement formation level. Material submission approval.
label | b7edf96b-f4dc-56ba-a385-62c46425914d |  | note | Reference Documents - Cl16.5.6 & 16.6.2.2
label | 1269190a-dcff-5390-9084-4e405c70093c |  | note | Inspection/Test Method - Document Review
label | f4389ac0-ef80-594f-bf52-856b6d8aa05b |  | note | Record of conformity - Aconex Ref
label | 62c05dc6-f5a7-5245-b8ba-0b49ce5d172c |  | note | HP
label | 1449f01c-c4aa-5c77-aa84-5af40b4e64e8 |  | note | Responsibility - Project/Site Engineer, Beca
date | affd4a93-a921-5aa2-8cd0-44c441e6648d |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 3.0 - Stormwater Delivery
checkpoint-status |  |  | checkpoint | 3.1 - RCP Delivery
label | 88e5903e-8133-58e3-8e64-8e8887c3b17a |  | note | Frequency - Each Delivery
label | 9ab65ed4-0c52-5684-b951-353241be59b1 |  | note | Acceptance Criteria - Drainage pipes supplied and delivered as per approved Material submission. Manufacturer’s conformance report.
label | 041fa456-d7d6-5468-88a3-8afbf07b794a |  | note | Reference Documents - CL16.6.1 & AS4058
label | 325517ec-3131-5c6c-8485-ad1ddfe7f2ff |  | note | Inspection/Test Method - Verify
label | 4f86dc35-1ead-595a-963f-52d63f59fb27 |  | note | Record of conformity - Order Acceptance Form
label | 6c5cabb9-9f3b-5c37-b5c0-8304d309bcb3 |  | note | IP
label | 5f4e3bae-bc6b-59ba-969b-1387a4915c0c |  | note | Responsibility - Project/Site Engineer
date | fdf5360e-5800-577c-ad9f-ffc483d77ba0 |  | date | Date Completed:
checkpoint-group |  |  | section | 4.0 - Construction Activities
checkpoint-status |  |  | checkpoint | 4.1 - Survey Setout
label | 184b7804-94df-5c10-9503-064b7e236985 |  | note | Frequency - Prior to construction and each lot
label | 74e80b21-7b41-5c14-8fd1-0aaea06ed169 |  | note | Acceptance Criteria - Set out the stormwater drainage as shown on the Drawings to identify the locations, lengths and levels at outlets and inlets of pipes. This constitutes a Hold Point.
label | c997444a-d4ec-5293-9985-137593984628 |  | note | Reference Documents - Cl16.7.1
label | 45c2e80c-419c-5521-b8b4-d3401d87004b |  | note | Inspection/Test Method - Survey
label | f12f3715-d50d-5ab2-ae65-f56d39c25ae4 |  | note | Record of conformity - ITP Signed
label | 572ef53e-e8d6-50be-be91-ee3ee56e43f0 |  | note | HP
label | 39a0f67d-1725-5c40-9a71-dcb48f857a75 |  | note | Responsibility - Project/Site Engineer, Beca
date | 54ba654f-6272-5c0d-b9e1-ea03ebe60ed6 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.2 - Excavation
label | ae9b32ec-7fff-5d0a-9424-24163091f7a9 |  | note | Frequency - Each Lot
label | 4d6accd7-8604-53a9-ba80-22e6de486899 |  | note | Acceptance Criteria - All excavation to be performed to the minimum depths, widths and batter slopes as shown on the Drawings, regardless of the type of material.
label | 923600d7-e22b-5c6b-b9b3-98e96bec5038 |  | note | ○ Trench excavation is to commence at the downstream end, where practical.
label | c06bac9c-d541-57f4-9632-d0d3b38d1659 |  | note | ○ The width of trench to be such that the horizontal clearance from the outside of the pipe to wall of the trench to be minimum 300mm when under the runway and taxiway graded strip. Trench width outside of the runway and taxiway graded strip to be the greater of 150mm and D/6.
label | f20b6792-e317-56ec-9aab-88b5226f314c |  | note | ○ Subgrade Inspection to constitute a Hold Point.
label | 107547f8-aa65-500c-ae0e-13c46097e260 |  | note | Reference Documents - Cl16.8.1 & Cl16.6.2.2
label | b4c9308b-6d7f-54c9-bb86-94b073803c26 |  | note | Inspection/Test Method - Verify
label | e4767b4c-5011-58e6-aed5-79760c673c48 |  | note | Record of conformity - ITP Signed
label | 2ed83b9e-e250-51d5-9d5f-c97d45d2ec14 |  | note | HP
label | 68cabd5c-0e9e-5d91-acd3-bdee66617bbb |  | note | Responsibility - Project/Site Engineer Beca
date | a9d66231-9287-5067-8242-cbb0f31407c8 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.3 - Site Dewatering
label | e99776f6-6cf4-5503-9c98-dd1a53bdacac |  | note | Frequency - Each Lot
label | 389dad6e-d921-5c6e-84c1-f0e86313a748 |  | note | Acceptance Criteria - Excavations are to be kept free from water during construction and backfilling and provide pumps, well-points or other equipment as necessary.
label | b278c28b-7740-546c-9834-724a125c10a8 |  | note | ○ Any temporary works to be designed such that flooding upstream of the diversion does not occur. This constitutes a Hold Point.
label | c55d97ae-880c-5161-913e-dea6114660c2 |  | note | Reference Documents - Cl16.8.4
label | da00b571-a482-5590-8ee3-bbb311c60c04 |  | note | Inspection/Test Method - Site Inspection
label | 93d02277-da10-5973-8a27-3ffba730c5a5 |  | note | Record of conformity - Aconex Ref
label | a7d77778-30f4-570c-a3f4-92e9ce0195a3 |  | note | HP
label | c829d6c5-3da0-555f-99f8-f98c7d2adf74 |  | note | Responsibility - Project/Site Engineer, Beca
date | 8e733820-540c-5f3f-ba59-1d720e847f55 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.4 - Confirm Ground Conditions
label | c24d7f4c-211d-512c-8f62-fb8c74c5f909 |  | note | Frequency - Each Drainage Line
label | 1f1e2149-09a6-5a8a-bf8e-05bcf9343e0e |  | note | Acceptance Criteria - 1 x DCP test to be undertaken per drainage line to confirm ground conditions.
label | 03f1408a-fcfa-59d9-9794-c463a54760c7 |  | note | ○ Contractor to notify the Contract Administrator of any area of the foundation which contains material that is inadequate to support the proposed drainage structure.
label | 21488094-6570-5bb8-b7d2-27530887acab |  | note | ○ Inadequate material is deemed to have a bearing pressure less than 130kPa, equivalent to 4 DCP blows per 100mm, per note 4 on drawing ZULU-BECA-012-DWG-07102.
label | 242cba19-a3d8-5f42-88f9-69b17170d46f |  | note | ○ Inadequate foundation material is to be replaced with a layer of coarse crushed aggregate compacted to 95% relative standard compaction to AS1289 Section 5.5.1 over a geotextile Bidim A29 or approved equivalent.
label | a504a46e-b0eb-5c9d-97d2-012af669a2a0 |  | note | Reference Documents - Cl16.8.2 & Tender Clarificatio n 179
label | b45513b3-79a1-56a5-ad23-95b269d572e3 |  | note | Inspection/Test Method - Site Inspection
label | 920754ad-5496-5649-ac23-cc159d334d41 |  | note | Record of conformity - DCP, Test Results
label | 19a4ccca-6f42-515d-a026-65b358677d48 |  | note | TP
label | e0837cd8-3bb2-5877-86de-a5278106923e |  | note | Responsibility - Project/Site Engineer/Beca
date | a252e786-e6c8-54d0-8b34-75422fb024b4 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.5 - Bedding
label | 61b37c59-fb70-5d0e-a698-20adcac2ec80 |  | note | Frequency - Each Lot
label | af9fe81b-be0f-51af-9fc1-0aa0674506f3 |  | note | Acceptance Criteria - Bedding material/ subgrade to be prepared for laying the pipes. Pipe support cradles to be placed on firm bedding. This constitutes a Witness Point.
label | a494ec9f-64b2-5c1a-adbb-3d56b1681edc |  | note | Reference Documents - Cl.16.6.2.1
label | 3dbef3ef-2cbd-5041-8907-f8b8307af3a2 |  | note | Inspection/Test Method - Visual Inspection
label | 1956b3b1-4e04-5e3e-9732-44247b2e39cf |  | note | Record of conformity - ITP Signed
label | b97739b7-6d89-55a2-b679-4865132d3009 |  | note | WP
label | 092f1bf4-ab52-5aea-8233-0f976053f229 |  | note | Responsibility - Project/Site Engineer, Beca
date | d2238a42-f78c-584c-9962-043e884ad5b2 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.6 - Laying of Pipes (Sample)
label | b0f015fc-6552-5b29-bc8d-4109aaefe0fa |  | note | Frequency - First Lot
label | fdcea21a-b0f1-5a9e-9488-f4881b37681d |  | note | Acceptance Criteria - Initial sample 20m length of concrete pipeline to be laid and approved by the Contract Administrator for line and level before continuing construction of pipe network, Hold Point.
label | 8154e474-aae9-522a-bb86-a36adaf49a47 |  | note | Reference Documents - Cl.16.9.1.6
label | ff430c75-267d-5dc4-9bb9-27ba336032d5 |  | note | Inspection/Test Method - Verify & Visual Inspection
label | c912703c-040e-512b-9f93-f947c2067b52 |  | note | Record of conformity - ITP Signed
label | 0a819ca1-a073-554e-b852-5981530c427d |  | note | HP
label | 45418fb0-ad6f-55e9-bb76-4c331754f30c |  | note | Responsibility - Project/Site Engineer, Beca
date | 364dcce2-0e59-5280-b67b-e0c39dfd3bbe |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.7 - Laying and Jointing of Pipes
label | 55ab6429-192d-55db-90d1-e22d55d14f86 |  | note | Frequency - Each Lot
label | 7ff6eaa5-759b-58da-bcda-b470e99c9620 |  | note | Acceptance Criteria - Concrete Pipes to be rigidly supported by approved steel pipe cradle during laying.
label | 1ab0c57c-d867-51c9-805d-1cfba53d82cb |  | note | ○ Pipes to be placed with spigot end facing downstream.
label | 6fe829fb-2d02-5890-ba73-92b42ff58f96 |  | note | ○ Pipes to be laid with the word ‘TOP’ and or lifting holes uppermost. Lifting holes to be plugged after installation.
label | 3f96e12c-a485-5858-aabe-f2cf56590f05 |  | note | ○ All Concrete Pipes to be checked and subject to the approval of the Contract Administrator prior to commencement of backfilling, Hold Point.
label | 2fcb497d-7650-53d4-a543-98138cafc299 |  | note | Reference Documents - Cl.16.9.1.6
label | eaf88d90-0d84-5b9d-9e63-fcd1e3dd790c |  | note | Inspection/Test Method - Verify & Visual Inspection
label | 4ad99015-63ff-5ef0-baa5-e0c2fe2c7d66 |  | note | Record of conformity - ITP Signed
label | 6a597174-ca65-5552-882a-99ff143fd83e |  | note | HP
label | c92309d5-ae3a-50f4-9998-027105030665 |  | note | Responsibility - Project/Site Engineer, Beca
date | e2eaa18f-509d-5079-a636-1319ae775611 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.8 - Survey
label | 19ba0200-7d70-5c1c-9869-0b767944f1c9 |  | note | Frequency - Each Lot
label | ba84b8bd-9cfc-5c75-8319-359bfbd60ead |  | note | Acceptance Criteria - The alignment, level and grade to be checked on the obvert of every third concrete pipe unit.
label | 051e0e72-b396-5bac-8001-2c429bd84e51 |  | note | Invert levels at the upstream and downstream ends to be submitted to the Contract Administrator for review.
label | 3bcbb87d-38bc-50b8-854c-b22cd0532cd9 |  | note | Deviation from Invert Level
label | 9cfa4cdb-4a32-599c-897b-a0be107b8529 |  | note | ○ Maximum deviation from design invert level to not exceed 20mm and not result in zero grade or reversal of grade in any length of concrete pipe.
label | b404e9c4-7ff7-5ee3-9781-a07bfd70a889 |  | note | ○ Where the design pipe grade is less than 1%, maximum deviation from pipe socket to pipe socket does not exceed 20 mm.
label | bf35ce05-4c92-599f-848f-79c69bdded2a |  | note | ○ Maximum deviation from design invert level between upstream and downstream structures to not exceed 20mm and not result in zero grade or reversal of grade in any length of concrete pipe.
label | 8ab47876-2624-553a-a091-f979dbe03713 |  | note | Deviation from Alignment
label | 8746020d-7933-5d0a-94d6-715b8f5b708e |  | note | ○ Maximum deviation of the concrete pipe from the alignment shown on the Drawings to not exceed 25mm.
label | 00bf8704-8b53-5f6d-90eb-dbeac1b3f060 |  | note | Reference Documents - Cl.16.7 & 16.9.1.6
label | 98e36215-0999-5d5f-b355-ee54b245c97c |  | note | Inspection/Test Method - Survey
label | 45d4783a-a78e-5de2-a1e9-a5aaae115305 |  | note | Record of conformity - Survey Report
label | e8c5c51b-7c73-5362-bbab-5bc699b81f75 |  | note | SCP
label | ec49249a-59ed-5f71-bd09-36378a6def97 |  | note | Responsibility - Project/Site Engineer
date | 29281e2a-c5e9-596e-a91c-3ba3578fbc68 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.9 - Backfill Materials
label | d330036d-185e-5e46-8366-c2c7f4b375fe |  | note | Frequency - Each Lot
label | c465880e-2673-5fe3-a924-adb7d7121a49 |  | note | Acceptance Criteria - RCP’s under Runway and Taxiway Graded Strip
label | 0ff8ca7d-6a9b-587d-82b3-ae0b80d2a9c6 |  | note | ○ 5MPa wet lean mix to 200mm above pipe obvert
label | b7a47116-f844-5054-8ea5-77a8929a72a8 |  | note | ○ 6% Cement Stabilised Sand to pavement formation level
label | 2b325fbd-334e-55c4-a31c-ad9693321040 |  | note | RCP’s outside Runway and Taxiway Graded Strip
label | 8e1d4e99-575a-5cb3-a0db-2ff00c22e48e |  | note | ○ 5MPa wet lean mix 150mm above pipe overt completed in stages
label | a2be7076-28f2-5a0b-989c-7dd7e1330b73 |  | note | ○ Site won material completed in 200mm loose layer thickness (maximum) to pavement formation level or 6% stabilised sand
label | be32f9d6-757b-5617-af9f-340f9192925c |  | note | Reference Documents - Cl.16.5.6 & IFC Drawings & Tender Clarificatio n #164
label | 599b4af8-1dfc-5861-8e5c-a43813aff579 |  | note | Inspection/Test Method - Verify and Site Inspection
label | c8ab4ca6-dd7b-503d-a5d1-861f531aca8e |  | note | Record of conformity - Delivery Docket and ITP Signed
label | 0d893b32-e969-5749-b54c-411d59d73362 |  | note | IP
label | ada9dd1b-ddca-5e6e-b385-6d121df1925c |  | note | Responsibility - Project/Site Engineer
date | 5b8512f3-b805-5670-9e2b-46b008eb4aa1 |  | date | Date Completed:
checkpoint-group |  |  | section | 5.0 - Testing and Inspection
checkpoint-status |  |  | checkpoint | 5.1 - Compaction Requirements (RCPs)
label | 20cf176f-a6b7-5c20-a15f-3a00128219f6 |  | note | Frequency - 1 test per lot.
label | 130a3c59-641f-510a-aa7a-32754c96dced |  | note | Acceptance Criteria - Concrete Backfill Under Runway and Taxiway Graded Strip
label | d7323c0b-d2a3-52ba-b3c3-bdbbc0c3869a |  | note | ○ 1 compressive strength test for each 50m3 of backfill
label | b81c3dbe-96d4-5cad-8aaa-3c074b3ed218 |  | note | ○ Concrete Backfill Outside Runway and Taxiway Graded Strip
label | 13116915-82ef-58ce-a250-2e687f1b84fa |  | note | ○ 1 compressive strength test for each 100m3 of backfill
label | 5b0edd3d-8dc9-5638-81b6-d2af923ddc36 |  | note | ○ Backfill Zone - Outside the Runway and Taxiway Graded Strip
label | 28818352-ac85-59f9-9890-d6dc2ad38044 |  | note | ○ Minimum RD of 95% SMDD (1 lot consists of every 50m3 for concrete backfill and every 2nd layer of backfill zone material.)
label | 50268ddf-4832-5a04-b762-7344556c95dc |  | note | Reference Documents - Cl.16.5.6.3 (c) & Cl.16.9.6
label | e4e7c828-7985-5b35-9867-0ed080422016 |  | note | Inspection/Test Method - Site Inspection
label | 7c2f5a42-9f8d-5f65-b4c2-8ab18d53ae71 |  | note | Record of conformity - Test Records
label | c98f2819-da3f-5a3b-9606-d21d1a15883d |  | note | TP
label | f5adbcf0-2707-52f6-844c-97e15c83e568 |  | note | Responsibility - Project/Site Engineer
date | 49e3653e-dbb4-598c-928a-a15de17bcc47 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 5.2 - Inspection of drainage lines
label | dc0e3d4b-5cd4-5d5d-a0ed-7e2dd2a289ab |  | note | Frequency - Prior to constructing pavement
label | 6dd1734b-9742-579c-9bb6-cb16e9c5a269 |  | note | Acceptance Criteria - CCTV inspection of RCPs required at the completion of the works. Submission of CCTV footage to the Contract Administrator for review is a Hold Point.
label | 65d7ac9b-b970-5c02-bb61-569d311577b3 |  | note | Reference Documents - Cl.16.10.1
label | 21589f61-502d-5693-b289-8a8c5369d97a |  | note | Inspection/Test Method - Verify
label | bd1cb358-993c-50bd-b162-888a5e2fe05e |  | note | Record of conformity - Aconex Ref
label | 5bfc6948-2c78-54c6-8b42-5e86765dbe38 |  | note | HP
label | 5125a29a-784c-58df-bca6-136d172fd69d |  | note | Responsibility - Project/Site Engineer, Beca
date | 0a750240-ecff-52c8-9832-f0ad5e348793 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | Final Inspection
label | 07843a40-ad75-597b-8d27-a2d33627f1bb |  | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
text | 74bea63c-2144-54cf-8d9c-2c5d0a5c32bb |  | textbox | Print Name:
text | ceef9121-eb7a-57ad-9b81-0ff6d16629d8 |  | textbox | Position:
date | 93d9e161-3a8c-5069-bbc8-466eab8fc03c |  | date | Work Completed On:
date | 4ad221ca-63b8-5fac-8d71-1d492ee82fa6 |  | date | Date:
checklist-sectioned |  |  | checklist | ITP028 - AGL Luminaires | itp |  |  |  | Yes | FH-ZU2-QU-ITP028 - AGL Luminaires - Rev 0 | ad747c49-f87d-4844-8e27-1928126c7091
checkpoint-group |  |  | section | 1.0 - Preliminary Works
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | 45188b90-c074-5b1d-933f-d973b6a7f558 |  | note | Frequency - Prior to commencing any activity
label | b4f990cd-8578-5d96-b3ec-83ed290b5675 |  | note | Acceptance Criteria - Ensure that all employees and subcontractors are using the latest and complete set of drawings
label | 299c6b6f-9b56-5f03-8b17-543b3b8a1192 |  | note | Reference Documents - IFC Drawings
label | e53cc3ec-5edf-56f5-9d11-7b62eec7584d |  | note | Inspection/Test Method - Verify
label | 671b36d7-a162-5f85-9fcf-b3978a19d032 |  | note | Record of conformity - Drawings
label | 17d1534d-25a1-5a61-8792-1f0a8ae1e240 |  | note | IP
label | 4c3bd523-baa2-53fa-8059-055b7670f080 |  | note | Responsibility - Project Engineer
date | 333d67bc-00bf-5033-a1b7-f3e716df09a2 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 49a231bf-b906-5649-bf3c-7602b4a869c8 |  | note | Frequency - Prior to commencing any activities
label | f3c6d51f-525d-550f-83f6-b60c9bcb732a |  | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
label | 66750f64-167b-5fa4-aae7-25f6c378f926 |  | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | 6dce2d8b-8923-5823-a91a-f5e089f904f0 |  | note | Inspection/Test Method - Verify
label | 500eaaee-8bde-5f1b-966a-38743a017751 |  | note | Record of conformity - Site and office Inspection
label | 4bd58ebc-3ba1-5dce-a282-03a3d186caaa |  | note | HP*
label | 22feba67-2016-5e32-ae33-d943c811a5d8 |  | note | Responsibility - Project Engineer / Site Supervisor
date | eac8d38e-8da9-5dc3-8888-314fdd3c8d3a |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Material/Equipment Approvals
label | 8d05f7a0-e127-552b-a463-aad00aa342e8 |  | note | Frequency - Prior to start
label | a465ca3e-6e36-571c-bc6c-e71344bec96f |  | note | Acceptance Criteria - All materials shall be proven to meet contractual requirements prior to acceptance.
label | 562f6d2e-dbd2-5b6f-86d4-780797469bf7 |  | note | – MAGS shall be from ATG Airfield guidance signs range
label | 08bd2925-2923-5dca-977b-9d2bc2c266d7 |  | note | – Taxiway centre lights shall be from the ADB Safegate range only
label | 18d0791e-a17c-504d-8921-d97d47279cf7 |  | note | – Runway guard lights shall be from ADB Safegate only.
label | 31ded2f8-921a-5895-b2c5-31eb083b4fa7 |  | note | – Intermediate hold position lights shall be from the ADB Safegate range only
label | e552258d-32c0-5eda-89fc-51e6a30c1347 |  | note | – Stop Bar Lights shall be from the ADB Safegate
label | 31f33bcb-3aab-534a-b029-c82040f40cb2 |  | note | – IWDI shall be from ALS
label | f80f1b4b-2b81-5628-a6ed-c210d1438813 |  | note | ○ Any deviation from the above suppliers shall be submitted to the Contract Administrator for approval prior to ordering.
label | 9d8a0bab-ea20-50c5-bb75-2f7831983538 |  | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl 2.3
label | 894313fb-1739-57be-b4ad-edca655ac05c |  | note | Inspection/Test Method - Verify
label | 7fb7a331-7a85-5dfb-95a7-fb9873d496d9 |  | note | Record of conformity - Aconex reference(s)
label | 77e93085-ef06-552a-a990-94853866273e |  | note | HP*
label | 540f394b-9d7a-5bbe-9edf-4818ea0a711f |  | note | Responsibility - Project Engineer
date | 1a8633b4-f85e-525e-b651-da0a15e83891 |  | date | Date Completed:
checkpoint-group |  |  | section | 2.0 - Installation of AGL Base
checkpoint-status |  |  | checkpoint | 2.1 - MAG Sign Base
label | 8e349d1b-1bd6-50b3-97b5-82616a758887 |  | note | Frequency - Each lot
label | 77c7602b-7768-5d4b-b8ba-0bfd5e23d21f |  | note | Acceptance Criteria - Position of rectangular base to be as per set out coordinated listed in MAGS schedules.
label | f0168d23-ccf7-58cb-97b7-9eb27e995fe5 |  | note | ○ 150mm thick class 2 crushed rock base layer compacted to 98% STD on prepared subgrade
label | 7e3fcfbe-c2e2-5f7f-9689-cd8b71ecd803 |  | note | ○ 50mm blinding concrete between subgrade and foundation
label | 7651e9d8-adb7-5e47-ba8a-92dc5f4bf4f1 |  | note | ○ Slab thickness to be 300mm for all
label | 183861dc-50ae-536d-b4bf-846c62345ae1 |  | note | ○ H<900mm signs (signage outside this range will require additional design)
label | 23661912-f6e8-5336-b1f0-265499c73132 |  | note | ○ N12-200 top and bottom reinforcing bars with minimum 50mm cover from edge of concrete.
label | e2dfd7a8-b615-55fc-9556-2df707cb1b01 |  | note | ○ Sign mounting brackets and frangible coupling as per manufacturers guidelines
label | 1df4bf19-d3f5-5727-b29b-7f4a6234fa56 |  | note | Reference Documents - ZULU-BECA-023- DWG-07502
label | a91f27f6-d54c-5bb1-9036-064b23ff65f4 |  | note | Inspection/Test Method - Visual Inspection
label | 29653f16-aedf-5ca8-8a7b-003a4ec188b9 |  | note | Record of conformity - This ITP signed, Avionics Installation of New MAG Slab and Sign checklist
label | 430458b3-cd5c-5e8d-a358-a05728f4b03d |  | note | IP
label | d4bc5bd7-cdb7-5f5a-8a03-dd72177ece69 |  | note | Responsibility - Project Engineer
date | 84b0c95d-b5e4-5ca4-8d09-bbd3efef8808 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Inset Luminaire Base
label | c9fefc86-fb33-598f-9cf3-ffafb2d464de |  | note | Frequency - Each lot
label | 86aa408b-bef2-549b-96fa-693e30b89e98 |  | note | Acceptance Criteria - Installed and backfilled in accordance with drawings.
label | 0016d5ae-6a22-5f76-99fe-a7e176ced792 |  | note | ○ Reinstatement in Flexible Pavement
label | 7fbd9ce3-1dac-5924-bc44-9f30e018683e |  | note | – 500mm deep circular concrete block (500mm diameter for 8” cans, 600mm diameter for 12” cans).
label | 34c04169-a21a-5f8e-a050-5d91cb926993 |  | note | – Core depth and pavement embedment for can as per can/fitting manufacturers recommendation.
label | c988ca6e-96cb-586f-92d0-d6ee7d2a9b58 |  | note | – Epoxy sealant as per can/fitting manufacturer’s specifications
label | ae510fee-86ad-52e4-a953-f4ba9d67caeb |  | note | – DOWSIL 890SL to gap between AGL can and pavement.
label | 89cb608f-5fee-5d0b-8c5e-1578de19108d |  | note | ○ Deep Can Installation for Rigid Pavement
label | b37bb9e9-ff75-55c6-b20f-4f8141806041 |  | note | – Concrete encasement for electrical conduit shall have 75mm minimum cover
label | 575822fd-0abb-54c9-9bb9-866bd255a723 |  | note | – 700mm diameter concrete foundation
label | 6da2a0a0-12d2-5eda-bbf8-ff872350e9f3 |  | note | – Minimum 200mm from bottom of can to bottom of foundation
label | b280ff3b-b128-5e99-beec-12afba8b6cf5 |  | note | – Concrete for deep base can foundation to be strength grade N32
label | d889ca9a-0b5e-5c73-bb8b-39b4675a0191 |  | note | – N12 reinforcement cage to be installed as per AGL details
label | 46a6b6b3-aab9-5548-9e65-4f479595e741 |  | note | – Epoxy to manufacturers specifications
label | 1067e53d-7805-5800-8cfc-ecc481fea930 |  | note | Reference Documents - ZULU- BECA-024- DWG- 07501, ZULU- BECA-024- DWG- 07506-8
label | 7f1af5e5-f78b-5ed2-acfc-4aed1f8d040a |  | note | Inspection/Test Method - Visual Inspection
label | f86b00a6-37d4-5197-aca2-a17c6a2edaa7 |  | note | Record of conformity - This ITP signed, Avionics Shallow Canister Installation checklist / Avionics Base Canister Installation checklist / Avionics Top Canister Installation checklist
label | e37077d5-62af-5cc9-a2c0-5f08212504ec |  | note | IP
label | 1c0618a2-e819-58b7-9f59-98d8d1093438 |  | note | Responsibility - Project Engineer
date | a6b7a370-6749-53f6-b6f3-77b9a8057de9 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Elevated Luminaire Base
label | 91741421-2a09-5d4d-8f25-f6e6ae4cc3d9 |  | note | Frequency - Each lot
label | 8bb92b89-5fc7-524a-8f60-e820635f4114 |  | note | Acceptance Criteria - Installed and backfilled in accordance with drawings.
label | 0d9fc6d0-1f1b-5948-a2be-680d095f1e4a |  | note | ○ One-piece L867 can to be installed
label | a39e6bc8-1f35-548a-9a48-2c6bf6b22f1a |  | note | ○ Min 500mm cover from finished surface to top of conduit
label | 37acdfea-8655-57fa-9d32-cd9cdb090adf |  | note | ○ Can to be fitted with frangible coupling and FAA type/secondary socket retaining arrangement plug and socket
label | 114d8185-5a73-5a1e-a953-0b69889cfe1c |  | note | ○ Foundation and reinforcement installation to match Deep Can Installation for Rigid Pavement
label | b1e98ab7-5e0e-5338-a187-8e051f7ba3a6 |  | note | Reference Documents - ZULU- BECA-024- DWG- 07507
label | 55777f42-8bdb-5ceb-aac3-6c655a8d9d3c |  | note | Inspection/Test Method - Visual Inspection
label | e0eb1772-1af5-576b-afff-723128b33379 |  | note | Record of conformity - This ITP signed, Avionics Base Canister Installation checklist
label | 546bfc35-6a83-593f-abc0-3e47d80c4c6e |  | note | IP
label | 9afe4ad0-9114-575c-a895-b4db2cd392cf |  | note | Responsibility - Project Engineer / Site Supervisor
date | 5baa4b44-14c0-5909-8952-4ded195017b1 |  | date | Date Completed:
checkpoint-group |  |  | section | 3.0 - Installation of AGL Luminaires
checkpoint-status |  |  | checkpoint | 3.1 - Setting out for Airfield Luminaires
label | 7dabc84b-7473-566d-ad84-49dcd215b3bc |  | note | Frequency - Each Lot
label | 89492ec1-9142-5984-8d91-49df3473eb94 |  | note | Acceptance Criteria - The Contractor shall survey the proposed light locations in conjunction with the new and existing linemarking to set out the proposed lights. A schedule of the proposed lights shall be produced by the
label | e63ca483-9afd-5a05-9c2b-eb3a490c18c3 |  | note | ○ Contractor with the following details:
label | 2847ec91-22b3-5aee-8192-b9092e83998e |  | note | – Surveyed location, with coordinates to the APAM database system.
label | b29375d1-e157-535a-9951-a6931ce25321 |  | note | – Orientation including any additional deviation angle from any tangents.
label | c7254d60-12ff-5604-8f76-e09c899af63b |  | note | – Colour
label | 7eb35854-ace2-54b7-954f-7534716f0bcc |  | note | – Circuitry
label | 2b6e95f2-6449-55fa-8e95-2be27b061345 |  | note | – Labelling
label | f05d9a96-37b2-5149-96f6-6b051944ed23 |  | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl 5.4
label | aac40af6-01a9-504e-863c-2dda04da28f7 |  | note | Inspection/Test Method - Verify
label | 21bdf6fd-05d1-5854-b89e-e80ff249536d |  | note | Record of conformity - Aconex reference
label | e5d04dd9-9143-571d-a011-e16c3febb70f |  | note | HP
label | cb6721d8-22cf-525e-8437-8fbe7e2ae371 |  | note | Responsibility - Project Engineer / Beca
date | d9bd0746-d039-5bfb-9c88-b7e37e5852a8 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - Elevated Light Installation
label | 6634e24c-fa71-50e4-bbbd-131b2d8d1b1e |  | note | Frequency - Each lot
label | a8723c1b-41ca-55ef-b111-953171308756 |  | note | Acceptance Criteria - Components of elevated lights shall:
label | b281ca7d-79a1-500a-b912-2e31e55ee884 |  | note | ○ Be less than 360mm above the pavement level including the frangible coupling.
label | e07aa034-acad-5b46-b2fa-7c323d4ccfd0 |  | note | ○ Be suitable for installation on a threaded connection when installed.
label | 95cabdfa-bacf-5de4-8cf1-6bac6fca7bfe |  | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl 4.4.4.1
label | 21431ab1-83cd-54e4-a019-03019d4a66cc |  | note | Inspection/Test Method - Verify
label | 938087ec-a520-5f95-aaee-67fac4652ea1 |  | note | Record of conformity - This ITP signed
label | ea96216a-8433-5adb-b895-a7583eb80382 |  | note | IP
label | f8803a94-01f1-565b-b452-4deea6f15dc4 |  | note | Responsibility - Project Engineer
date | cd0d12c0-a29a-5582-869b-b2d55a39313d |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.3 - Inset Light Installation
label | d81b1680-d50d-5752-84bc-e62945616e39 |  | note | Frequency - Each lot
label | 2d9ab315-0011-5027-ac54-be1f606f0063 |  | note | Acceptance Criteria - Components of inset lights shall:
label | bdf7c9ac-0ca2-582d-a8d9-0743c3a3f55d |  | note | ○ Be less than 13mm height above the surrounding surface.
label | bbdcd9f6-5624-50c0-b7bf-27e2f2dd3c88 |  | note | ○ Have a slope of surface of the unit to be less than 20º (not including any recesses).
label | 57d42f17-7d7c-5233-9f50-89278ecbe79b |  | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl 4.4.4.3
label | c9677232-f1f5-5010-99af-2e6fe9b3744a |  | note | Inspection/Test Method - Verify
label | efe18c69-f0da-5d18-b64c-43b3aad8cd8a |  | note | Record of conformity - This signed ITP, ADBSG Installation of Inset Light Fittings checklist
label | 574b6650-279f-55b7-bd88-b04738dab085 |  | note | IP
label | b893dbcc-9cfb-5c1e-8a63-f2c01a5c5951 |  | note | Responsibility - Project Engineer
date | 1b1e0b53-422e-549e-a8af-20faff0a8565 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.4 - Series Isolation transformer
label | 1c296be2-5acb-5ed5-bcb0-d333afd9db29 |  | note | Frequency - Each lot
label | 2c4e033d-9187-5c7e-b634-a3f2f6dae415 |  | note | Acceptance Criteria - SITs shall be installed in specified deep base cans or pits.
label | c5341822-d986-5f3c-b7a2-6827c4204edb |  | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl 4.3
label | e476a62b-2bff-52e1-bd7d-8e57c13a6f50 |  | note | Inspection/Test Method - Verify
label | a91e10c4-b9d1-5af1-ada5-39662dedc2b2 |  | note | Record of conformity - This ITP signed, ADBSG Installation of Series Isolating Transformer (SIT)
label | d9bcc36c-3668-5912-a49e-dbff975e172b |  | note | IP
label | 8bf9df93-7733-5de9-a112-d8687d18751b |  | note | Responsibility - Project Engineer
date | 6c6a0538-172a-502b-a3e4-69bc51a421c1 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.5 - Luminaire Circuit
label | 05b6f2a7-a7dc-5eff-a543-3754ee19fb93 |  | note | Frequency - Each lot
label | 4b6370ce-dbb2-5181-be3b-d92419850e2f |  | note | Acceptance Criteria - Each luminaire fitting shall be installed on the appropriate circuit as specified in the AGL schedule.
label | 579ea467-d8ab-533d-8fe8-ec47731b48f7 |  | note | Reference Documents - ZULU- BECA-024- DWG- 09001-16
label | d1dd4d91-1d2d-5954-83f2-c261daed6b22 |  | note | Inspection/Test Method - Verify
label | fa828051-8ae3-5637-9702-d02e19383558 |  | note | Record of conformity - This ITP signed, As-Built Documentation
label | 02336182-9a95-5c91-b600-0af6f46bc29d |  | note | IP
label | df27e8e1-a0f3-5808-becd-da625b46453d |  | note | Responsibility - Project Engineer
date | c3b166a8-7002-5b1d-8602-6b8a1867a1c3 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.7 - MAG Sign Face
label | 5f7fd4cc-8423-571c-b0a9-8ba5657e1aca |  | note | Frequency - Each lot
label | 3f25cac7-2d33-5fc6-896e-d5a4387caf98 |  | note | Acceptance Criteria - The proposed location for MAGS are to be as indicated on the Drawings.
label | a16b5662-f1e1-578d-a010-c38f26be8719 |  | note | ○ All MAGS that are to be mounted on frangible couplings. The provision of internal illumination of the MAGS shall be as detailed on the Drawings.
label | ac84bd72-ccf1-5595-9f88-7fe06b4416ae |  | note | ○ Where multiple panels are required, the inscription shall appear continuous over any joint and shall only include a bar if the bar is part of the inscription.
label | c64ce33e-07c7-545a-afdd-89a40fe6fed3 |  | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl 4.7.1
label | 90895ab7-525e-5101-8918-34b2691ec5ea |  | note | Inspection/Test Method - Verify
label | a1f7e9c6-a90d-5021-afb4-ff95ba288e06 |  | note | Record of conformity - This ITP signed, Avionics Installation of New MAG Slab and Sign checklist
label | 2318e7d0-a559-587b-9d8f-2b0c7e3196ad |  | note | IP
label | ea29714b-2030-5ae1-b9a8-e54c3866a56c |  | note | Responsibility - Project Engineer
date | d6c4a89b-100a-555d-b027-5a7ff186e44e |  | date | Date Completed:
checkpoint-group |  |  | section | 4.0 - Post Construction
checkpoint-status |  |  | checkpoint | 4.1 - As-Built
label | 24087dbc-7d7d-5b84-854a-7245a0eb7f52 |  | note | Frequency - Each lot
label | 79224cf8-f549-57f3-8a61-f2fb462f4a4d |  | note | Acceptance Criteria - Submission of surveyed luminaire position to superintendent prior to practical completion
label | 27c2c045-cc56-55ef-a950-7533a2712d3f |  | note | Reference Documents - WP-001-09
label | 7cba3ea0-4c37-55d1-86bb-c4eee89a5b12 |  | note | Inspection/Test Method - Verify
label | 3b3bf420-040f-5adb-b1db-a0c73e5c9319 |  | note | Record of conformity - SCP
label | b264a672-d2eb-5971-809d-2fd936948756 |  | note | IP
label | 51a06999-ce69-56aa-b53d-4f4f34967e6d |  | note | Responsibility - Project Engineer
date | 063e9fee-724f-53d4-b647-5e48c8277771 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | bc4c7bc9-4c72-5dd2-a326-bfc57e7f481c |  | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
text | ef55b6e3-5391-598e-967d-c8fffb506eb4 |  | textbox | Print Name:
text | 923d6766-91c8-53cc-aad0-617794df8088 |  | textbox | Position:
date | c18b8729-d183-5b0f-beee-88c9e001818e |  | date | Work Completed On:
date | 603d6059-7f3a-56dc-91de-d46bfdaa7119 |  | date | Date:
checklist-sectioned |  |  | checklist | Order Acceptance Certificate - Lot: |  |  |  |  | Yes | Order Acceptance Certificate | d9fa5533-4678-44db-ad39-7d61dd04ee01
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Order Acceptance Certificate -- Details:
text | 12a7c1e5-72a9-5807-befc-b9efc424750a |  | textbox | Subcontractor (full name of Subcontractor, ABN, Subcontractor's ACN and ABN)
text | 5af93389-f25c-5d80-b77f-39a4818315e4 |  | textbox | Order No.:
text | 4133d23c-5515-5362-b530-be47a6518f52 |  | textbox | Delivery Site/Location:
date | cd8c425f-9f53-5c2d-ad08-4b2c599e8049 |  | date | Date on which materials delivered:
select | c0097141-a841-55bf-8ae3-c53f2873beca |  | dropdown | Inspecting Engineer: | Abdallah Saidan, Abdul Saad, Alex Soo, Angela Julianto, Brad Carroll, Chris Cappelleri, Cristin Swar, Fadi Hanna, Faiyaaz Ahmed, Giuliano Follacchio, Jamal Khodr, Jasman Singh, Jihad Barbar, John Kakoliris, Jonathon Rock, Jordan Nicolaou, Marianne Sales, Michael Natalizio, Owen Tieu, Patrick Croagh, Tirrell Slaney
text | 45e3f212-8d1c-543b-9a35-0358266c0e47 |  | textbox | Inspecting Engineer (if not included above)
text | 4966c6cb-3e3d-5752-bb82-0a115d0656d6 |  | textbox | Subcontractor's delivery personnel (full name)
text | 6b811dd6-6dc3-548c-b57f-0364a98d27a7 |  | textbox | Delivery vehicle registration number
checkpoint-status |  |  | checkpoint | The Subcontractor has checked all Materials included in this delivery and is satisfied that all of the Materials comply with the Subcontract.
checkpoint-group |  |  | section | Packaging Inspection
checkpoint-status |  |  | checkpoint | Inspection Result ID:
button | 5af37914-7f8a-57ac-b8eb-af8f32f81e30 |  | button | Special Storage/ Handling Requirements? | Yes, No, N/A
text | d472a224-2992-568f-9627-b4deeee5931a |  | textbox | If yes, provide details
label | 5c6b6948-bc83-52c5-9b75-ea98613e1ad4 |  | note | The following is for completion by Fulton Hogan
button | 6d4bcd5e-6127-574d-a9b9-fb512def9611 |  | button | Confirmation of receipt of Units delivered. [Subcontractor does not complete. Contractor will initial on receipt.] | Yes, No, N/A
button | 70fd54d0-3acd-5341-b686-5705578dd7c0 |  | button | QA/Compliance Docs Delivered? | Yes, No, N/A
button | 49ff98bb-f0fa-5156-a58c-e12bcb2510f0 |  | button | Defective? | Yes, No, N/A
checkpoint-status |  |  | checkpoint | 1)
text | 14fbd31c-3ed8-50d5-8bdf-b1544e387fea |  | textbox | Item ID:
text | 2994839b-a721-5165-ac58-c135d99c2709 |  | textbox | Item description:
text | 65816c8d-705e-5e01-a0e3-31d06a01fe72 |  | textbox | Units ordered:
text | 2a8a3e58-1dff-56b1-9a34-9c5d3d05d8c9 |  | textbox | Units delivered:
text | d727198e-a11c-508d-b0e2-c3d4c1563815 |  | textbox | Number Accepted
text | d0755175-ee3f-501a-a373-48d612f07c5b |  | textbox | Number Rejected
label | 111ddf99-8375-57e2-92b4-62eb39931b6b |  | note | Inspection Result ID (select below)
boolean | eb186f37-07fd-507f-a68b-4eba6d0d570c |  | tickbox | OK = Meets all criteria
boolean | d18323b2-c7d1-5115-a09c-544c7bdfcd3b |  | tickbox | QI = Quantity incorrect
boolean | 0d812c22-f0a3-5d0c-9055-d001df447d3f |  | tickbox | IN = Item incomplete
boolean | bd28b41a-6ae4-5899-b676-258553c470b5 |  | tickbox | MI = Make or type incorrect
boolean | aab47e5e-1a43-5442-b958-df4ebb9be7ee |  | tickbox | TD = Damaged in transit
boolean | 98d6ddf2-47e8-59a0-9158-0dbdfaa17086 |  | tickbox | NI = Not properly Identified
boolean | d6144275-4bd2-5780-83d0-a0e828e846d1 |  | tickbox | CD = Compliance docs not provided
checkpoint-status |  |  | checkpoint | 2)
text | bcb8a80c-62a2-5601-8016-580bbc87704f |  | textbox | Item ID:
text | 1b8dc746-448e-5455-895a-f55bcd8ebb83 |  | textbox | Item description:
text | 4c97d56b-02c8-5d15-b1b2-77fb99e0d5ec |  | textbox | Units ordered:
text | a7fc8070-6e1b-5dba-bf70-313ca170f523 |  | textbox | Units delivered:
text | 932ae001-ff39-554d-9551-288cb472e167 |  | textbox | Number Accepted
text | 415e27e9-065d-5622-b00d-a2681ed2da3d |  | textbox | Number Rejected
label | f9f13e5f-856f-534d-a759-79009afd7c7c |  | note | Inspection Result ID (select below)
boolean | 29b66bee-d998-50b8-bc4b-51bcc0a4b891 |  | tickbox | OK = Meets all criteria
boolean | 4df1d900-41f1-5892-9255-6196f48f45b2 |  | tickbox | QI = Quantity incorrect
boolean | b6316236-2594-55a7-8f43-05628dd24ba8 |  | tickbox | IN = Item incomplete
boolean | 0260be27-5d9c-5126-9cd6-2bdb101cfedc |  | tickbox | MI = Make or type incorrect
boolean | 99b072dd-aa0b-5134-90bb-cb8ce550164e |  | tickbox | TD = Damaged in transit
boolean | 53310f68-ca19-5463-a84e-fbb01226322e |  | tickbox | NI = Not properly Identified
boolean | 3d1740fb-d64a-5717-8671-52a78e10fb91 |  | tickbox | CD = Compliance docs not provided
checkpoint-status |  |  | checkpoint | 3)
text | 7d0b2e97-16e6-5457-98d3-76cd64b0f7e4 |  | textbox | Item ID:
text | eaca7272-0657-5d88-ba36-14ecc6e4f300 |  | textbox | Item description:
text | bfcf3a2f-2700-522c-82fe-c8b1bfd41064 |  | textbox | Units ordered:
text | c85741be-5e1d-508b-9596-988eabaa0f2a |  | textbox | Units delivered:
text | edd2e7e2-63ef-5942-ac19-b879a6054401 |  | textbox | Number Accepted
text | ba9cf8c6-51f0-5fea-a9af-e267a9c2954d |  | textbox | Number Rejected
label | 1a5019de-b026-5684-bb61-9054252a1b79 |  | note | Inspection Result ID (select below)
boolean | 18eb4d14-d9f2-5767-bd57-95ef30adb9af |  | tickbox | OK = Meets all criteria
boolean | a5db3abf-a7d9-5d87-ba79-115540460781 |  | tickbox | QI = Quantity incorrect
boolean | e3505139-cebb-5419-a051-7ef94dd7113c |  | tickbox | IN = Item incomplete
boolean | b2ff2970-0289-502b-bad3-211bbc4fd855 |  | tickbox | MI = Make or type incorrect
boolean | 592bbd0c-4513-567e-b6bd-330459126e7d |  | tickbox | TD = Damaged in transit
boolean | 9f04d024-b4de-5d63-9de0-e34bb90ecf2e |  | tickbox | NI = Not properly Identified
boolean | 4278a3d3-eb65-553f-b192-ad44788bbdf1 |  | tickbox | CD = Compliance docs not provided
checkpoint-status |  |  | checkpoint | 4)
text | 02030a4a-e9f9-5de5-b134-e3c68ff5647b |  | textbox | Item ID:
text | 0adef97f-9057-5939-ac0e-36f39d8591bf |  | textbox | Item description:
text | f1deff30-74cc-527b-97ac-ca8758e545bb |  | textbox | Units ordered:
text | bad31414-c790-55f1-94df-e9b3e7db8d0c |  | textbox | Units delivered:
text | 6126b4ab-c1a1-5e47-803d-d37b5714cefb |  | textbox | Number Accepted
text | 2608bb75-8749-5221-b1ae-e7e03b904cf1 |  | textbox | Number Rejected
label | cb797cad-1ab2-5fa4-93b8-5639b0145c17 |  | note | Inspection Result ID (select below)
boolean | 485a4c56-ea86-5699-a275-6085cba522d1 |  | tickbox | OK = Meets all criteria
boolean | 3657c271-31a4-5827-b9be-83ccb17cfea9 |  | tickbox | QI = Quantity incorrect
boolean | aea79501-99ea-5d7c-a344-23456988306a |  | tickbox | IN = Item incomplete
boolean | 375a4393-fb27-5712-85d2-a3d39c6bea58 |  | tickbox | MI = Make or type incorrect
boolean | 014225a6-fd62-55e4-a7fc-248b025fa0b5 |  | tickbox | TD = Damaged in transit
boolean | 9e770ae4-cb01-5510-8737-fa33711c1bfb |  | tickbox | NI = Not properly Identified
boolean | dabc3c4d-271a-52e4-848a-b6f31b0f5dd6 |  | tickbox | CD = Compliance docs not provided
checkpoint-status |  |  | checkpoint | 5)
text | ee3e5da8-de72-531e-95b5-9d20e807142c |  | textbox | Item ID:
text | 8e7052af-a398-5e46-92b7-a2e49a4d9b3d |  | textbox | Item description:
text | 89b51c1b-da9e-5489-8e93-95759094bd01 |  | textbox | Units ordered:
text | 839dbb10-e1dd-5507-befe-477e8984beed |  | textbox | Units delivered:
text | b255ed66-3db3-518b-9402-6788fc4751b1 |  | textbox | Number Accepted
text | 9ca98e0a-965c-5b4a-931b-555565640b79 |  | textbox | Number Rejected
label | 2b9365df-3a69-5e77-9670-c4c1643e71dd |  | note | Inspection Result ID (select below)
boolean | 83b4e2c3-6d8a-5719-a07a-3f29a40bd4c0 |  | tickbox | OK = Meets all criteria
boolean | 0f572fc2-39e3-5ccd-a238-48068a967c0f |  | tickbox | QI = Quantity incorrect
boolean | 1b0d93e3-fbf6-56d6-9ebd-234da000b0a4 |  | tickbox | IN = Item incomplete
boolean | 9d4ab8e8-64d7-51e9-bceb-3aa3845370a1 |  | tickbox | MI = Make or type incorrect
boolean | b81b70ef-1498-5b95-afa1-955a18d41376 |  | tickbox | TD = Damaged in transit
boolean | 880ad6fd-7a04-5537-8145-e9ec30b0af67 |  | tickbox | NI = Not properly Identified
boolean | 5947b083-7280-51a0-bbba-ef46a1b46c3d |  | tickbox | CD = Compliance docs not provided
checkpoint-status |  |  | checkpoint | 6)
text | f5213d94-b80a-58ad-9e02-f4c55d406424 |  | textbox | Item ID:
text | edd20faa-cb86-5256-bc0a-01f72d478ff4 |  | textbox | Item description:
text | 777534c3-f873-5c72-b8bc-84a8652d31c5 |  | textbox | Units ordered:
text | c70ed69f-7b0f-51a7-9ebc-8e8780ed4eba |  | textbox | Units delivered:
text | bf72f1f5-fd8a-5f81-bfa7-30ec85b2b7b4 |  | textbox | Number Accepted
text | c066d4e0-a8b8-55e3-80b1-95163a7f00d9 |  | textbox | Number Rejected
label | f4a433b9-bedb-535f-afb2-38b96236e638 |  | note | Inspection Result ID (select below)
boolean | 78f4fb22-5dd4-53c8-ae6f-45f0e5bbec26 |  | tickbox | OK = Meets all criteria
boolean | 76a89976-b7bb-58ec-9dd9-5273687c8bb7 |  | tickbox | QI = Quantity incorrect
boolean | e3057735-dba9-579a-883b-f54c31d4dda4 |  | tickbox | IN = Item incomplete
boolean | b1e39859-58b0-57c7-a46f-b8dcece44ae6 |  | tickbox | MI = Make or type incorrect
boolean | 317c7343-d44b-5e6f-ac4d-14777d996856 |  | tickbox | TD = Damaged in transit
boolean | 22d1c960-40b1-5717-a111-2733e94a093b |  | tickbox | NI = Not properly Identified
boolean | 5627b1ca-a2cb-569b-b8d7-4b4fdf5390e5 |  | tickbox | CD = Compliance docs not provided
checkpoint-status |  |  | checkpoint | 7)
text | 24420331-8897-5df8-8e20-28850ce6820b |  | textbox | Item ID:
text | 050f2298-60e1-597c-ba41-19f372d6f9ea |  | textbox | Item description:
text | 4aed13e8-5b70-5ac5-b063-27682e4b1e7d |  | textbox | Units ordered:
text | a8455a7c-3e34-5fe2-9484-44265dbc6270 |  | textbox | Units delivered:
text | c96e5370-3e8a-546d-b3ba-30efbbacacd3 |  | textbox | Number Accepted
text | 2ef35f51-cea1-59a0-a464-7b59d63adaef |  | textbox | Number Rejected
label | 8d6998f0-ae2a-550b-9a35-ce9a90bcd907 |  | note | Inspection Result ID (select below)
boolean | 38731218-084d-5300-8ed7-2fa488172541 |  | tickbox | OK = Meets all criteria
boolean | f5fab120-e143-55d9-98b3-47b141326437 |  | tickbox | QI = Quantity incorrect
boolean | 1bbc596b-6778-5be7-be40-a3679ec04117 |  | tickbox | IN = Item incomplete
boolean | 59d81aa0-cf54-5156-96b1-253b1feaf6aa |  | tickbox | MI = Make or type incorrect
boolean | a2040892-0694-53d0-bcd2-55ecc0661f89 |  | tickbox | TD = Damaged in transit
boolean | 5ff1772d-def4-5790-807b-814328b8894d |  | tickbox | NI = Not properly Identified
boolean | 4aee0408-6d70-5ad6-a317-4bbc96d33a65 |  | tickbox | CD = Compliance docs not provided
checkpoint-status |  |  | checkpoint | 8)
text | 0a389b74-9f90-525d-8b0c-2552b759cf12 |  | textbox | Item ID:
text | da5d972b-2633-569a-ac0d-39ab45185063 |  | textbox | Item description:
text | 5225212b-ed5d-5287-97df-f33b1afb8849 |  | textbox | Units ordered:
text | 93ccb08d-1a0e-5bbd-b3fe-401d00e9b93f |  | textbox | Units delivered:
text | efe49955-ccdf-5024-a811-8666f33136b1 |  | textbox | Number Accepted
text | ded9f1eb-3668-56ca-b5a9-a52244bb2ade |  | textbox | Number Rejected
label | ae08ee64-0f14-5936-97e7-b66bc37e6886 |  | note | Inspection Result ID (select below)
boolean | 369bd422-e8d4-5e79-93e2-fec34f9dcbe0 |  | tickbox | OK = Meets all criteria
boolean | 36c62b89-9687-5b3e-8bae-397801b4f57c |  | tickbox | QI = Quantity incorrect
boolean | db8728c7-e9ea-5d6b-b0e6-ebd0d5eb6d8d |  | tickbox | IN = Item incomplete
boolean | ed22784c-94c4-5299-b9ac-d91e57c69287 |  | tickbox | MI = Make or type incorrect
boolean | 5a8fff9f-6801-5421-98eb-2215df843cbe |  | tickbox | TD = Damaged in transit
boolean | 676893f2-c88c-51b8-80f3-69b2dc890cfc |  | tickbox | NI = Not properly Identified
boolean | 67c8e16c-c8f8-588a-9ee8-31eb20893fad |  | tickbox | CD = Compliance docs not provided
checkpoint-status |  |  | checkpoint | 9)
text | 65eae4e7-939c-5ce5-9db2-eece6a4a649f |  | textbox | Item ID:
text | 974acc2a-4b50-5eee-9e15-9ba65a782a7c |  | textbox | Item description:
text | 21e915b9-fedf-5b73-a47d-be5243581d53 |  | textbox | Units ordered:
text | 0cced952-00de-55ce-8584-6be8030a25ee |  | textbox | Units delivered:
text | f3a96a9e-67cf-55a6-8f0d-bf09c6d85ef8 |  | textbox | Number Accepted
text | d3a1489b-5278-579a-9a15-15c1cea2f994 |  | textbox | Number Rejected
label | f383bbb4-9354-50cb-b763-6b692204c157 |  | note | Inspection Result ID (select below)
boolean | 05656c8c-a056-5d75-971d-973831c209d5 |  | tickbox | OK = Meets all criteria
boolean | aee89344-f771-5ce8-8c50-075d95882fce |  | tickbox | QI = Quantity incorrect
boolean | 377a752a-da2e-5870-83e8-7d570544216a |  | tickbox | IN = Item incomplete
boolean | 8158ea5b-dcb3-5a4a-970a-029eebc1a66c |  | tickbox | MI = Make or type incorrect
boolean | 9fe0fffb-3708-50b7-a9ce-0792b5913c20 |  | tickbox | TD = Damaged in transit
boolean | f81eae3f-8b92-5308-9e64-456dbeb343cb |  | tickbox | NI = Not properly Identified
boolean | 6857182b-1b54-522a-a5d4-8dbdcedde131 |  | tickbox | CD = Compliance docs not provided
checkpoint-status |  |  | checkpoint | 10)
text | f31045c7-1532-5996-9539-a059c44e9143 |  | textbox | Item ID:
text | bf14bf6a-0c22-5298-acce-1b1e76efa58b |  | textbox | Item description:
text | 275633ff-23c0-509e-994c-a32a2affc4d8 |  | textbox | Units ordered:
text | f4f913e7-857f-587d-853a-582fc5c6cea6 |  | textbox | Units delivered:
text | 0ad7f80a-763c-56c2-a5d0-fccc379240e3 |  | textbox | Number Accepted
text | 728face4-b70a-51ba-9372-5306f854b124 |  | textbox | Number Rejected
label | 09e54c31-f69e-559c-9836-3041d059feb5 |  | note | Inspection Result ID (select below)
boolean | f83dc770-5925-5f78-8f97-99ada5109ef4 |  | tickbox | OK = Meets all criteria
boolean | 24966949-b70a-5c70-8b17-e0f2631cc6df |  | tickbox | QI = Quantity incorrect
boolean | 4f31970c-fe9c-5c41-b197-736cf33848ba |  | tickbox | IN = Item incomplete
boolean | 26817fea-ad8e-5d03-ab40-a2308c1e1b90 |  | tickbox | MI = Make or type incorrect
boolean | aa968b3c-f799-56e7-b410-ef29880b0530 |  | tickbox | TD = Damaged in transit
boolean | a7e94359-1c7f-51d6-b0c8-688f94b72d28 |  | tickbox | NI = Not properly Identified
boolean | 945ea484-67de-5837-a72f-5e3f7a05d714 |  | tickbox | CD = Compliance docs not provided
checkpoint-group |  |  | section | Sign Off
checkpoint-status |  |  | checkpoint | Accepted by Fulton Hogan
holdpoint |  |  | signoff | Sign Off
checklist-sectioned |  |  | checklist | ITP025 - AGL Conduit and Boring Installation | itp |  |  |  | Yes | FH-ZU2-QU-ITP025 - AGL Conduit and Boring Installation - Rev 0 | e5c4ed83-6e8c-4060-ab4e-866cf668ad0e
checkpoint-group |  |  | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | b8a32079-1aa5-57e6-8a66-15d046efe9a4 |  | note | Frequency - Prior to commencing activity
label | dca089ff-fabe-5dfd-9155-fd95e5e738e2 |  | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
label | dba1a5c0-d0de-5d6d-b571-cae043ee78fd |  | note | ○ Using the correct and complete set of drawings.
label | 99e63a8b-aa25-5791-87ed-2128adff683e |  | note | ○ All drawings are the latest revision.
label | 0d37360b-f68e-5e84-8b12-8e39c9daf073 |  | note | Reference Documents - Drawings / Aconex Register
label | e1eaf8d7-ca21-5f67-8a56-b4657842d17c |  | note | Inspection/Test Method - Verify
label | 8d9414de-68d1-5128-86de-09bf100caffa |  | note | Record of conformity - Drawings and drawing registers
label | cac2c81a-95d7-527f-ba64-e416799584f2 |  | note | HP*
label | 7f726786-8251-5e46-83af-455cd1302016 |  | note | Responsibility - Project Engineer
date | 10a06d2c-0727-5f35-9bdc-3e4672b3a79c |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 9e830bc9-6113-5cb4-9a34-eba9ba021b42 |  | note | Frequency - Prior to commencing activity
label | 9418b1c8-716b-5ea0-a719-ba1ccd42d304 |  | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
label | 81fa21ec-76e9-5833-816a-8d4f88d14f18 |  | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | 5b75c70f-9e38-5946-9d65-a6a3204df160 |  | note | Inspection/Test Method - Visual inspection
label | 1deda285-60ca-5351-b3d3-e42caadce55e |  | note | Record of conformity - This ITP signed
label | 3767b002-064d-5f2b-a08e-c974d9b21578 |  | note | HP*
label | 4cbb564b-8fa9-59a0-893a-1706d763fe3f |  | note | Responsibility - Project Engineer
date | 343fa595-a04c-5db6-b296-f79f8b91a9a9 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Definition of the work area (survey)
label | 2a01ebfc-039d-5ba5-a171-e3056faf5778 |  | note | Frequency - Prior to commencing activity
label | ff5b4170-c852-50d2-86d7-a1bfe1389ea8 |  | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Limits of excavation clearly defined.
label | 2360f750-b416-5fe2-bb88-558bdaeec326 |  | note | Reference Documents - Drawings
label | d84c98fa-fcb1-575a-a417-1f8ecf6ca0a3 |  | note | Inspection/Test Method - Visual inspection
label | 79ded8b4-2e16-52fe-b9f2-cb72048a09e9 |  | note | Record of conformity - This ITP signed
label | 3de3e26d-10d8-5785-bd23-f9c04341127d |  | note | HP*
label | bf9859db-19aa-5d27-9a66-8544815d825c |  | note | Responsibility - Project Engineer / Surveyor
date | b31fbb3b-c423-5d91-a5ab-4207c71c863d |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.4 - Check conduit compliance
label | ca75f7e2-9fe0-5872-8553-2e25ec68ebeb |  | note | Frequency - Prior to commencing activity
label | bda3bffd-140a-5c53-a9d5-ed07bf6460c2 |  | note | Acceptance Criteria - Ensure that uPVC conduits comply with AS 1477 or equivalent AS 2053. Shall be heavy duty, orange for electrical services and white for communication services.
label | 0a9b4a58-a26a-5475-97ba-dfaf945b9ef1 |  | note | ○ Ensure that pipe diameter is correct as per the drawings.
label | 2228e221-89bc-5623-96c3-d7daf7b13c94 |  | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.4 AS 1477 AS 2053
label | cf302bda-01b5-536e-9688-e3b16a7a9c35 |  | note | Inspection/Test Method - Verify
label | 86110fe3-7368-5cab-a456-dd3623a8f731 |  | note | Record of conformity - Aconex reference This ITP signed
label | 5af08d7a-b984-5b02-9978-fc0db3cb6214 |  | note | IP
label | 593f0f5e-a639-5aa7-b8c4-36cdafa92cab |  | note | Responsibility - Project Engineer
date | cec57df8-208a-5528-9608-2e86de3bf819 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.5 - Check bedding material compliance
label | 5f2c1b92-3599-5a8a-834a-427ad7a18190 |  | note | Frequency - Prior to commencing activity
label | 6fb6c1f2-9d81-5b59-b99f-e5f49ee6ddb5 |  | note | Acceptance Criteria - Ensure that conduit bedding material is non- plastic granitic sand complying with Table 3-1 and 3-2 under cl. 3.8.3.3 of the Works Specification.
label | 020b801f-5412-5d77-9d2a-2145dfd4cc60 |  | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.8.3.3
label | 8727225b-c976-525a-8b39-a8a70dd7c5b2 |  | note | Inspection/Test Method - Verify
label | 7636d754-0604-5df7-9841-02fb51f9bc27 |  | note | Record of conformity - Aconex reference
label | c4bc2b8d-464c-5b8b-a1ce-34e10567a9a9 |  | note | TP
label | c202e6eb-af88-5ad4-b192-43b7eadbf787 |  | note | Responsibility - Project Engineer
date | c7e23314-96b2-5d4f-95ae-b805ad0bb910 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.6 - Locate and prove existing services
label | b481a873-1b9b-587c-bb85-6db6664f6e12 |  | note | Frequency - Prior to commencing activity
label | 079fe04c-e0fd-5abd-89d5-2beade7873ef |  | note | Acceptance Criteria - Location of services to be found and marked on the ground within the works;
label | cab71392-4f1d-5730-b896-8dc966adc310 |  | note | ○ Contractor to obtain excavation permit from APAM prior to any demolition works.
label | c12281a4-c363-5678-af29-17485de6279a |  | note | ○ Services located within the works area to be exposed/proven, recorded as survey data and also on a service plan which is to be attached to the Excavation Permit.
label | e3f2e297-de92-5390-a29a-e6ecffaa0e1b |  | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.15
label | f37db078-ea05-5781-947a-5141c960d86d |  | note | Inspection/Test Method - Verify
label | 47c50d96-5b10-547a-b164-c366eded8ae3 |  | note | Record of conformity - Melbourne Airport Excavation Permit
label | 6ae7ada3-828e-5efa-b02d-1f97814f83c4 |  | note | HP*
label | 21f800ce-67b2-55b4-b05d-59bd92905a1b |  | note | Responsibility - Project Engineer / Surveyor
date | 22b782f4-e33b-586a-9f54-a5ccbadb9f8b |  | date | Date Completed:
checkpoint-group |  |  | section | 2.0 - Construction
checkpoint-status |  |  | checkpoint | 2.1 - Excavate trenches for conduits
label | 5bd4a899-f778-5d8c-b992-335b43cabe80 |  | note | Frequency - Each lot
label | 47fee060-3be0-5cd5-92ff-7cc2ecafb650 |  | note | Acceptance Criteria - Trenches for conduits shall be excavated to the width and depth required enabling construction of the conduits to the requirements specified on the drawings.
label | 08811dd7-8796-5bb3-8ac0-cdca7c1dae5f |  | note | ○ The level at the bottom of the trench shall not be above the required level at any point.
label | 6b0450c6-a3f2-5f66-89e7-7f3673de58ad |  | note | ○ Any over excavation under pavements shall be restored using 5MPa lean mix concrete in conjunction with the embedment.
label | 80e258da-eebe-5947-af44-4382d2235a85 |  | note | Reference Documents - Drawings ZULU-BECA- 001-SPC-00004 cl. 3.6
label | 6ef7be7b-a588-5265-ac5d-3cdc2601cbf3 |  | note | Inspection/Test Method - Visual inspection
label | 8be7f315-2c5e-5326-8ad1-19ab81608184 |  | note | Record of conformity - This ITP signed
label | 4c8ef0f8-c97d-5915-a9db-4f39a711b06a |  | note | IP
label | 01d592f3-fdb5-502b-82ac-c60be15407cf |  | note | Responsibility - Project Engineer / Foreman
date | 21de2358-3437-5033-a795-74e2bc6a791b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Existing services crossing new conduits
label | ad540ad0-90dd-5cfe-b7b4-cd38d1129a8b |  | note | Frequency - Each lot
label | 8610695a-f5b6-5cde-aede-10dd232465a0 |  | note | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
label | 15c7adb2-452b-5f6f-903e-0b6b2d59e030 |  | note | ○ Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
label | 8c691458-22ee-56c5-8d0c-e75f284652b2 |  | note | Reference Documents - WMS002 – Working Near Existing Services
label | c4d3d455-51a3-5cf5-bc75-56a0a78aa1bc |  | note | Inspection/Test Method - Visual inspection
label | 62d0f4e4-b8ea-51a3-badf-52674410f43c |  | note | Record of conformity - As-built survey report
label | cb8ad14c-84af-5a07-9bcf-1568b1c7441e |  | note | SCP
label | 8a014a96-019e-5793-8c6b-9d9a6c7f2a18 |  | note | Responsibility - Project Engineer / Surveyor
date | b9cd8c33-d715-597c-b3a2-9debd806dc21 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Laying and jointing of conduits
label | a6d44dc9-0037-5d39-8d4a-0172eede369a |  | note | Frequency - Each lot
label | f32cb045-a292-5246-87d4-d27f7f190010 |  | note | Acceptance Criteria - All conduits shall be rigidly supported and positioned by concrete or plastic spacer blocks so that no displacement occurs during backfill.
label | a339ad4c-3e9f-59ea-b9f1-185bbda9515c |  | note | ○ Where conduit ends are not open to a pit, UPVC end caps shall be temporarily fitted to each end.
label | cff3ddce-2f19-59ad-b7ba-f60ad7f88809 |  | note | ○ Number of conduits and duct route to be confirmed for conformity with design.
label | a0edff87-a828-5c1e-8c99-46f0d6a2a643 |  | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.7
label | 9101403f-eeba-575d-82b0-a0702d54a132 |  | note | Inspection/Test Method - Visual inspection
label | df67a876-f59e-5da8-97cb-148c5ebf4c95 |  | note | Record of conformity - This ITP signed
label | 2aeb0379-0633-5c03-af97-8446cd0ed6ba |  | note | IP
label | 8e72718a-8e55-528f-8731-d5c59ffe18f2 |  | note | Responsibility - Project Engineer / Foreman
date | e4395f7c-9b90-5450-bc92-c1e031fe526d |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Survey as-built
label | 8ae894e3-637b-5fdf-a08c-96583d56b234 |  | note | Frequency - Prior to backfilling each lot
label | 7d523446-7f0c-5c9e-839a-bcbb7c6c5b79 |  | note | Acceptance Criteria - Surveyor to pick up completed conduit runs before backfill
label | b3ba4b9a-ccd1-531e-96fd-fd243d60682e |  | note | Reference Documents - FH QMP
label | 4d18d776-ce5e-598f-81ad-04054ca2922a |  | note | Inspection/Test Method - Verify / Inspection
label | 3f74a3af-7a35-51d7-bdae-fd3f196f6863 |  | note | Record of conformity - Survey report
label | 83f3fdd7-21a2-5f4a-b12e-2487dac36cee |  | note | SCP / IP
label | 99848c36-7396-5e20-b1bc-49bfd1f61ff2 |  | note | Responsibility - Project Engineer / Surveyor
date | 69571608-498b-5acb-b8a7-5ef9bf8be068 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.5 - Pre-pour inspection
label | 63e1ddfb-324e-5352-9960-19ac059be51f |  | note | Frequency - Prior to backfilling each lot
label | 6ca47f8f-1783-5edc-9745-8a5e7115652f |  | note | Acceptance Criteria - WITNESS POINT
label | 30198f96-49f8-5a96-8f9d-8b6683ec08e9 |  | note | ○ The Contractor must provide the Principal’s Representative notice of the Contractor’s intention to backfill trenches within a Lot. This must include details of the date, time and location of the proposed work.
label | e44ee0b4-2433-5de2-ac27-d8b2b4fde155 |  | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.8.1
label | 8562ecdb-2c4f-5f07-b889-1f23e5f9f6ed |  | note | Inspection/Test Method - Inspection
label | 652e0800-e063-5a07-ba7f-3bc1de37badc |  | note | Record of conformity - This ITP signed
label | 43d6d4a8-04db-576a-b546-2c9247a84fc5 |  | note | WP
label | cdb2e9f2-10a0-504c-af39-93028bb6a316 |  | note | Responsibility - Project Engineer / Principal’s Representative
date | 573ab9dc-8565-5dac-ad8b-861c41d100c2 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.6 - Backfilling conduits under pavement
label | 9b79ab7a-473c-565a-a81c-bb41bd53e5af |  | note | Frequency - Each lot
label | 84a78bd4-7be1-5deb-bfa2-179e60c267dd |  | note | Acceptance Criteria - Concrete encasement of conduits: Conduits to be encased in 5MPa lean mix concrete as per drawings.
label | abc9cbbe-1707-5518-b988-c316816c6500 |  | note | ○ Trenches in existing pavement: Surface shall be reinstated to match surrounding pavement. Unless noted otherwise, reinstate asphalt pavement surfaces to a minimum of 70mm (or to match existing depth (whichever is greater)).
label | 566010c6-75cd-57c1-8111-ec78c8b7c60f |  | note | ○ Trenches in new pavement: Pavement shall be constructed as per the drawings and specification.
label | fa092b72-e40e-55ac-98ab-6d7b0007dfee |  | note | Reference Documents - Drawings ZULU-BECA- 001-SPC-00004 cl. 3.8.2.1, cl. 3.8.2.2
label | de46ec6a-dabe-58d8-8332-7a8328fca9ab |  | note | Inspection/Test Method - Verify
label | 1e85192b-473e-51fa-b43d-fedae8eb6680 |  | note | Record of conformity - Delivery docket This ITP signed
label | 59f28043-12cd-563f-a677-368f1909068b |  | note | IP
label | 9fe060f9-0b13-5bae-a2af-be5f946c1a9c |  | note | Responsibility - Project Engineer/Foreman
date | 26f5dcc8-5e5e-530f-9875-62c54f019961 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.7 - Backfilling conduits in grassed areas
label | 45368ed3-77e7-5171-ae93-bcbf8cd8ee0b |  | note | Frequency - Each Lot
label | 29da3ecb-bb95-5c21-b2a4-32111784782f |  | note | Acceptance Criteria - HOLD POINT
label | 59d30ef8-d784-5d37-8c08-6a0a18f2bed1 |  | note | Conduits to be encased in compacted sand bedding. The material shall be non-plastic and comply with properties specified in Table 3-1 & 3-2 of the specification. Details of the proposed sand shall be submitted to the Principal’s Representative.
label | 28cf0053-f801-58d7-b6cb-b6e4e75f8fc3 |  | note | ○ Backfill layers:
label | 433db3cd-880b-58a5-96bb-b64607ef2cca |  | note | – Not exceeding 300mm compacted thickness.
label | 4c8cc8c4-fe17-5dec-9fdf-60b2222e0f42 |  | note | – Not less than 90% maximum dry density (test no. 5.1.1).
label | edc91752-a980-5b96-8dc6-f1574072c350 |  | note | – Not less than 70% of density index (test E6.1).
label | baaf9703-c6e3-5675-8495-e3496825ad94 |  | note | ○ Compaction testing carried out at a rate of not less than:
label | d5d45f2f-1e5f-5b35-b476-6a00e3449a19 |  | note | – Bedding: 1 test per 400m of conduit laid (min. 3x).
label | 7d9a0b65-e19f-5032-8ca8-9b2334162178 |  | note | – Backfill: 1 test per 400m of conduit laid per 0.5m of backfill depth (min. 3x).
label | 0a94df08-b49c-54ec-9da7-9d5387495e3e |  | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.8.3.1 cl. 3.8.3.2 cl. 3.8.3.3, AS 1289 Test no. 5.1.1 Test no. E6.1
label | 3902882f-cc33-546e-8317-145c2bf69871 |  | note | Inspection/Test Method - Verify
label | fb15c6af-65a4-5e70-b3d4-d83cb1c14892 |  | note | Record of conformity - Test report Aconex reference This ITP signed
label | 20898b04-d7b6-5eed-a433-b87081831e0f |  | note | HP / TP / IP
label | c261cac0-2e86-5ade-b734-ce96ebb85be3 |  | note | Responsibility - Project Engineer / Principal’s Representative / Foreman
date | 426b21e9-fdfa-5522-9c7f-1cc15b76b64b |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.8 - Conduit markers & warning tape
label | 6ea7d1b1-ffa1-5921-83a5-3151011919a2 |  | note | Frequency - Each lot
label | de28fb13-ba74-59ad-8e7a-eeeab8d601aa |  | note | Acceptance Criteria - Pavement edge duct markers shall be installed at the edge of pavements immediately over the centreline of duct banks.
label | bcbeb64e-f56a-569b-8128-3ed37af656e4 |  | note | ○ Warning tape shall be to AS 2648.1, and coloured orange for electrical/white for communications conduits.
label | 38f811d4-24d1-5c07-9dac-4c36110837a8 |  | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.11 cl. 3.12 AS 2648.1
label | 6634aa92-d07c-546d-a377-973a89791ee2 |  | note | Inspection/Test Method - Visual inspection
label | 66351acf-25c2-572e-ab3d-e8deb113b632 |  | note | Record of conformity - This ITP signed
label | b4c3b1d6-8dc3-5b46-9a4c-652f4e4c3e1e |  | note | IP
label | 4bae3308-85c1-5999-a239-9a56912eb3a0 |  | note | Responsibility - Project Engineer / Foreman
date | c6c08a2b-8e73-5271-b9f4-e2d11ff92c70 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.9 - Checking of conduit lines
label | 8df5d2ce-8815-57bc-921e-dc99ad009ab5 |  | note | Frequency - Each lot
label | 16282afc-900c-56dc-8833-be8ad010029a |  | note | Acceptance Criteria - HOLD POINT
label | 68f2e7f4-e2ad-5085-8702-3990e8c8fc8a |  | note | ○ Following installation, the conduit shall be checked by passing a mandrel (not less than 300mm long and having a diameter of not more than 6mm less than the diameter of the conduit) through each way, followed by a brush with stiff bristles to clean the conduit of any foreign materials.
label | 5b24093c-85b7-51d8-84d5-238e6ef03f3e |  | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.9
label | 89ce2275-1a9c-5b93-a389-9b14dc59ca27 |  | note | Inspection/Test Method - Visual inspection
label | 883bc1e9-e8ae-54f0-a3c5-3319d36a752e |  | note | Record of conformity - This ITP signed, Avionics Primary Trenching Checklist
label | 33cd7518-82c4-584a-a692-fd104f0153a6 |  | note | HP
label | d83875da-a9e6-515e-856e-19e14be8752f |  | note | Responsibility - Project Engineer / Principal’s Representative
date | c6b5ba0f-7684-5962-b28d-e9ec011c0279 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.10 - Conduit draw cord
label | 39a43258-897d-53f9-8eb9-2a6c7ad42338 |  | note | Frequency - Each lot
label | 53ed455d-bef3-5f8d-9f79-194429c69199 |  | note | Acceptance Criteria - Each duct way in each duct bank shall be fitted with a single unjointed length of draw cord of a length equal to the length of the duct plus 4m. The draw cord shall be nylon rope and be 6mm in diameter, blue in colour. The ends of the rope shall be coiled at the bottom of each pit or wound around a stake.
label | 665cc1aa-388f-535b-8ea2-10b9cf3d21f6 |  | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.10
label | 4f86ab93-9bc3-5ff3-b5ad-bb0b015601ba |  | note | Inspection/Test Method - Visual
label | 24a47102-b649-5f4b-8d21-4dc7e7aff131 |  | note | Record of conformity - This ITP signed, Avionics Primary/Secondary Trenching Checklist
label | 8279a195-1659-53b5-a19b-95f8bb45a797 |  | note | IP
label | b01fffed-b77c-58ea-a416-62f65a36c6dd |  | note | Responsibility - Project Engineer / Foreman
date | 62de86f8-cca8-5a9f-b2bb-fb681f5dfd91 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | b9a2a72e-561e-5add-b8d1-123fa722ca24 |  | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
text | f0a12b20-87af-5dea-882d-bd621cdc94fe |  | textbox | Print Name:
text | c60d8987-74b3-564f-8180-461412b0997f |  | textbox | Position:
date | 4bf0e38d-9853-5314-85c3-d70bb09bf2e2 |  | date | Work Completed On:
date | cea302a6-96d9-579a-96fe-62850ecaae65 |  | date | Date: