## Checklists
Type | Name | Values | Prefix | Postfix | Usage Count | User Addable | Template Name
checklist-flat | JHA - Job Hazard Analysis
section | Job details
date | Date:
textbox | Permit No.
textbox | Job No.
textbox | Site
textbox | Activity Location
textbox | Asset:
textbox | Work Details:
section | Prompts for Hazards - Mark all that apply.
button | Sparks/Open flame | YES,NO
button | Disabled safety device(s) | YES,NO
button | Uneven surfaces | YES,NO
button | Fatigue, over-exertion | YES,NO
button | Crane movements | YES,NO
button | Moving/Rotating parts | YES,NO
button | Remote area, working alone | YES,NO
button | Conflicting work/SIMOPS | YES,NO
button | Electrical arc flash | YES,NO
button | Sharp objects/materials | YES,NO
button | Restricted/Difficult Entry/Exit | YES,NO
button | Overhead obstacles | YES,NO
button | Ignition sources (other) | YES,NO
button | Access/Egress | YES,NO
button | Water body | YES,NO
button | Live equipment | YES,NO
button | Slippery surfaces | YES,NO
button | Suspended loads | YES,NO
button | Hazardous substances (chemicals) | YES,NO
button | Use of non-intrinsically safe equipment | YES,NO
button | Weather extremes | YES,NO
button | Moving vehicles | YES,NO
button | Task related noise | YES,NO
button | Engulfment | YES,NO
button | General waste | YES,NO
button | Hazardous waste | YES,NO
button | Hazardous/toxic substance, fumes, gas | YES,NO
button | Flammable materials - Gas, liquids, solids | YES,NO
button | Reduced visibility, lighting | YES,NO
button | Electricity | YES,NO
button | Static electricity | YES,NO
button | Work at height | YES,NO
button | Underground services | YES,NO
button | O2 Deficiency/Excess | YES,NO
button | Temperature extremes | YES,NO
button | Heavy objects | YES,NO
button | Radiation | YES,NO
button | Potential energy - Tension/Compression | YES,NO
button | Flying particles/Dust/Objects | YES,NO
button | Vehicle entry | YES,NO
button | Exposure to process temperatures. | YES,NO
section | Prompts for Initial Consequences - Mark all that apply | YES,NO
button | Falling/Dropped objects | YES,NO
button | Fall from height | YES,NO
button | Trip/Slip/Fall | YES,NO
button | Gas release | YES,NO
button | Pressure release | YES,NO
button | Struck by object | YES,NO
button | Exceeding tool limits | YES,NO
button | Overloading people | YES,NO
button | Unplanned shutdown | YES,NO
button | Exposure to O2 deficiency/excess | YES,NO
button | Exposure to hazardous substance | YES,NO
button | Entanglement | YES,NO
button | Flying objects | YES,NO
button | Loss of control | YES,NO
button | Loss of containment | YES,NO
button | Excess exposure to Emissions, dust, fumes, noise, fibres, heat | YES,NO
button | Loss of structural integrity | YES,NO
button | Equipment failure | YES,NO
button | Uncontrolled ignition source | YES,NO
button | Collision | YES,NO
button | Ignition/Fire | YES,NO
button | Back strain/Injury | YES,NO
button | Burns | YES,NO
button | Heat exhaustion | YES,NO
section | Initial controls - Mark all that apply. | YES,NO
note | People controls | YES,NO
button | Safety/Fire watch person | YES,NO
button | Barriers/Flagging | YES,NO
button | Warning signs | YES,NO
note | Equipment controls | YES,NO
button | Master tags and locks | YES,NO
button | Scaffolding for access | YES,NO
button | Radio communication | YES,NO
note | Environmental controls | YES,NO
button | Ventilation | YES,NO
button | Lighting | YES,NO
button | Gas Testing | YES,NO
note | High risk controls | YES,NO
button | WSCS Work permit | YES,NO
button | WSCS Certificates | YES,NO
button | Critical lift/Fall protection plan | YES,NO
button | Specialised PPE | YES,NO
button | Spill kit | YES,NO
button | Fire extinguisher | YES,NO
section | Signatures
textbox | Applicant name
signoff | Applicant signature
checklist-flat | JHA - Job Step
section | Task Step - add task step for each individual task
date | Date:
textbox | Task step number (eg. Step 1, Step 2 etc):
textbox | Task details:
textbox | Hazards:
dropdown | Initial score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
textbox | Potential consequence:
textbox | Controls:
textbox | Recovery steps:
dropdown | Residual score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
checklist-flat | Toolbox Meeting
section | Toolbox meeting
date | Date:
textbox | Meeting location:
textbox | Meeting conducted by:
textbox | Meeting attendees:
textbox | Today's work scope/Hazards
textbox | Hazard controls:
signoff | PICWS Signoff
checklist-flat | As-Built Drawings
section | As-Built Drawings - attach scanned documents
textbox | Drawing no.
checklist | Civil Checklist - LV Pillar Foundation
section | Ground Conditions:
checkpoint | Verify ground conditions are as-per design assumption
section | NAL/Schneider LV Pillar foundation installation:
checkpoint | Correct location per drawings
checkpoint | Subgrade has been prepared per drawings (attach photo)
checkpoint | Check for level
section | Ensure the conduits between Pillar and EV Charger are:
checkpoint | Sized as indicated in drawing
checkpoint | Routed per drawings
checkpoint | Depth defined in drawing
section | Ensure the conduits between Pillar and Site Lighting/Selector Switch are:
checkpoint | Sized as indicated in drawing
checkpoint | Routed per drawings
checkpoint | Depth defined in drawing
section | Ensure the Fibre Optic/Earthing conduits between Pillar and Sales Store are:
checkpoint | Sized as indicated in drawing
checkpoint | Routed per drawings
checkpoint | Depth defined in drawing
section | Verify working space from front of LV Pillar
checkpoint | Ensure placement will allow for working area and emergency egress
section | As-built height of foundation
checkpoint | Verify protrusion above ground level is as per specification/drawing
section | LV Pillar Installation - if LF Pillar is installed ensure:
checkpoint | Ensure LV Pillar has been bolted down with the correct torque settings as per LV pillar specification
checkpoint | Water tightness/IP Specifications are being met
checkpoint | Record and photograph the serial number of the LV Pillar
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Civil Checklist - NAL Solution/Monolithic Foundation
section | Ground Conditions:
checkpoint | Verify ground conditions are as per design assumptions
section | Verify STAKKAbox Installation is:
checkpoint | Subgrade prepared per drawings
checkpoint | STAKKAbox installed at location shown on drawing
checkpoint | Correct number of STAKKAbox installed
checkpoint | STAKKAbox are clear of any debris
checkpoint | STAKKAbox are installed at correct depth
checkpoint | Conduits enter at correct locations and verify depth
checkpoint | Protruding above the ground within the specified limits
section | Verify NAL EV Charger Socket is:
checkpoint | Installed per drawing
checkpoint | Correct depth as-per drawing
checkpoint | Verify level prior to EV charger placement
section | Verify NAL Bollard Sockets are:
checkpoint | Installed per drawing & Counts verified
checkpoint | Correct depth & spacing
checkpoint | Verify level
section | Verify NAL Flex-Bollards are:
checkpoint | Installed per drawing & counts verified
checkpoint | Correct height & spacing
checkpoint | Verify they are plumb
checkpoint | Pass pull-test/unable to be lifted out by hand
section | Verify Monolithic foundation (as required) is:
checkpoint | Installed as-per drawing
checkpoint | Pad/foundation is correct depth and dimensions
checkpoint | Rebar is proper size and correctly spaced (Photo)
checkpoint | Top of pad is free of defects, has an even surface with broom finish
checkpoint | Verify conduits are stubbed up in correct location
checkpoint | Protruding above the ground within the specified limits
section | Verify Anchor bolts:
checkpoint | In correct location as per drawing
checkpoint | Proper embedment depth
checkpoint | Pass pull-test/unable to be lifted out by hand
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Civil Checklist - Lighting Columns/Selector Switch/Fixture
section | Verify that lighting columns are:
checkpoint | As-per drawings
section | Verify lighting selector switch is:
checkpoint | Installed per manufacturers specification
checkpoint | As-per drawings
section | Light fixtures
checkpoint | Verify Lumens as per specification
checkpoint | Record serial numbers
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Civil Checklist - EV Charging Parking Stalls
section | Verify dimensions match drawings
checkpoint | Depth, Length and Width are per drawings
section | Painted stripes are clean and correct colour
checkpoint | No over spray, colour is correct, lines are straight
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Civil Checklist - Miscellaneous Site Civil
section | New curb/gutter footpath per plans
checkpoint | Concrete is consistent and installed to match existing appearance and levels
section | Existing curb/gutter sidewalk undamaged
checkpoint | No damage to existing curb/gutters
section | Landscaping removed/damaged during construction is replaced to match
checkpoint | Replacements match what was damaged
section | New landscaping installed per plans. Ensure proper watering is in plans. Verify:
checkpoint | Correct species
checkpoint | height of plants is per plan
checkpoint | irrigation is provided
section | Irrigation system working properly. Irrigation that was disrupted during construction is:
checkpoint | Repaired and operation verified (Site host to provide signature)
checkpoint | Spray patterns are set correctly
section | Air & Water station relocation
checkpoint | Verify air & water station is functioning after relocation (Site host to provide signature)
section | Wheel stops are installed per drawings
checkpoint | Dimensions, height and width are per drawings
section | Parking stall signage complete per plans
checkpoint | Confirm the height of sign posts above grade is accurate and matches drawings
section | Site clean up
checkpoint | All debris removed by the time commissioning occurs. Site housekeeping must be kept up to minimize the disruption to the landlords
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Civil Checklist - Miscellaneous - Site Specific
section | Corrosion Protection
checkpoint | Ensure all corrosion prone surfaces are covered
section | Sharp objects
checkpoint | Ensure no sharp edges/protrusions are present following the completion of work
section | Concrete slump test
checkpoint | Concrete slump test to be conducted prior to all concrete pour. Refer to concrete specification in drawings
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-flat | Cable Test Record
checkpoint | Upload completed ITR scans
checklist | Tritium - Site Installation checklist
checkpoint | Upload completed Tritium checklist scan
checklist | Electrical checklist - LV Pillar
section | LV Pillar Setup/Installation
checkpoint | Confirm the switchboard is correctly located, aligned and foundation bolts and fixings are secure as-per switchroom layout drawings
checkpoint | Check that the final factory test and inspection record is enclosed with the LV Pillar delivered.
checkpoint | Check the LV pillar serial number matches the factory test and inspection record.
checkpoint | Check the LV Pillar is correctly installed and sealed on the foundation plinth, as per the IOM Manual
checkpoint | Visually inspect the LV pillar for external damage (including paintwork)
checkpoint | Verify nameplate details against data sheet. (LV Pillar type, compliance standard, rating in amps)
checkpoint | Check all cubicle doors can be fully opened without obstruction and that door hinges are installed correctly.
checkpoint | Check inside of the switchboard is clean and dry, check that all preservation (i.e. silica gel) has been removed (Pre-Energization)
checkpoint | Ensure all major components conform to vendor's design documentation and drawings.
checkpoint | Check all fuses/fuse carriers and link are correct to drawings
checkpoint | Check all equipment carries the correct circuit identification
checkpoint | Check busbar phase identifications are correct and phasing is maintained
checkpoint | Ensure all busbars are encapsulated as-per design requirements
checkpoint | Check the protective device(s) rating match the approved design
checkpoint | Check LV Cable terminations are completed correctly and are tight and secure
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Electrical checklist - Cables/Cable Entry Points/Cable Containment
section | Cables/Cable Entry Points/Cable Containment
checkpoint | Check all cable entries are correct to design requirements and spare enters are correctly plugged with Rayflates/Foam
checkpoint | Check that the depth of installation of the duct network matches the approved design. (To be witnessed by BP)
checkpoint | Check the number and type/size of ducts installed meets the approved design. (To be witnessed by BP)
checkpoint | Check the cable entry is at the correct depth (Minimum bending radius achieved)
checkpoint | Check the correct type of reinstatement material has been used to backfill the cable/duct network. (100mm of sand below and on top of ducts/cables.)
checkpoint | Check cable warning tape is laid prior to backfilling
checkpoint | Check the high level cable containment (Trays/Ladders) and cable cleats match the approved design.
checkpoint | Check all metal cable containments are bonded and connected to the main earthing system
checkpoint | Check that the tray/ladder is not damaged and is free of any sharp edges.
section | Cables
checkpoint | Check the cables installed are the correct type/size, as per the approved design.
checkpoint | Check the correct bending radius is being applied to the cable at the entry/exit points
Check the cable cleat and clamp screw are secure and tight
Check that the cables have been fully tested after installation and prior to terminating to the LV Pillar (Continuity, insulation resistance)
Check that the cable ends have been correctly capped after installation in ducts, to avoid water ingress in the cable (unless terminated straight after installation and testing)
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Electrical checklist - Earthing System
section | Earthing System
checkpoint | Check earth electrode system is installed at the correct depth and as per the approved design
checkpoint | Earth bosses installed correctly
checkpoint | Check all earth cables/electrodes are correctly sized
checkpoint | Check that the equipment is bonded to the main earth
checkpoint | Check all the earth cable lugs and cable idents are fitted correctly
checkpoint | Check earth cable mechanical protection is installed
checkpoint | Location of earth rod as per the location drawing
checkpoint | Check any metal doors and louvres are bonded to earth correctly
checkpoint | Earth pit installed properly according to finish ground level without any damages and connection facilities are installed
checkpoint | Earth pit tagging complete and is as-per the drawings
checkpoint | If the site is a hot site (EPR > 430V), check that the HV/LB earthing systems are fully segregated (HV/LV earth link removed in the LV Pillar)
checkpoint | Check the earthing system of the EV charger is as per the approved design.
section | Earthing System Test
checkpoint | Test certificate to be provided with a detailed SOW and test results
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Electrical checklist - Metering
section | DNO Cutout and Metering
checkpoint | Check that the metering unit matches the approved design
checkpoint | check sufficient space is available between the meter and incoming cutout
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Electrical checklist - Lighting and Small Power
section | Lighting Columns
checkpoint | Verify the number as-per the drawing
checkpoint | Provide lighting cable test results
checkpoint | Check lighting operation
checkpoint | Check lux level of lighting meets design requirements
section | Power supply for Comsat unit
checkpoint | Verify the install is per the agreed design
checkpoint | Provide test results for the small power installation (separate test sheet)
checklist | Electrical checklist - EV Charger
section | EV Charger
checkpoint | Check the charger is free of any damage
checkpoint | Check the internal arts are free of any damages
checkpoint | Check the unit s correctly located as-per layout drawing
checkpoint | Check the unit is installed correctly and is level
checkpoint | Check the charger rating matches the purchase order
checkpoint | Check the type of sockets match the purchase order
checkpoint | Check the payment terminal matches the purchase order
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Electrical checklist - FO Install
section | FO Equipment
checkpoint | Verify the install is per the agreed design
checkpoint | Provide test results for the FO cable and associated equipment (separate test sheet)
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP