## Network Drainage
|  |  |  | Process Control Plan |  | FHIMS-QA-6007 | Approved |  | Signature
|  |  |  | Contract Name: | Luggate Water Supply Upgrades |  | FH Engineer
|  |  |  | Procedure: | Raw watermain install |  | FH Quality Manager
Inspection & Test Plan / Checklist
Lot No: |  |  |  | Corresponding Work Instruction: |  | C-25-049 |  | Compliance with Work Instructions and Specifications
Detailed Location: Church Road
Chainage: CH 0 - 241
No: | Inspection / Test Point | ACTION (Hold, Monitor, Witness) | Detail | Frequency | Inspection / Test Method submission, visual inspection, testing, measure, review | Conformance Criteria | Records | FH Initials | Design Engineer Initials (Grey if not required) | Date(s)
1 | Permits | M | Obtain Permits | As required | Document Review | Control Checklist - Digging Checklist (incl. marking out & potholing existing services), PTW #2 - Trench Excavation Inspection, PTW #1 - Confined Space. Notify Worksafe NZ if required. Ensure all necessary Permit to Works & Controlled Checklists are in place | Permit attached or permit number noted | Site Engineer
2 | Pre-construction sign offs | H | Ensure that Sub-Contract and Supplier Agreements are signed, TMP is approved all personnel are inducted to site | Prior to commencement | Document Review | All personnel inducted to site, TMP as required for sub-work area, any permits/approvals required for work area obtained | As per conformance criteria | Site Engineer
3 | Design | H | Ensure that Design is approved and Drawings are of the latest revision | Prior to commencement | Document Review | — | Check Drawing Register | Site Engineer
4 | Installation of Erosion and Sediment Controls (1) | H | Set up Erosion and sediment controls as per ESCP and undertake pre & post rainfall checks | Prior to commencement | Document Review | Check ESCP and monitor weather for rainfall checks | EMP | Site Engineer
4 | Installation of Erosion and Sediment Controls (2) | M | Monitor effectiveness of the ESCP Controls throughout the construction process | — | Visual Inspection | — | Check EMP | Site Engineer
5 | Survey Setout | H | Survey setout of pipeline of GPS design on excavation machinery as required by contractor to construct to design | Prior to commencement | Survey/ Use of GPS design | — | Survey receipt where used | Site Engineer
6 | Locate existing services by hand digging | M | Ensure all services conflicting with the line of trench has been exposed by hand digging | Prior to commencement | Potholing | All conflicts have been located. New services and/or conflicts recorded. | Service Location & Potholing PCP | Site Engineer
7 | Trenching and Excavation (1) | H | Inspect trench profile and ensure it is correct to lines and levels to design | Daily | Visual/Inspection | Line and level is correct | Drainage Line Record | Site Engineer
7 | Trenching and Excavation (2) | H | Ensure trench width meets the specification | Daily | Visual/Inspection | Trench width meets design cross sections - Detail A Raw water steep shared trench detail | Drainage Line Record | Site Engineer
8 | Undercut material for re-use as trench backfill in berm/access road | H | Backfill Construction Material | Excavated material for re-use as trench backfill (Excluding steep slope section CH 80-120) | Document Review | Field testing | Lab Test Report | Site Engineer
9 | Foundation Compliance | H | Test formation level on completion of excavation to check if undercut required | One test per 10 linear metres (Excluding steep slope section CH 80-120) | Scala Penetrometer or Shear Vane as appropriate for soil type | If scala is less than 2 blows per 100mm or shear strength less than 50Kpa, then the engineer shall be notified | Drainage Line Record | Site Engineer
|  | H | Test formation level on completion of excavation to check if undercut required | As stated | Visual Inspection by Designer | Designer to inspect formation level at outfalls / inlets. | FHIMS-CS-4025 | Site Engineer | Design Engineer
10 | Pipe Bedding/Haunching Material Compliance (1) | H | Pipe bedding | Prior to commencement | Lab Testing | MDD & PSD | Lab Test Report Pipe supplier letter | Site Engineer
10 | Pipe Bedding/Haunching Material Compliance (2) | H | Backfill Construction Material | Prior to commencement | Lab Testing | MDD & PSD | Lab Test Report | Site Engineer
10 | Pipe Bedding/Haunching Material Compliance (3) | H | Backfill Construction Material (Road crossing) | Prior to commencement | Lab Testing | MDD & PSD | Lab Test Report | Site Engineer
11 | Bedding | W | Ensure bedding material is compacted | Prior to laying pipe | Testing | Testing undertaken to correlate Clegg hammer target (CIV) to MDD via NDM testing | Clegg test results | Site Engineer | Design Engineer/QLDC Representative
12 | Pipes, valves & fittings | H | Confirm pipes diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | Each delivery to site | Certification | Pipe - Diameter & Class | Material certificate | Site Engineer
13 | Pipe Welding (1) | H | Pipe welding meets specification requirements | Each Weld | Welding records | Butt Welding to be completed as per specification | Weld Reports | Site Engineer
13 | Pipe Welding (2) | H | Butt weld testing | During Construction | Test results | Two welds undertaken to demonstrate the pipes have been successfully welded under the site conditions. Tensile strength of 95% with no brittle fracture. | Test results | Site Engineer
13 | Pipe Welding (3) | H | EF weld testing | During Construction | Test results | One test welds undetaken on thickest walled PE pipe to demonstrate the pipes can be successfully using equipment and methodology.Maximum brittle fracture is 33% of the fusion length. | Test results | Site Engineer
14 | Pipe Laying (1) | H | Notification to Engineer that pipe laying works are due to commence to allow Engineer opportunity to inspect as work proceeds | Prior to commencement | Notification | — | This PCP | Site Engineer
14 | Pipe Laying (2) | M | Pipe Laying -Variation between design invert level to as-laid invert level must meet specifications. | Daily | Visual/Inspection | Grade >1%: Invert 10mm or less from design (If pipe less than or equal to 1% grade, invert to be no more than 3mm from design levels) | Photos & Drainage Line Record | Site Engineer
14 | Pipe Laying (3) | W | DN 315 OD PE 100 PN 16 Watermain & shared trench services | During Construction | Visual/Inspection | Installed as per IFC drawings ad meets design cross sections - Detail A Raw water steep shared trench detail | Photos | Site Engineer | Design Engineer/QLDC Representative
14 | Pipe Laying (4) | M | Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness | Prior to backfilling | Visual/Inspection | No defects/ gaps / pipes are aligned correctly Pipes are clean nd free from dirt and debris. | Photos | Site Engineer
14 | Pipe Laying (5) | M | As-built survey of pipes installed | During Construction | Survey | As per IFC drawings and as per specification. | Survey Receipt | Site Engineer
15 | AV installation | H | Installation as per IFC drawing detail | During Construction | Visual/Inspection | As per IFC drawings and as per specification. | Photos/Inspections | Site Engineer
16 | Design Engineer Pre-backfill Inspection | W | Inspection of pipes prior to backfilling to ensure they have been installed correctly and that the joints are sealed. Check for any gaps. | Prior to backfilling | Visual Inspection | Compliance with the Specification | Inspection Record | Site Engineer | Design Engineer/QLDC Representative
17 | Haunching/Backfilling (berm/access road crossings) | W | Backfill in 200 mm loose lifts. Noting that backfill will comprise of scalpings, and re-use of excavated material. | Clegg testing every 50m along trenchline at 200 mm lifts | Testing | NDM testing will be undertaken at intervals of 1 in every 2km to correlate Clegg hammer target (CIV) to MDD | Clegg test results | Site Engineer | Design Engineer/QLDC Representative
| Haunching/Backfilling (Steep slope - CH 80-120) | W | Backfill with AP20 cement mixture as per IFC Detail A Raw water steep shared trench detail | Prior to backfilling | Batch report | Supplier to provide batch report to confirm correct weightings of cement and AP20- | Batch report | Site Engineer | Design Engineer/QLDC Representative
18 | Pressure testing (1) | H | Notification to Engineer of at least 48 hours of testing and completion of pre-requisites | Prior to Commissioning | Notification | — | This PCP | Site Engineer
18 | Pressure testing (2) | W | Pressure pipelines to be pressure tested | Prior to Commissioning | Testing | Pressure Test Record Compliance with QLDC CoP Appendix C criteria. | Pressure Test Record | Site Engineer | Design Engineer/QLDC Representative
19 | Disinfection | H | Disinfection & bacteriological testing | Prior to Commissioning | Testing | Disinfection as per approved methodoloy in accordance with QLDC CoP Appendix D aceptance criteria | Bacteriological test results | Site Engineer
20 | As-builts | M | Red pen mark up drawings to be included in QA file | At the completion of the Lot of work | Document Review | — | Asbuilt Drawing | Site Engineer
21 | Asset Capture | H | Asset register to be completed | At the completion of the Lot of work | Document Review | Asset informtion to be entered to correct spreadsheets | Asset register | Site Engineer
22 | Lot Number QA File | W | Ensure all OFIs are closed and included within QA file, Delivery Dockets, Test Reports Surveys and Check Sheets to be included in QA File | At completion of Lot | Document Review | Ensure all QA is uploaded | All lot QA | Site Engineer
Comments:
IFC Drawings used for Construction incl. Rev numbers:
Reference Documentation (Notices/OFIs etc.):
QA Compiled By : |  | Maddie Irving |  |  | Signature: |  |  | Date:
QA checked By Discipline Manager: |  | Andy Boyd |  |  | Signature: |  |  | Date:
QA checked By Quality Manager: |  | Kurt Beeton |  |  | Signature: |  |  | Date:
Accepted By Design Engineer: |  | TBC |  |  | Signature: |  |  | Date:
Note on D12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This will be a monitor action.
Note on I22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assume best place to record this is on drainage line record. Can we confirm who will be completing the scalas? Does drainage have a scala available for this? Suggest foreman best placed due to frequency of testing required - Let me know ASAP if this is going to be an issue Reply: Agreed, Will include on drainage line record and foreman can complete scalas
Note on I25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm that MDD & PSD allowed for within pricing - and what are the timeframes on this. We will need to organise this ASAP if not done already. Have a feeling Cody has had some testing done at Luggate quarry? Please confirm ASAP
Note on I26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should be attainable from quarry - AP65 Reply: I can chase this up
Note on H30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Need to arrange to be done before Polypipe disestablish - arrange asap Reply: Will arrange
Note on H31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See spec Pre-construction weld tests. Calls to prove tensile strength/brittle fracture. Polypipe should be able to provide this Reply: Destructive test results for DN 315 PE PN16 pipe ^^^^ Reply: Cody asked polypipe to do this last week. I’ll send through once I have results
Note on I33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is there any additional record that could support this. Maybe the drainage line record? And completed by foreman as works proceed. Let’s discuss Reply: Will add to the drainage line record Reply: Nice
Note on D34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Witness action