## Network Drainage
[5 empty] | Process Control Plan |  | FHIMS-QA-6007 | Approved |  | Signature
[5 empty] | Contract Name: | Luggate Water Supply Upgrade |  | FH Engineer
[5 empty] | Procedure: | Headworks Assembly |  | FH Quality Manager
Inspection & Test Plan / Checklist
| Lot No: Borehead works |  |  |  | Corresponding Work Instruction: |  | C-25-049 |  | Compliance with Work Instructions and Specifications
Detailed Location: Church Road
Chainage:
| No: | Inspection / Test Point | ACTION (Hold, Monitor, Witness) | Detail | Frequency | Inspection / Test Method submission, visual inspection, testing, measure, review | Conformance Criteria | Records | FH Initials | Design Engineer Initials (Grey if not required) | Date(s)
| 1 | Permits | M | Obtain Permits | As required | Document Review | Control Checklist - Digging Checklist (incl. marking out & potholing existing services), PTW #2 - Trench Excavation Inspection, PTW #1 - Confined Space. Notify Worksafe NZ if required. Ensure all necessary Permit to Works & Controlled Checklists are in place | Permit attached or permit number noted | Site Engineer
| 2 | Pre-construction sign offs | H | Ensure that Sub-Contract and Supplier Agreements are signed, TMP is approved all personnel are inducted to site | Prior to commencement | Document Review | All personnel inducted to site, TMP as required for sub-work area, any permits/approvals required for work area obtained | As per conformance criteria | Site Engineer
| 3 | Design | H | Ensure that Design is approved and Drawings are of the latest revision | Prior to commencement | Document Review | Shop drawings approved | Check Drawing Register | Site Engineer
|  |  | H | Test formation level on completion of excavation to check if undercut required | As stated | Visual Inspection by Designer | Designer to inspect formation level at outfalls / inlets. | FHIMS-CS-4025 | Site Engineer | Design Engineer
| 4 | Material Compliance (1) | H | Stainless steel pipework | Prior to commencement | Document Review | All stainless-steel pipe is to be new with dimensions per ASME B36.19M and material in accordance with ASTM A312 Gr. TP316L. | Materials analysis cerificate | Site Engineer
| 4 | Material Compliance (2) | H | Stainless steel flanges | Prior to commencement | Document Review | All stainless-steel flanges and fittings to be new and material in accordance with ASTM A182 Gr. F316L or ASTM A403 Gr. WP316L. | Material certificate | Site Engineer
| 4 | Material Compliance (3) | H | Stainless steel elbows | Prior to commencement | Document Review | All stainless-steel pipe elbows shall be long radius butt weld pipe fittings to ASME B16.9. | Material certificates | Site Engineer
| 5 | Stainless Steel weld inspections | H | Stainless steel fabricated pipework | During Construction | Test results | 100% visual scanning and; 5% radiography for workshop fabrication; 10% radiography for site welding. Non-destructive examination of all welds shall be carried out in accordance with AS/NZS 1554.1 and AS/NZS 1554.6. Welding inspectors shall verify that fabrication/erection welding is performed in accordance with the requirements of the Specifications and the applicable Standards. All weld inspections shall be performed by independent welding inspectors ed in accordance with AS 1554.1 and AS/NZS 1554.6. | Inspection report | Site Engineer
| 6 | Valves & fittings | M | Confirm pipes diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | Each delivery to site | Certification | Pipe - Diameter & Class | Material certificate | Site Engineer
| 7 | Borepump testing | H | FAT testing | Prior to delivery | Test results | Pumps shall be Factory Performance Acceptance Tested in accordance with the requirements of Hydraulic Institute 14.6 and using grade 1U acceptance criteria for Rated flow, Total head and Efficiency. Pumps shall also be Factory Performance Acceptance Tested for vibration in accordance with ISO 10816-7 Category II. | Test results | Site Engineer | Design Engineer/QLDC Representative
| 8 | Pipework assembly (1) | M | Stainless steel pipework, valves & fittings all installed as per approved drawings | During Construction | Visual inspection | As per approved shop drawings | Photos | Site Engineer
| 8 | Pipework assembly (2) | M | Flange dressing sets | During Construction | Visual inspection | Gaskets shall be nitrile rubber, complying with WSA 109:2021 All bolts, nuts and washers shall be grade 316 stainless steel with factory applied “Molybond” coatings. Each bolt head shall be marked as A4-70 (rolled thread) Where stainless steel bolts are connecting flanges of material other than stainless steel, the Contractor shall isolate the stainless steel bolt from the flange by the use of Delrin washers or equivalent approved washer to provide electrical isolation between the dis-similar metals. Interfaces between dissimilar metals shall be isolated with suitable flange isolating kits, as indicated on the drawings. | Photos | Site Engineer
| 8 | Pipework assembly (3) | M | Buried Pipework | During Construction | Visual inspection | Buried stainless steel pipework to be wrpped in Denso petrolaum protection as detaild in the Mechanical Specification | Photos | Site Engineer
| 9 | Borepump testing | H | Onsite vibration testing | Following insgtallation | Test results | Vibration testing shall be carried out on the installed pump and motor units on site in accordance with ISO 10816-7 Category II. | Test results | Site Engineer | Design Engineer/QLDC Representative
| 10 | As-builts | M | Red pen mark up drawings to be included in QA file | At the completion of the Lot of work | Document Review | The depth setting of the water level sensor and its datum shall be recorded on As-Built plans submitted to QLDC. | Asbuilt Drawing | Site Engineer
SS | 11 | Asset Capture | H | Asset register to be completed | At the completion of the Lot of work | Document Review | Asset informtion to be entered to correct spreadsheets | Asset register | Site Engineer
| 12 | Lot Number QA File | W | Ensure all OFIs are closed and included within QA file, Delivery Dockets, Test Reports Surveys and Check Sheets to be included in QA File | At completion of Lot | Document Review | Ensure all QA is uploaded | All lot QA | Site Engineer
Comments:
IFC Drawings used for Construction incl. Rev numbers:
Reference Documentation (Notices/OFIs etc.):
| QA Compiled By : |  | Maddie Irving |  |  | Signature: |  |  | Date:
| QA checked By Discipline Manager: |  | Ben Seaton |  |  | Signature: |  |  | Date:
| QA checked By Quality Manager: |  | Kurt Beeton |  |  | Signature: |  |  | Date:
| Accepted By Design Engineer: |  | TBC |  |  | Signature: |  |  | Date:
Note on D12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This will be a monitor action.
Note on D24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Witness action