## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | FHIMS-QA-6007 - PCP Headworks Assembly | itp |  |  |  |  | FHIMS-QA-6007 - PCP Headworks Assembly Rev 0
section | PCP Headworks Assembly
checkpoint | 1 - Permits
label | ACTION (Hold, Monitor, Witness) - M
label | Detail - Obtain Permits
label | Frequency - As required
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Document Review
label | Conformance Criteria - Control Checklist - Digging Checklist (incl. marking out & potholing existing services), PTW #2 - Trench Excavation Inspection, PTW #1 - Confined Space. Notify Worksafe NZ if required. Ensure all necessary Permit to Works & Controlled Checklists are in place
label | Records - Permit attached or permit number noted
checkpoint | 2 - Pre-construction sign offs
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Ensure that Sub-Contract and Supplier Agreements are signed, TMP is approved all personnel are inducted to site
label | Frequency - Prior to commencement
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Document Review
label | Conformance Criteria - All personnel inducted to site, TMP as required for sub-work area, any permits/approvals required for work area obtained
label | Records - As per conformance criteria
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3 - Design
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Ensure that Design is approved and Drawings are of the latest revision
label | Frequency - Prior to commencement
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Document Review
label | Conformance Criteria - Shop drawings approved
label | Records - Check Drawing Register
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4 - Material Compliance (1)
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Stainless steel pipework
label | Frequency - Prior to commencement
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Document Review
label | Conformance Criteria - All stainless-steel pipe is to be new with dimensions per ASME B36.19M and material in accordance with ASTM A312 Gr. TP316L.
label | Records - Materials analysis cerificate
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4 - Material Compliance (2)
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Stainless steel flanges
label | Frequency - Prior to commencement
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Document Review
label | Conformance Criteria - All stainless-steel flanges and fittings to be new and material in accordance with ASTM A182 Gr. F316L or ASTM A403 Gr. WP316L.
label | Records - Material certificate
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4 - Material Compliance (3)
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Stainless steel elbows
label | Frequency - Prior to commencement
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Document Review
label | Conformance Criteria - All stainless-steel pipe elbows shall be long radius butt weld pipe fittings to ASME B16.9.
label | Records - Material certificates
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5 - Stainless Steel weld inspections
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Stainless steel fabricated pipework
label | Frequency - During Construction
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Test results
label | Conformance Criteria - 100% visual scanning and; 5% radiography for workshop fabrication; 10% radiography for site welding.
label | ○ Non-destructive examination of all welds shall be carried out in accordance with AS/NZS 1554.1 and AS/NZS 1554.6. Welding inspectors shall verify that fabrication/erection welding is performed in accordance with the requirements of the Specifications and the applicable Standards.
label | ○ All weld inspections shall be performed by independent welding inspectors ed in accordance with AS 1554.1 and AS/NZS 1554.6.
label | Records - Inspection report
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6 - Valves & fittings
label | ACTION (Hold, Monitor, Witness) - M
label | Detail - Confirm pipes diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
label | Frequency - Each delivery to site
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Certification
label | Conformance Criteria - Pipe - Diameter & Class
label | Records - Material certificate
checkpoint | 7 - Borepump testing
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - FAT testing
label | Frequency - Prior to delivery
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Test results
label | Conformance Criteria - Pumps shall be Factory Performance Acceptance Tested in accordance with the requirements of Hydraulic Institute 14.6 and using grade 1U acceptance criteria for Rated flow, Total head and Efficiency.
label | ○ Pumps shall also be Factory Performance Acceptance Tested for vibration in accordance with ISO 10816-7 Category II.
label | Records - Test results
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 8 - Pipework assembly (1)
label | ACTION (Hold, Monitor, Witness) - M
label | Detail - Stainless steel pipework, valves & fittings all installed as per approved drawings
label | Frequency - During Construction
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Visual inspection
label | Conformance Criteria - As per approved shop drawings
label | Records - Photos
checkpoint | 8 - Pipework assembly (2)
label | ACTION (Hold, Monitor, Witness) - M
label | Detail - Flange dressing sets
label | Frequency - During Construction
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Visual inspection
label | Conformance Criteria - Gaskets shall be nitrile rubber, complying with WSA 109:2021
label | ○ All bolts, nuts and washers shall be grade 316 stainless steel with factory applied “Molybond” coatings. Each bolt head shall be marked as A4-70 (rolled thread)
label | ○ Where stainless steel bolts are connecting flanges of material other than stainless steel, the Contractor shall isolate the stainless steel bolt from the flange by the use of Delrin washers or equivalent approved washer to provide electrical isolation between the dissimilar metals. Interfaces between dissimilar metals shall be isolated with suitable flange isolating kits, as indicated on the drawings.
label | Records - Photos
checkpoint | 8 - Pipework assembly (3)
label | ACTION (Hold, Monitor, Witness) - M
label | Detail - Buried Pipework
label | Frequency - During Construction
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Visual inspection
label | Conformance Criteria - Buried stainless steel pipework to be wrpped in Denso petrolaum protection as detaild in the Mechanical Specification
label | Records - Photos
checkpoint | 9 - Borepump testing
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Onsite vibration testing
label | Frequency - Following insgtallation
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Test results
label | Conformance Criteria - Vibration testing shall be carried out on the installed pump and motor units on site in accordance with ISO 10816-7 Category II.
label | Records - Test results
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 10 - As-builts
label | ACTION (Hold, Monitor, Witness) - M
label | Detail - Red pen mark up drawings to be included in QA file
label | Frequency - At the completion of the Lot of work
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Document Review
label | Conformance Criteria - The depth setting of the water level sensor and its datum shall be recorded on As-Built plans submitted to QLDC.
label | Records - Asbuilt Drawing
checkpoint | 11 - Asset Capture
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Asset register to be completed
label | Frequency - At the completion of the Lot of work
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Document Review
label | Conformance Criteria - Asset informtion to be entered to correct spreadsheets
label | Records - Asset register
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 12 - Lot Number QA File
label | ACTION (Hold, Monitor, Witness) - W
label | Detail - Ensure all OFIs are closed and included within QA file, Delivery Dockets, Test Reports Surveys and Check Sheets to be included in QA File
label | Frequency - At completion of Lot
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Document Review
label | Conformance Criteria - Ensure all QA is uploaded
label | Records - All lot QA
checkpoint | Final Inspection
label | QA Compiled By: Maddie Irving
label | QA checked By Discipline Manager: Ben Seaton
label | QA checked By Quality Manager: Kurt Beeton
textbox | Accepted By Design Engineer:
signoff | Sign ITP