## Project Structure EG (hidden)
Folder Structure |  |  |  | Checklists
Site QA
Switchboards
S1
|  |  | S.1 Assembly | QA_TEM_013_Switchboard & Distribution Board Assembly
|  |  | S.1 Installation | QA_TEM_012_Switchboard & Distribution Board Installation
|  |  | S.1 Cable Termination | QA_TEM_014_Cable Terminations
|  |  | S.1 Accessories | QA_TEM_015_Accessories Installation
|  | S2 |  | Same as S1
|  | S3 |  | Same as S1
|  | S4 |  | Same as S1
|  | S5 |  | Same as S1
|  | S6 |  | Same as S1
|  | S7 |  | Same as S1
|  | S8 |  | Same as S1
|  | S9 |  | Same as S1
|  | S10 |  | Same as S1
Cable Support
Room 1
|  |  | Prior | QA_TEM_008_Cable Support Prior to Cabling
|  |  | Post | QA_TEM_009_Cable Support Post Cabling
|  | Room 2 |  | Same as per Room 1
|  | Room 3 |  | Same as per Room 1
|  | Room 4 |  | Same as per Room 1
|  | Room 5 |  | Same as per Room 1
|  | Room 6 |  | Same as per Room 1
Emergency Lighting
|  | Room 1 |  | QA_TEM_023_Emergency & Exit Lighting
|  | Room 2 |  | QA_TEM_023_Emergency & Exit Lighting
|  | Room 3 |  | QA_TEM_023_Emergency & Exit Lighting
|  | Room 4 |  | QA_TEM_023_Emergency & Exit Lighting
|  | Room 5 |  | QA_TEM_023_Emergency & Exit Lighting
|  | Room 6 |  | QA_TEM_023_Emergency & Exit Lighting

## Project Structure 00594
Folder Structure |  |  |  |  | Checklists
Site QA
Electrical
Switchboards
MDB-A
|  |  |  | Mains & Submains Installation | QA_TEM_011_Mains & Submains Installation
|  |  |  | Switchboard & DB Installation | QA_TEM_012_Switchboard & Distribution Board Installation
|  |  |  | Switchboard & Distribution Board Assembly | QA_TEM_013_Switchboard & Distribution Board Assembly
|  |  |  | Cable Terminations | QA_TEM_014_Cable Terminations
|  |  |  | Rough In | QA_TEM_042_Rough In Checklist
|  |  |  | Fit Off | QA_TEM_043_Fit Off Checklist
|  |  |  | Power Commissioning | QA_TEM_041_Power Cable Commissioning
|  |  |  | Final Sub Circuit | QA_TEM_010_Final Sub Circuit Installation
DB-BOP
|  |  |  | Mains & Submains Installation | QA_TEM_011_Mains & Submains Installation
|  |  |  | Switchboard & DB Installation | QA_TEM_012_Switchboard & Distribution Board Installation
|  |  |  | Switchboard & Distribution Board Assembly | QA_TEM_013_Switchboard & Distribution Board Assembly
|  |  |  | Cable Terminations | QA_TEM_014_Cable Terminations
|  |  |  | Accessories Installation | QA_TEM_015_Accessories Installation
|  |  |  | Light Fitting Installation | QA_TEM_016_Light Fitting Installation
|  |  |  | LCP's & Field Devices | QA_TEM_018_LCP's & Field Devices
|  |  |  | Control Cables | QA_TEM_022_Control Cables
|  |  |  | Emergency & Exit Lighting | QA_TEM_023_Emergency & Exit Lighting
|  |  |  | Lighting Rough In | QA_TEM_042_Rough In Checklist
|  |  |  | Power Rough In | QA_TEM_042_Rough In Checklist
|  |  |  | Lighting Fit Off | QA_TEM_043_Fit Off Checklist
|  |  |  | Power Fit Off | QA_TEM_043_Fit Off Checklist
|  |  |  | Power Commissioning | QA_TEM_041_Power Cable Commissioning
|  |  |  | Multi Core Cable Commissioning | QA_TEM_040_Multi-Core Cable Commissioning
|  |  |  | Final Sub Circuit Installation | QA_TEM_010_Final Sub Circuit Installation
Cable Tray
Area 1
|  |  |  | Cable Support Prior to Cabling | QA_TEM_008_Cable Support Prior to Cabling
|  |  |  | Cable Support Post Cabling | QA_TEM_009_Cable Support Post Cabling
Conduit Installation
|  |  | Area 1 |  | QA_TEM_006_Surface Conduit Installation
Temporary Services
Temp DB 1
|  |  |  | August 2023 | QA_TEM_063_Construction Distribution Boards
|  |  |  | September 2023 | QA_TEM_063_Construction Distribution Boards
|  |  |  | October 2023 | QA_TEM_063_Construction Distribution Boards
|  |  |  | November 2023 | QA_TEM_063_Construction Distribution Boards
Communications
|  | Rough In |  |  | QA_TEM_042_Rough In Checklist
|  | Fit Off |  |  | QA_TEM_043_Fit Off Checklist
|  | Data & Comms Cabling |  |  | QA_TEM_025_Data & Communications Cabling
|  | Cable Terminations |  |  | QA_TEM_014_Cable Terminations
|  | Final Sub Circuit Installation |  |  | QA_TEM_010_Final Sub Circuit Installation

## Checklists
type | name | values
checklist | QA_TEM_003_Earth Electrode
checkpoint | Record electrode type and size (AS/NZS 3000 Table 5.2)
text | Material
text | Diameter
checkpoint | Earth electrode is driven to the minimum depth (AS/NZS 3000 5.3.6.3)
bool | Vertical type - 1.2 metres
bool | Strip type - 3 metres
checkpoint | Earth electrode is installed in a correct location (AS/NZS 3000 5.3.6.4)
label | External to the building in ground that is exposed to the weather
label | Separated from conductive enclosures of other buried services
label | Is in an accessible location
checkpoint | Earth electrode is mechanically protected and labelled in accordance with AS/NZS 3000 5.5.1.3
label | WARNING MAIN ELECTRICAL EARTHING CONDUCTOR—DO NOT DISCONNECT
checkpoint | Earth connection point to stake is protected from corrosion (i.e. painted earth clamp) (AS/NZS 3000 5.5.5.3)
checkpoint | Location of the earth electrode has been identified at the main switchboard.
checkpoint | If measurement of the resistance of the earth electrode is requested, refer to the test procedure detailed in AS/NZS 3017 clause 3.8.
checklist | QA_TEM_006_Surface Conduit Installation
checkpoint | Conduits are the correct type
checkpoint | Conduits are following the approved route as specified
checkpoint | Conduits are straight plumb/parallel
checkpoint | Conduits have sharp edges and burrs removed (steel)
checkpoint | Conduits have expansion joints installed where required
checkpoint | Conduits have specified support installed
checkpoint | Conduits have product branding cables removed or not visible
checkpoint | Conduits are sealed against water ingress where required
checkpoint | Conduits have equipment entries correctly sealed
checklist | QA_TEM_008_Cable Support Prior to Cabling
checkpoint | Cable support has correct origin and destination
checkpoint | Cable support follows correct route
checkpoint | Cable support is correct type material and not damaged
checkpoint | Cable support is correctly aligned
checkpoint | Cable support has correct type/quantity supports
checkpoint | Cable support is attached securely to supports
checkpoint | Cable support has correct type and size of fittings
checkpoint | Cable support is complete for the entirety of its length
checkpoint | Cable support has correct segregation
checkpoint | Cable support is earthed correctly
checklist | QA_TEM_009_Cable Support Post Cabling
checkpoint | Cable support is properly sealed at all penetrations
checkpoint | Cable support has divider strip if required
checkpoint | Cable support has cover fitted if required
checkpoint | Cable support has correct segregation
checklist | QA_TEM_010_Final Sub Circuit Installation
checkpoint | Cable has correct origin and destination
checkpoint | Cable has correct number of cores
checkpoint | Cable cores are of the correct cross sectional area
checkpoint | Cable type and configuration is as specified
checkpoint | Cable follows the correct route
checkpoint | Cable meets minimum bending radius requirements
checkpoint | Cable is clear of heat sources
checkpoint | Cable is clear of electronic / signal cables
checkpoint | Cable is secured as specified
checkpoint | Cable is installed in a neat and orderly manner
checkpoint | Cable is routed to minimise crossovers
checkpoint | Mechanical protection of cable is correct
checkpoint | Cable is supported correctly
checkpoint | Cable is marked with cable or circuit number
checkpoint | Cable has correct segregation
checklist | QA_TEM_011_Mains & Submains Installation
checkpoint | Cable is in good condition and free from damage and defects
checkpoint | Cable has correct origin and destination
text | Origin
text | Destination
checkpoint | Cable Type, Number of Cores, Size and Configuration is as specified
text | Size (mm2)
text | Cores
text | Cable Type
text | Earth Size (mm2)
text | Cores
text | Cable Type
checkpoint | Bending radius recommended by the cable manufacturer has been observed
text | Bending Radius (mm)
label | Where manufacturer’s information is not available, the following minimum internal radii may be considered suitable
label | Unarmoured sheathed cables = 6 times the cable diameter
label | Armoured sheathed cables = 12 times the cable diameter
checkpoint | Cable follows the correct route
checkpoint | Cable is clear of heat sources
checkpoint | Cable is segregated from telecommunications cables by either a continuous barrier or separated by at least 50mm - AS/NZS 3000 Clause 3.9.8.4 (c).
checkpoint | Cable is secured and mechanically protected (where required).
checkpoint | Cable is marked with cable or circuit number
checklist | QA_TEM_012_Switchboard & Distribution Board Installation
section | Check that the switchboard
checkpoint | Is the correct unit
checkpoint | Is located in the correct position
checkpoint | Has correct clearances on all sides
checkpoint | Is properly secured
checkpoint | Is labelled correctly
checkpoint | Is fitted with correct types, ratings and quantities of functional units
checkpoint | All escutcheons and cover plates are fitted
checkpoint | Finishes are as specified
section | Check each functional unit for
checkpoint | Correct labelling
checkpoint | Check all cable terminations are secured correctly & tensioned as per switchboard manufacturers advice
checkpoint | Check all busbar connections are secured correctly & tensioned as per switchboard manufacturers advice
checkpoint | Check cubicle has been cleaned of all rubbish, dust, filings, tools, etc.
checkpoint | Check for presence of properly completed circuit
checkpoint | Schedule/single line diagram
checklist | QA_TEM_013_Switchboard & Distribution Board Assembly
section | Built as per plans
checkpoint | Main Switch
text | Correct Size, Rating & Type
checkpoint | Isolators
text | Correct Size, Rating & Type
checkpoint | Circuit Breakers
text | Correct Size, Rating & Type
checkpoint | Cable Size
text | Correct Size, Rating & Type
checkpoint | CT's
text | Correct Size, Rating & Type
section | Visual Check
checkpoint | Escutcheons Fitted Correctly
checkpoint | Gland Plates Fitted Correctly
checkpoint | All Locks Fitted correctly, operation and keys incl.
checkpoint | Earth straps fitted correctly
checkpoint | Labels
bool | Main Switch
bool | Isolators
bool | Strip Labels
bool | Earthing & Neutral Bars
bool | Meters
section | Cables
checkpoint | Terminated & Tensioned
checkpoint | Neutrals - Correct terminal and number
checkpoint | Bend Radius as per AS 3000
checkpoint | Correctly Labelled
section | Testing (as per QA_FRM_005_Final Installation Test Sheet)
checkpoint | 3 ø Board @ 1000V
checkpoint | 1 ø Board @ 500V
checkpoint | Point to Point - Control Circuits
checkpoint | Correct Operation of Control Circuits
section | Cabinet
checkpoint | Correct Finish
checkpoint | Correct Size
checkpoint | Clean & damage free
checklist | QA_TEM_014_Cable Terminations
checkpoint | Correct type and size gland
checkpoint | Gland properly and securely fitted
checkpoint | Correct cable identification
checkpoint | Correct core identification
checkpoint | Cores loomed properly
checkpoint | Cores on correct terminals
checkpoint | Terminals properly tensioned
checkpoint | Cores correctly lugged
checkpoint | Lugs correctly insulated
checkpoint | Adequate clearances
checklist | QA_TEM_015_Accessories Installation
checkpoint | Accessories are the correct type
checkpoint | Accessories are located in the correct position
checkpoint | Accessories are securely fitted
checkpoint | Accessories are fitted in accordance with manufacturers recommendation
checkpoint | Accessories are plumb & level parallel
checkpoint | Accessories are sealed correctly
checklist | QA_TEM_016_Light Fitting Installation
checkpoint | Fitting/s are the correct type
checkpoint | Fitting/s are located in the correct position
checkpoint | Fitting/s are securely fitted
checkpoint | Fitting/s are fitted with correct lamps
checkpoint | Fitting/s accessories fitted in accordance with manufacturers recommendation
checkpoint | Fitting/s are damage free
checkpoint | Fittings/s have correct termination
checklist | QA_TEM_017_Fire Sealing
checkpoint | Covers are 1.6mm minimum galvanised sheet metal
checkpoint | Fire proof material is in place to comply with AS 3000 & the Building Act
checkpoint | Plastic grommet is around metal edges bearing against cable
checkpoint | Sheet metal covers are painted to match surrounds
checkpoint | Proprietary fire barriers to comply with the Building Act in lieu of above
checklist | QA_TEM_018_LCP's & Field Devices
checkpoint | Installation/s are the correct type
checkpoint | Installation/s are located in the correct position
checkpoint | Installation/s are properly secured
checkpoint | Installation/s are correctly labelled or identified
checkpoint | Installation/s are assembled correctly
checkpoint | Check all functions for correct operation
checkpoint | Check that the support stand or bracket is
bool | The correct type
bool | Properly secured
checkpoint | Check that all unused entries have been properly sealed against ingress of dust, solids, or liquids
checkpoint | Confirm that the whole unit/s has been installed in a workmanlike manner
checklist | QA_TEM_022_Control Cables
checkpoint | Type and configuration is as specified
checkpoint | has correct origin and destination
checkpoint | has correct number of cores
checkpoint | cores are of correct Cross Sectional Area
checkpoint | follows the correct route
checkpoint | meets minimum bending radius requirements
checkpoint | is clear of heat sources
checkpoint | is clear of power cables
checkpoint | is secured as specified
checkpoint | is installed in a neat and orderly manner
checkpoint | is routed to minimise crossovers
checkpoint | mechanical protection is correct
checkpoint | inter cable spacing/segregation is correct
checkpoint | cable is correctly supported
checkpoint | cable marked with cable number
checklist | QA_TEM_023_Emergency & Exit Lighting
checkpoint | Fitting/s are the correct type
checkpoint | Fitting/s are located in the correct position
checkpoint | Fitting/s are securely fitted
checkpoint | Fitting/s are fitted with correct lamps
checkpoint | Fitting/s accessories fitted in accordance with manufacturers recommendation
checkpoint | Fitting/s are compliant with specification
checkpoint | Fitting/s are correctly identified
checkpoint | Fittings/s are tested to AS 2293 Emergency escape lighting and exit signs for buildings
checkpoint | Log book is completed and copy on-site
checkpoint | Log book ID number and as-installed drawing/s match
checkpoint | Exit sign/s visible
checkpoint | correct operation
checklist | QA_TEM_025_Data & Communications Cabling
checkpoint | Check that cable to be installed matches Job Spec Requirement ie. Brand and Class
checkpoint | Check that all cable pathways comply with ACA and Vendor requirements
checkpoint | Install cables, making sure of all strain and bend radius requirements, label cables correctly
checkpoint | Bundle sizes to be checked to Specification and number of cables not exceeded
checkpoint | Cables to be tied in with Velcro as per specified distance between ties
checkpoint | All Clearances between power and other services to be maintained as per requirements
checkpoint | When cable is installed into wall cavity, Corro should be used to maintain support and bend radius
checkpoint | Corrugated conduit to be extended to outlet position if segregation is required from power in same cavity
checkpoint | Sort cables into correct Patch Panel Groups for looming into Data Cabinet/Frame
checkpoint | Loom cables into Data Cabinet being sure that they are supported properly and bend radius is correct
checkpoint | Terminate cables on Patch Panels/frames adhering to all regulations for the particular cable and Vendor
checkpoint | Label all Patch panels and Racks as required
checkpoint | Check position of outlets on Architectural plans if available
checkpoint | Terminate cables in the field as per regulations and Vendor requirements
checkpoint | Label all field outlets correctly
checkpoint | Test Cables to the relevant standards and Vendor requirements
checkpoint | Fill in record books if required, Check asbuilt plans and modify if necessary
checkpoint | Supply test results and as-installed drawing/s
checklist | QA_TEM_030_Security Inspection
checkpoint | Check TDCs for correct type (T), position (P), clearances (C), & attachment (A):
bool | T
bool | P
bool | C
bool | A
checkpoint | Check Expanders for correct type (T), position (P), clearances (C), & attachment (A):
bool | T
bool | P
bool | C
bool | A
checkpoint | Check Main Panels for correct type (T), position (P), clearances (C), & attachment (A):
bool | T
bool | P
bool | C
bool | A
checkpoint | Check Electric Locks for correct type (T), position (P), clearances (C), & attachment (A):
bool | T
bool | P
bool | C
bool | A
checkpoint | Check Proximity Points for correct type (T), position (P), clearances (C), & attachment (A):
bool | T
bool | P
bool | C
bool | A
checkpoint | Check Single Door Controllers for DOTL (D), Forced Doors (F), Prox operation (P), & Lock activation (L):
bool | D
bool | F
bool | P
bool | L
checkpoint | Check Two Door Controllers for DOTL (D), Forced Doors (F), Prox operation (P), & Lock activation (L):
bool | D
bool | F
bool | P
bool | L
checkpoint | Check Four Door Controllers for DOTL (D), Forced Doors (F), Prox operation (P), & Lock activation (L):
bool | D
bool | F
bool | P
bool | L
checkpoint | Check Active Panels Timezones (T), Holidays (H), Auxilleries (AU), Automation (A):
bool | T
bool | H
bool | AU
bool | A
checkpoint | Check Single Door Controllers Timezones (T), Holidays (H), Auxilleries (AU), Automation (A):
bool | T
bool | H
bool | AU
bool | A
checkpoint | Check Two Door Controllers Timezones (T), Holidays (H), Auxilleries (AU), Automation (A):
bool | T
bool | H
bool | AU
bool | A
checkpoint | Check Four Door Controllers Timezones (T), Holidays (H), Auxilleries (AU), Automation (A):
bool | T
bool | H
bool | AU
bool | A
checkpoint | Check activation of Door Reed Switches
checkpoint | Check activation of Intruder Detectors
checkpoint | Check that all cables are the correct type, size, configuration, length & quantity
checkpoint | Visually check all terminations for correct colour codes and acceptable looming
checklist | QA_TEM_033_Control Cable Point to Point Testing
checkpoint | Continuity test of each & every individual core
text | Earth
text | 1
text | 2
text | 3
text | 4
text | 5
text | 6
text | 7
text | 8
text | 9
text | 10
text | 11
text | 12
text | 13
text | 14
text | 15
text | 16
text | 17
text | 18
text | 19
text | 20
checklist | QA_TEM_035_Multi-Core Point to Point Testing
checkpoint | Continuity test of every core
text | Earth
text | Core 1
text | Core 2
text | Core 3
text | Core 4
text | Core 5
text | Core 6
text | Core 7
text | Core 8
text | Core 9
text | Core 10
text | Core 11
text | Core 12
text | Core 13
text | Core 14
text | Core 15
text | Core 16
text | Core 17
text | Core 18
text | Core 19
text | Core 20
text | Core 21
text | Core 22
text | Core 23
text | Core 24
text | Core 25
checklist | QA_TEM_036_Power Cable Point to Point Testing
checkpoint | Continuity test of each & every individual core
text | Earth 1
text | Earth 2
text | Earth 3
text | Screen
text | Neutral
text | Phase A
text | Phase B
text | Phase C
checklist | QA_TEM_037_Install Field Instruments
section | Check that all Instruments are:
checkpoint | the correct type
checkpoint | located in the correct position
checkpoint | properly secured
checkpoint | correctly labelled or identified
checkpoint | Check that the support stand or bracket is:
bool | the correct type
bool | properly secured
section | Check that the instrument air is:
checkpoint | connected correctly to the instrument
checkpoint | connected correctly to its supply point
checkpoint | adequately secured along its length
checkpoint | Check that all unused entries have been properly sealed against the ingress of dust, solids, or liquids
checkpoint | Confirm that the whole unit has been installed in a workmanlike manner
checklist | QA_TEM_040_Multi-Core Cable Commissioning
section | Cable Install
checkpoint | Type, configuration, number of cores & cross sectional area is as specified
checkpoint | Cable has correct origin and destination & follows the correct route
checkpoint | Meets minimum bending radius requirements with minimal crossovers
checkpoint | Is clear of heat sources with mechanical protection fitted if required
checkpoint | Is secured properly & correctly supported as specified
checkpoint | Is installed in a neat & orderly manner with inter cable spacing/segregation
section | Origin Termination, Location
checkpoint | Gland is correct type & size, & also fitted & secured properly
checkpoint | Cable numbers fitted correctly & securely
checkpoint | Cores loomed neatly with correct identification
checkpoint | Cores in the correct terminals & correctly tensioned
checkpoint | Cores correctly lugged & insulated
section | Destination Termination, Location
checkpoint | Gland is correct type & size, & also fitted & secured properly
checkpoint | Cable numbers fitted correctly & securely
checkpoint | Cores loomed neatly with correct identification
checkpoint | Cores in the correct terminals & correctly tensioned
checkpoint | Cores correctly lugged & insulated
section | Testing
checkpoint | Point to Point, Continuity test of each core
bool | Earth
bool | Core 1
bool | Core 2
bool | Core 3
bool | Core 4
bool | Core 5
bool | Core 6
bool | Core 7
bool | Core 8
bool | Core 9
bool | Core 11
bool | Core 12
bool | Core 13
bool | Core 14
bool | Core 15
bool | Core 16
bool | Core 17
bool | Core 18
bool | Core 19
bool | Core 20
checklist | QA_TEM_042_Rough In Checklist |  | Require 72 Circuits in Sections (ie. Circuit 1, Circuit 2 etc.
section | Inspection 1
checkpoint | Has all information been recorded and checks completed?
text | Circuit ID
text | Cable Size/Type
text | Number of Points
bool | Feeds - Visual Check - All feeds have been roughed in
bool | Feeds - Identification - All feed cables have been identified/marked
bool | 1st Rough In - Visual Check - All cable loops have been roughed in
bool | 1st Rough In - Identification - All cable loops have been identified/marked
bool | 2nd Rough In - Visual Check - All cable loops have been positioned and ready for fit off
bool | 2nd Rough In - Final Check - Ensure cable is appropriately identified and made safe, if required
Require 72 Circuits in Sections (ie. Circuit 1, Circuit 2 etc.
checklist | QA_TEM_043_Fit Off Checklist
section | Inspection 1
checkpoint | Has all information been recorded and checks completed?
text | Circuit ID
text | Number of Points
bool | Fit Off - Visual Check - All points have been fit off/terminated
bool | Fit Off - Identification - Ensure cable is appropriately identified, post termination
bool | Final Check - All fit off complete, ready for switchboard termination
checklist | QA_TEM_063_Construction Distribution Boards
checkpoint | AS/NZS 3012:2019 - 2.3.1.1 - The distribution board is legibly and indelibly marked to identify the source of supply from which it originates. (min 6mm letters)
checkpoint | AS/NZS 3012:2019 - 2.3.1.1 - The distribution board shall be readily accessible and protected from damage.
checkpoint | AS/NZS 3012:2019 - 2.3.1.2 - The distribution board shall be positioned in a manner that eliminates the need for leads to be run between levels.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (a & b) - The distribution board is of robust construction with a minimum IP 23 rating.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (c) - Live parts are eﬀectively protected at all times against contact by personnel operating equipment located on the distribution board, including the connection or disconnection of plugs to socket-outlets.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (c) - All penetrations are closed oﬀ, with propriety fittings, i.e. bungs & lock rings for unused penetrations and pole fillers for unused circuit breaker poles.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (d) - An insulated tie bar is fitted for extension leads to prevent strain on socket/outlets.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (e) (i) - The door or lid requires the use of tool for removal.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (e) (ii) - The door or lid is fitted with a facility for locking.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (e) (iii) - The door or lid shall be fitted with means of retention in the open position.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (e) (iv) - The door or lid shall not damage leads and allow the safe entry of leads.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (e) (v) - A clearly visible and legible sign shall be fixed on the external surface. "KEEP CLOSED - RUN ALL LEADS THROUGH BOTTOM"
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (f) - Distribution board is clearly labelled to distinguish one board from another. (by means of numbers, letters or both)
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (g) - Switchboards is marked in accordance with appendix C to indicate presence of live parts.
checkpoint | An electric shock risk sign is displayed in locations where additional attention is required in the removal of covers, e.g. covers for switchboards or cable junctions.
checkpoint | A danger sign with an additional message indicating the presence of live parts within, is conspicuously displayed on the enclosure.
checkpoint | AS/NZS 3012:2019 - 2.3.3 - Distribution board is securely fixed in position, attached to a pole, post, wall, floor. (if it is not fixed down for any reason the board should not be in service)
checklist | QA_TEM_041_Power Cable Commissioning
section | Cable Install
checkpoint | Confirm cable type, configuration, number of cores & cross sectional area is as specified
checkpoint | Confirm cable has correct origin and destination & follows the correct route
checkpoint | Confirm cable meets minimum bending radius requirements with minimal crossovers
checkpoint | Confirm cable is clear of heat sources with mechanical protection fitted if required
checkpoint | Confirm cable is secured properly & correctly supported as specified
checkpoint | Confirm cable is installed in a neat & orderly manner with inter cable spacing/segregation
section | Origin Termination / Location
checkpoint | Confirm gland is correct type & size, & also fitted & secured properly
checkpoint | Confirm cable numbers fitted correctly & securely
checkpoint | Confirm cores loomed neatly with correct identification
checkpoint | Confirm cores in the correct terminals & correctly tensioned
checkpoint | Confirm cores correctly lugged & insulated
section | Origin Termination / Location
checkpoint | Confirm gland is correct type & size, & also fitted & secured properly
checkpoint | Confirm cable numbers fitted correctly & securely
checkpoint | Confirm cores loomed neatly with correct identification
checkpoint | Confirm cores in the correct terminals & correctly tensioned
checkpoint | Confirm cores correctly lugged & insulated
section | Testing
checkpoint | Point to point / Continuity of each core
bool | Earth
bool | Red
bool | White
bool | Blue
bool | Black
checkpoint | Insulation Resistance Test (results recorded on QA_FRM_005_Final Installation Test Sheet)