## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat | 8fc28b2c-6c1d-421b-ab41-3f08c172330c |  | checklist | HW Hot Water Meters |  |  |  |  | Yes | HW Hot Water Meters | 02769bc8-0090-441f-a113-1a427ce9862d
checkpoint-status | 802155b8-2bfd-4e2f-a54f-b7f2cc6fddee |  | checkpoint | Water Meter Details:
text | 7a8f0fa3-09ff-5386-aea8-5c554e27b47a |  | textbox | Meter No:
text | da1827b2-c38d-5a27-a9d3-b2bb4a6ce9c5 |  | textbox | Level:
text | 084adfeb-a922-5893-96f0-36a4e95634eb |  | textbox | Meter Size:
checkpoint-status | 865686b3-7f20-4819-b1f8-618084362348 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 233baefe-8f17-45e4-b43c-5a5383cbfe79 |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | b49f6498-3324-496c-8d70-dec8df4d4a69 |  | checkpoint | Meter bracketed
checkpoint-status | b374331c-ceee-4c56-82dc-4c9c250b5df0 |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | ab99a934-d9c6-4984-9efe-0ceb8f0f9754 |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | b7e5fe72-a082-437d-a24a-d14605e79293 |  | checkpoint | Pulse rate value is correct
checkpoint-status | eab3f7ae-5e5b-48d3-813f-9de02805b0bf |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | d724a9a7-4279-4880-91c9-245d5f4bff46 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | d01b471e-96b2-42f9-a72f-a048c7453090 |  | checkpoint | Flow direction is correct
checkpoint-status | 444a473e-e2e1-4600-a2f2-40657adee01d |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 36b8d63c-3ef9-467a-8f18-3ac985c4d44e |  | checkpoint | Record installation by photo & time/date
checkpoint-status | 5416713a-3295-40ea-ba3e-151726e35bb5 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 27ad5f32-a25f-4e86-be79-14d9a7ae076c |  | checklist | RW Rough-in (High Level) |  |  |  |  | Yes | RW Rough-in (High Level) | 09f16d52-3839-47c6-8057-7ecfee02b604
checkpoint-status | 12ba887c-ea5f-45e1-9ea4-1dbdf9cb192b |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 6e202e1b-2ed8-4777-b21c-5ce293311c2e |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | b758d218-d16a-4ab4-83d5-d7b2512577bf |  | checkpoint | Pipe materials are correct for application
checkpoint-status | abebe7fc-d0f8-4ae3-8875-0ef10fb2db34 |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | fe2e0211-52c6-4512-937f-f0771519e166 |  | checkpoint | Check silicone applied to studs
checkpoint-status | 801c705b-cf4e-40aa-9585-41a418787815 |  | checkpoint | Check for possible cross connections
checkpoint-status | ad2837f4-62c2-4fb6-8007-9b5e12ec6dbd |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | 0dc25855-7d1f-4841-a0cf-722314d2f096 |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status | 88fa9e07-d745-4d56-a645-dbcfe3bcf33b |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | e8371e92-d6a3-471b-9994-8685c63eb53c |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | b5b7a32c-8b08-495c-be0b-df5b8d0ca721 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 30dc31fa-9827-4860-8979-076aa2ba6102 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 0df79968-e9eb-4ced-bf29-456c837f9860 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 2c955d87-c17d-4214-93b2-71ecca366047 |  | checklist | RW Risers (Pumped or Mains Pressure Risers) |  |  |  |  | Yes | RW Risers (Pumped or Mains Pressure Risers) | 0d50bbf2-fe47-485b-8440-ecc796691b71
checkpoint-status | 83480c04-bfcd-481c-8262-0fd484a537c5 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 84f8d95f-3095-4847-bb12-259dbedd1cd8 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 85d5da0f-2d08-4568-a428-e9ff0d623e26 |  | checkpoint | Penetrations are installed
checkpoint-status | 7c7c6d42-99d5-46d7-892c-67f3ae1d8c1c |  | checkpoint | Pipe materials are correct for application
checkpoint-status | afd38a27-0eba-43eb-8920-7cd28c001133 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 7c354e53-633b-43ae-847d-d9bb16c47423 |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 1dda99b1-4649-420f-81db-8e849f126760 |  | checkpoint | Ensure all risers are installed professionally with no abnormalities
checkpoint-status | b712ca53-996a-44fe-a62f-1e9bc08fbe5f |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | d4c4e7f5-ad4b-4678-9a74-4a73cbc7f701 |  | checkpoint | Welded pipe joints are completed
checkpoint-status | 88a3bf3a-8c4e-4437-9ac4-e609df66e0a5 |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | 34f18272-db06-4a70-a20a-b6d858e7ea89 |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | 464bc64e-42f8-43b8-8593-da910f1725fa |  | checkpoint | Pipe penetrations are caulked
checkpoint-status | 6cd8e533-35d5-4e98-b41b-ce8e9f387dea |  | checkpoint | Anchors are installed as per manufacturer instructions & compliant with AS3500
checkpoint-status | 6615a1d7-deb8-41ef-85f3-e24625997920 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 49b51fa2-fed5-4cf7-9d31-f280b7575b01 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 961ccab6-2b7f-48b2-a544-3437991c0d79 |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | caabce3d-bb48-43f3-bb70-b0eb6e8d9c17 |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | 5d858f45-e4ee-4767-a2b6-839789adfd55 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | d91e437c-017b-4837-a0d9-437a1c546ae0 |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status | 40fc0389-d486-4290-88f4-3ec61c375874 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 56c18991-2bc6-4eb0-bb63-dfeff55a54d7 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 8d882aa4-56ab-4fba-ad4b-b615a6360341 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | fae1b1ef-b42a-431e-9b07-ebaa9781b6a4 |  | checklist | HW High Level/Corridors |  |  |  |  | Yes | HW High Level/Corridors | 0d9ada3b-543e-4463-bea8-a5ff876c577d
checkpoint-status | 35ab1971-da0e-43d0-a541-9ccdf8017500 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 898312af-4045-4f02-aa4e-1310b2680d5d |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | e9516ffc-ef1c-48c8-bd09-719dffef3992 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 2e0b053b-571c-4a91-94ed-45398344ee84 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 5afee796-a94a-4ac7-a58b-30d625094c7b |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 7c45c6e9-2c74-4faa-9737-80e667fd3de7 |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | 6f28991a-1e5e-4857-8a35-8055aece7599 |  | checkpoint | Welded pipe joints are completed
checkpoint-status | af16468e-310f-4796-9201-583e0d35528b |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | e33a78be-938d-4f3a-8501-38140621d09c |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | 6834cc92-c14e-4ac8-b25c-00b6a1d6213f |  | checkpoint | Meter manifolds & frames are firmly bracketed & installed in sizes, quantities & locations as per design
checkpoint-status | 474a608d-878a-4a8c-8db3-236ecea8e5a6 |  | checkpoint | PR valves are installed. Pressure rate & flow correct
checkpoint-status | 052db33a-1f32-477f-8459-358600901ed6 |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | 01c5f481-e0ea-4e3c-b4be-cbb9338c9b11 |  | checkpoint | Balancing valves are installed & flow correct
checkpoint-status | 5af5ae73-ed0e-488d-a16c-8500390369d6 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | e95f5a71-be5d-49bc-88a8-661d275f5cc5 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 7461b8f8-e850-4162-8e54-beeb121c436d |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | dae9297f-25fc-4610-98a8-3b24c9d2a19e |  | checkpoint | Heat trace installed if required
checkpoint-status | 360af0a5-f1d9-4030-affa-0cc293a1fe65 |  | checkpoint | Thermal insulation installed & correct weight as designed
checkpoint-status | 3f8d7357-5c89-4eea-ac29-da3cf2751a45 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 9f6f35b9-36a5-4619-a29c-438cde20398f |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 96110f71-4c63-4e1e-9e96-1549a3bb285d |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | bc7a3210-ff76-4a24-a7cb-4860c3aefc3f |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 69e6bca9-15ed-42f8-8d9d-d6111c697916 |  | checklist | 10.6 NG Purging of Consumer Fitting Line |  |  |  |  | Yes | 10.6 NG Purging of Consumer Fitting Line | 1614960e-9aad-4867-ac7c-0cc1d443029d
checkpoint-status | 66278665-796c-415d-8c12-2e5303fc5afc |  | checkpoint | Complies with requirements of either AS3500 and AS5600.1
checkpoint-status | 88029b1d-440e-45d4-8150-6a968185503f |  | checkpoint | Complies with the latest IFC specifications & drawings
checkpoint-status | cdaf51e8-01ba-4d92-9968-5347b10525f5 |  | checkpoint | A "Tool Box" meeting to be held on the morning of the meter installation date to define personnel rolls & responsibilities
checkpoint-status | 08fd0aef-9c95-4d9b-914f-585494546b6a |  | checkpoint | Select the purge areas and ensure no ignition sources are within these areas
checkpoint-status | 3a9154ca-4b13-47f2-89b6-144dec01ed77 |  | checkpoint | Prominently display warning signs surrounding the purge areas
checkpoint-status | ebc03ad5-12ee-4548-9775-89e376a2b482 |  | checkpoint | A purge stack or purge bucket must be available and operated by one designated team member
checkpoint-status | 2908574d-94de-448e-bdc7-c196efc963d0 |  | checkpoint | Provide suitable fire-extinguishers within the purge venting areas
checkpoint-status | c0397de5-ea6e-4543-9c50-9d82099f3359 |  | checkpoint | Nitrogen and connection equipment is available for the purge
checkpoint-status | 48997309-917c-4606-a6b5-1604c4aee5e0 |  | checkpoint | Ensure personnel are familiar with operation of the fire-extinguishers
checkpoint-status | b6c87043-e0a6-4c38-922e-eb3cc3951c1b |  | checkpoint | All electronic equipment to be used in the purge area must be rated as "electromagnetically safe"
checkpoint-status | 2da4e964-42ad-44c7-8200-d3b6d6535bfa |  | checkpoint | The team leader is to remain in the gas meter room to control & oversee proceedings
checkpoint-status | 7d18d79b-bd59-4923-96fc-b47e21472be5 |  | checkpoint | Reliable two-way radio devices are to be issued to all personnel as the means of primary communication
checkpoint-status | dde21088-993d-49eb-bb96-d59c48e56b92 |  | checkpoint | Hydraulic Services contractor to purge all air from the consumer line using nitrogen until air is displaced with a nitrogen plug
checkpoint-status | 0a87032a-10ba-4dc3-8fdf-d33a4263d107 |  | checkpoint | ESVs' meter contractor is instructed that all is in readiness for the commencement of his works
checkpoint-status | 0a32d802-8a49-46a1-8c61-d9b4dd6845d9 |  | checkpoint | ESVs' meter contractor fits the meter in position and immediately commences the purging & calibration of his meter
checkpoint-status | 8631ff9d-585e-4d9a-9744-1dfc6eb020b2 |  | checkpoint | At this stage only a minor amount of nitrogen gas will be displaced for venting in the purge areas
checkpoint-status | c5278c56-34c5-4794-8dd5-4afdc2d39b57 |  | checkpoint | Following the successful installation & calibration of the meter, the ESV contractors' engagement is complete
checkpoint-status | 0b1bc146-01e4-46c3-88f4-2d71614aaee0 |  | checkpoint | The Hydraulic Services team now takes over and commences the consumer fitting line primary purge
checkpoint-status | c4d923e3-a4c2-4d31-ad61-4bea1ffc6fda |  | checkpoint | Calculate the volume of the main run of pipe before commencing the purge (Re: ESV GIS No: 14 - Table 1 and the example in Appendix 2). Observing the volume passing through the meter will indicate when gas is expected to flow through the purge stack or the purge bucket.
checkpoint-status | 78ad7dc7-7b07-4ced-bd62-ff6dd8411acb |  | checkpoint | Note the gas meter test dial position for indication of the flow rate
checkpoint-status | da86de99-8c39-4558-b21e-d73e3324e842 |  | checkpoint | A purge stack or purge bucket has previously been connected to the further most point of the consumer fitting line
checkpoint-status | a2093032-9c4d-4680-859d-e5832da0e3e2 |  | checkpoint | Carefully open the primary gas control valve & commence the purging process
checkpoint-status | 36664ca5-1cab-4faf-b33b-9c32088fc11e |  | checkpoint | Ensure the maximum purge pressure is not exceeded (Pressure is labelled on fitting line)
checkpoint-status | 39e12e45-b44b-40ea-808f-67f8908d91b8 |  | checkpoint | Continue to purge through the purge stack or purge bucket until natural gas is commences being presented
checkpoint-status | 63771ff4-1bdf-46fa-93d2-89eab44336ae |  | checkpoint | Take a sample from the purge stack or purge bucket sampling point using a suitable gas detector (minimum acceptable reading 95% gas).
checkpoint-status | c13f46f9-78b7-43ea-85b7-200e4f6fcf14 |  | checkpoint | An indication that the purging of natural gas is nearing completion is seen when mass gas aeration evacuates from the purge bucket and proceeds to disperses.
checkpoint-status | 8f220191-fa88-4756-8a9a-808ec4e95e9c |  | checkpoint | Continue purging & testing until an acceptable reading on the gas detector is obtained
checkpoint-status | a9f7ae77-0e37-4ce0-95c3-5bf3efd0052a |  | checkpoint | When the correct test result is obtained, purging of this section will be complete.
checkpoint-status | 5889495a-8583-4f46-bf05-8e91dbf38ebb |  | checkpoint | Relieve the pressure in the purge hose by opening the purge stack main valve.
checkpoint-status | f7cba317-6de5-4625-ad0b-89fcf3b04cca |  | checkpoint | Disconnect the purge hose and the hose inlet valve from the installation. Cap & seal the fitting line immediately to avoid gas escaping and air re-entering the line.
checkpoint-status | ff5ea3a6-40af-47a0-95a7-0f9c0162f20c |  | checkpoint | Transfer the purge stack or purge bucket and hose to the end of the branch nearest the meter and repeat the procedure.
checkpoint-status | 6c223fc1-a108-4af5-a545-14939a78b766 |  | checkpoint | Continue purging all branches, moving away from the meter, until the whole installation is filled with gas.
checklist-flat | c3a7dd80-2927-4b59-97ca-b03a30e3b4f4 |  | checklist | FO Clothes Washing Machine Stops |  |  |  |  | Yes | FO Clothes Washing Machine Stops | 1753a8a2-a079-4c29-81a0-0bef92891b2e
checkpoint-status | a67d194b-7cee-4ccf-b55a-1b6aae535de0 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | d07b1e29-307c-4c98-acf8-c5aebd2b2fd8 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | d986add7-f0fd-4406-9141-062b8f0bbce2 |  | checkpoint | General finish & alignment both level & centre of tapware
checkpoint-status | e0df35a7-9a68-4587-b0fc-ef2b90a0efa2 |  | checkpoint | Check flood stoppers
checkpoint-status | 42386290-2820-49b8-92d1-da8657c938e0 |  | checkpoint | Solid installation & mounting of tapware
checkpoint-status | bdad37b4-fe57-47fb-b9f0-08fa6d005c4d |  | checkpoint | Check cover plates are installed
checkpoint-status | 98d2016c-4c87-4079-9aa0-91dfb77efdc0 |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status | c471711d-5860-4740-8a65-e436a4b2821b |  | checkpoint | Seal or cap off any open ends if required for security
checklist-flat | 756f5eed-9b56-49ae-ac0a-7a5f28d35eea |  | checklist | CW Reduced Pressure Zone Device(RPZD) Rough-in |  |  |  |  | Yes | CW Reduced Pressure Zone Device(RPZD) Rough-in | 1a36c7e5-426e-4d6a-93ab-0ab84aeac9c0
checkpoint-status | 6d905ef1-ca5d-4fd9-8ac8-9c473b9f7de9 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 9394911b-7031-4d4b-9d57-caee71612d78 |  | checkpoint | General finish & alignment both level & center of valve assembly
checkpoint-status | bd91f412-1afa-4c50-93fe-759b7c0a04e3 |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | 1e973406-b6c1-45f0-8ae5-81c59ccdaf3e |  | checkpoint | Check silicone applied to studs
checkpoint-status | ae31f4c0-a4d6-41a4-9037-64069de414ad |  | checkpoint | Wall box is installed if required
checkpoint-status | 5acddc14-9446-419d-b235-08ec4b5bac89 |  | checkpoint | Check RPZD correct location
checkpoint-status | 5f2bd211-e33d-4e99-9372-b2fc93279c98 |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | 7bf47135-3a55-46ad-95c8-90df0f1bd3b3 |  | checkpoint | Flow direction is correct
checkpoint-status | 0ef73ab8-36b9-48c0-bc2c-9306be70b6c6 |  | checkpoint | Test result is compliant with AS3500 (Record test by photo & time/date)
checkpoint-status | d34d4410-adf4-476c-b66c-bfddc615dbf2 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | bb0e2004-0610-451d-95c5-11b452505121 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | ae050eda-6d39-4b74-a32c-eec68a2c5ed5 |  | checklist | FO Cleaners Sinks |  |  |  |  | Yes | FO Cleaners Sinks | 1a7a356b-963b-4ced-82dd-6b58294285c5
checkpoint-status | 18d56098-ffbc-4aaf-8d64-041bea23e5c7 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 3e35c924-bcff-447a-833c-8b4894bd4cf2 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 2a0d0f15-d2cd-478e-9d7d-2f0585cec41f |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status | a6e2cc42-0755-4734-9bed-b02ec3460956 |  | checkpoint | Solid installation & mounting of sink bowl & mixer
checkpoint-status | a8539c52-f518-4e17-8790-25614d841abc |  | checkpoint | Wall brackets are well fitted & secure
checkpoint-status | 2339c138-6ef1-4a92-b299-cf70051bf0c6 |  | checkpoint | Bucket grate is well fitted & secure
checkpoint-status | 3d6ee26b-900c-43b6-b877-bc79807c4276 |  | checkpoint | Check operation of plug & washer
checkpoint-status | 35936f24-88b4-46a0-94d2-e2246d2995e7 |  | checkpoint | Check in cupboard for signs of leakage
checkpoint-status | e730e844-7b64-4c57-8ae4-50ae5a1c20cb |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status | f251752a-e1c0-4e03-bf44-e4fa776916fb |  | checkpoint | Check cover plates are installed
checkpoint-status | 723affb0-d3b0-4e49-9477-4868a6cd3767 |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status | 485c592a-69c6-4bd7-b395-c6b4ae44e24a |  | checkpoint | Check trap is installed & nuts are tight
checkpoint-status | c504deee-4f1c-4dbd-ab18-2b7d7db9996f |  | checkpoint | Check trap & waste pipe connection for signs of leakage
checkpoint-status | 0342bfa4-1b09-4426-ac32-c7e3ed19af48 |  | checkpoint | Operate mixer & half fill bowl then discharge
checkpoint-status | 50cc1f86-8ebd-452c-894c-f1e39f32bc5c |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | 9ba23a94-2501-4494-a627-d153a04b1731 |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status | a14e491d-3a56-4ee2-a67c-4e6122d3b667 |  | checkpoint | Check caulking is correct
checklist-flat | e90358ad-fa55-4908-99da-474dcd4c31a2 |  | checklist | RW Rough-in (Low Level) |  |  |  |  | Yes | RW Rough-in (Low Level) | 1b44c508-4a1e-43dd-92c7-c18649fce351
checkpoint-status | ec58e273-0f1b-4873-be78-bca889d504d3 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 13e53228-edc4-4538-a5bf-c2cc4f761ad0 |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | d5bff27a-48c6-48b8-8b63-7129991804f2 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 70cc5d5e-ee3a-4b96-8610-559da6155e98 |  | checkpoint | Check silicone applied to studs
checkpoint-status | df4bd6fe-ccd8-4fab-951e-73b8e48a242a |  | checkpoint | Check in-wall noggings are installed to correct locations
checkpoint-status | 101b8a32-5de1-460a-8814-ce987e04a091 |  | checkpoint | Check In-wall lugged elbows are installed to correct locations
checkpoint-status | f1fd2ac7-5410-49e4-8772-0819442055cb |  | checkpoint | Check in-wall pan/cistern brackets are installed to correct locations
checkpoint-status | 980e60c6-e7b4-4f20-83db-fa80568510f0 |  | checkpoint | Check for possible cross connections
checkpoint-status | 6fee58df-cac7-42fe-825c-c11a71f59b94 |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | f27e117a-a252-4484-aa70-59952f55e7b3 |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status | 573abe61-ad8d-41c3-a180-6a8fd9e8a29a |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 83e9c7b2-f0e2-4996-87f8-31bb40860471 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | c05a85f9-a635-48d5-9703-c35835f2045a |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | f29d7d99-f2cb-4f2b-a0cd-1692a42e2e0b |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | eb515d00-3b84-4940-937e-6c99e16647e1 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 6959891d-0b92-44ae-b087-8b8411faa2f9 |  | checklist | Enter Level/Apartment/Description |  |  |  |  | Yes | Record Hold-Up | 21beb992-20d6-4dc5-8a0a-6161b6f1629b
checkpoint-status | 29c1ce54-3941-416f-970e-71384848811e |  | checkpoint | Decription of Hold Up
label | 2e3c3582-73df-5fa8-9088-8e2c74dbcf06 |  | note | (See Photos & Comments Attached Below)
checklist-flat | 1b169243-dc68-43ce-b405-664d74a27b8f |  | checklist | RW Re-Cycled Water Meters |  |  |  |  | Yes | RW Re-Cycled Water Meters | 29a09817-efe8-4756-976b-5d8a933e50f1
checkpoint-status | 68567258-f241-468e-9da2-4a6a240990dd |  | checkpoint | Water Meter Details:
text | 1bf0a78f-c1c5-5d33-a2b6-21766dd8e902 |  | textbox | Meter No:
text | d9333858-2bd7-50bc-acf2-4f936820fcfb |  | textbox | Level:
text | 8523f3d8-97e0-51ae-90ae-9301724d8b73 |  | textbox | Meter Size:
checkpoint-status | 59b77962-09bf-4630-a7c9-567c16bba5b2 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | ce60ab8a-39ee-4e19-bf63-bfd726813a5a |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | 63c79889-40d8-4667-8d98-ee69e8e64d03 |  | checkpoint | Meter bracketed
checkpoint-status | 4675ee96-af85-4fc8-926a-6457b5706530 |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | 19ca28be-68a1-433a-9382-74036e4af81e |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | 0dd40b27-76bf-4008-9190-c6d42772d2a2 |  | checkpoint | Pulse rate value is correct
checkpoint-status | 2c346f9a-33e8-4681-8bf0-a4cd30eae8b8 |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | 87be5c84-3fc9-4775-bbdb-8191f27ae3f2 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | a1b5d034-e3e1-47f8-b04d-238316441540 |  | checkpoint | Flow direction is correct
checkpoint-status | ae5e9c9f-3701-4c8c-85fa-e394467bd765 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 35c8c864-ee82-4cc9-b1a2-910fa9f0c9a8 |  | checkpoint | Record installation by photo & time/date
checkpoint-status | 50fd5e50-683f-4cbe-8389-08df4164f490 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 3257ceca-046f-469b-9a21-c62013da22e6 |  | checklist | CW High Level/Corridors |  |  |  |  | Yes | CW High Level/Corridors | 33c7b06e-5695-42a6-b157-de7b4655a322
checkpoint-status | ca9e237c-ea53-4bb2-82f6-1289473d79f9 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 378603b0-9083-4646-aa48-4673f5e6821b |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 8a50e4bb-cad2-4dd0-803f-3229e98a83df |  | checkpoint | Pipe materials are correct for application
checkpoint-status | a3b2ccb8-1c60-4814-97cd-69c38fc75103 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | c1ef2aea-c83b-41ba-999b-b8588269f97a |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 82aba98d-5a49-4f87-af71-8c2bbb969938 |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | bf5750c7-9f60-40fc-a13e-f9f1d35e1f8e |  | checkpoint | Welded pipe joints are completed
checkpoint-status | 0ccf37c6-2e2f-41e3-8704-7d193fea19db |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | f7d362a1-4e98-4320-ac99-ba35b952538e |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | 16bc3443-ac8b-47e2-b161-90cd04741c50 |  | checkpoint | Meter manifolds & frames are firmly bracketed & installed in sizes, quantities & locations as per design
checkpoint-status | 65368135-71fb-4e3c-b694-260368d60575 |  | checkpoint | PR valves are installed. Pressure rate & flow correct
checkpoint-status | 55e46df0-c061-4d99-a0ad-f3bf0284658f |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | f6f5cd47-cfef-4307-a251-7987b3e73562 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 47c9960c-0afe-47a2-aeee-8e61f78fe0d8 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | f24fa30e-0b56-49d7-9834-cc9709240b68 |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | 1e014d01-a3cc-47b3-8686-cf9df3c29e2e |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 7e0dfe69-cd2e-44c3-85e7-75216469332a |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 8b9f3da8-9687-421f-b961-1f3df40191bf |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 07611780-9a10-4b68-ad6a-10d9325bb014 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 67aac4f5-f36a-4a2b-85f8-75bbb3dd5270 |  | checklist | PE Above-Ground Potable Cold Water Pump Package |  |  |  |  | Yes | PE Above-Ground Potable Cold Water Pump Package | 34229ed9-33a1-49fc-8e7d-38defa7dfe4d
checkpoint-status | 7dc86013-3e22-4315-b52b-17683ed4a578 |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | eb3079ae-3e4b-451f-8d09-e2e63bffb3a2 |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | ad3d4f7e-6b02-441f-a49f-994d9e85958d |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | e955bf79-2365-48cd-8d86-766bb38227f9 |  | checkpoint | General visual check for damage, etc
checkpoint-status | 7b04d0b6-6440-4abb-a644-fba2c3d283da |  | checkpoint | Visual check for water & oil leakage
checkpoint-status | 7dc00e14-1993-4fe4-9b6a-76eede4b7deb |  | checkpoint | Mountings fixed & torqued down to plinth
checkpoint-status | 8ff43dec-4f84-4fe0-9ae4-9b051a5c8c04 |  | checkpoint | Inlet pipework is installed & connected
checkpoint-status | 4ebb2173-29f3-4664-8a9f-43861243b149 |  | checkpoint | Outlet pipework is installed & connected
checkpoint-status | 63d4fa66-02b0-4abb-b822-366b9b75f96f |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status | ce958cb1-da47-4cfc-9a11-ab3d059edbba |  | checkpoint | Electrolysis prevention in place if required
checkpoint-status | 89e68855-7a55-4efa-a7d1-be071333fdbe |  | checkpoint | Electrical cable is installed
checkpoint-status | 23253fda-8b9e-4e3b-bc9f-c819024f4e54 |  | checkpoint | Control panel is installed
checkpoint-status | d35db932-fb2b-4b97-a23c-e41e671ea646 |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status | c9bc9e29-061b-46a8-982d-c5e969cfdc87 |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status | d8edb78a-de3b-4eb3-9e3c-8cdf20fe7cf9 |  | checkpoint | Pumps cycles set & test run & certified by pump provider
checkpoint-status | e592beb4-8a20-4674-b319-629b8ac6d55a |  | checkpoint | Pressure gauges installed & running within operating limits
checkpoint-status | 9808fb6c-3ec9-47fd-9766-12d8ab608720 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 73330255-2be7-426c-bcd1-39504c298c85 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | 5d75f097-83af-49b4-bf26-17806731d374 |  | checklist | PE In-Ground Grease Arresting Tank |  |  |  |  | Yes | PE In-Ground Grease Arresting Tank | 3610fdc7-e1c8-4afd-911e-ba71fa814825
checkpoint-status | 86bc1298-2e7f-4340-a246-a03b5f45e4da |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | cde537a2-b5d8-491f-a8a1-8cc17ebd0e76 |  | checkpoint | Authority applications & start work notices accepted
checkpoint-status | 8553dc35-7a68-435d-9639-9140fcfcc201 |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | 1c275509-8043-4248-b0a5-bc023d5aadea |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | 0c9dc1fe-77f9-49f9-8c9c-895f039133df |  | checkpoint | General visual check for damage, etc
checkpoint-status | e2d3ad6e-7ff1-4e07-82eb-4da247d5ebf9 |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status | ee13ab41-d2e3-41b5-886f-3c9994302c36 |  | checkpoint | Vents are installed if required
checkpoint-status | 501327ba-c0da-4bb1-b657-81d8a16aff95 |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status | 6d9d01e0-700a-4548-bb2d-17ee96cd9d79 |  | checkpoint | Spoil is removed
checkpoint-status | 44bad9f3-a08b-42b6-8189-9812c7bf6f65 |  | checkpoint | Inlet drain is installed & connected
checkpoint-status | 04f5b1ef-a561-470e-b056-b34895bfc5b7 |  | checkpoint | Outlet drain is installed & connected
checkpoint-status | 6580f9dd-5584-4ef7-ad13-44413e4da7bf |  | checkpoint | Disconnector trap is installed & connected
checkpoint-status | 8e68e923-613e-48a4-9088-da3f4881c6e9 |  | checkpoint | Vacuum-line installed & connected
checkpoint-status | c8e5af29-fd97-4e36-aa10-2aa174c79c10 |  | checkpoint | Vacuum-line stortz couplings & caps are installed
checkpoint-status | ef18c647-bb05-4623-8c2d-a0b54ac05382 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 5a3c8bb1-58d6-4679-8b45-3cd7ac05cda8 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | 87be32f1-f680-47cb-9f45-c4d7043286bb |  | checklist | MT Natural Gas Meters |  |  |  |  | Yes | MT Natural Gas Meters | 3784e5ea-4e76-410d-a494-d44ba47bb392
checkpoint-status | eb0aa058-3929-44ac-a60a-b0f4916ae5ee |  | checkpoint | This installation and following checks are to comply with AS-5601
checkpoint-status | 3547cc79-bfa8-433c-aef8-f726173cc618 |  | checkpoint | Natural Gas Meter Details:
text | a89b7158-e638-5e52-a4f2-dac5be2ea6a4 |  | textbox | Meter No:
text | 26a0a29d-e5d0-5d6e-9bac-19662f28e2f9 |  | textbox | Meter Location:
text | ad1b815f-a712-5058-a4dd-62528b1ea0e6 |  | textbox | Meter Size:
checkpoint-status | bee4c451-6e86-4f8c-a244-090f6b80a65a |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 4d768b32-e863-425d-959f-322076c2c90d |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | bb71efa5-fd0b-4cd7-a91c-4132e38824eb |  | checkpoint | Meter bracketed
checkpoint-status | a8f8cc3d-bcb2-451d-b8a2-d672736532be |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | 7164cf45-73f8-49b2-8208-e7f7f9de201c |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | 2992908b-6f33-4913-a233-891c733edee0 |  | checkpoint | Pulse rate value is correct
checkpoint-status | 2bed7e83-0078-4f89-8621-f20366413711 |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | 841242d2-556d-4d54-8229-9097d8078448 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | e85ac9d3-31c8-4bdf-93b4-cca2d4397341 |  | checkpoint | Flow direction is correct
checkpoint-status | 7ef96c22-0cc0-4e87-a0a6-2d414433e2e2 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 9c361f2f-4def-49ba-b61a-0180c3028bfd |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 33026a99-4b86-438c-9778-3cf342b19409 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 34dc9509-59f5-480d-8b6e-046389a4d85d |  | checklist | RW High Level/Corridors |  |  |  |  | Yes | RW High Level/Corridors | 3a570b5f-cbf4-4923-a16a-070a74aca063
checkpoint-status | 0a5c5113-5c0a-4e1b-8655-bcbf5f6bee15 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | ade914e9-49d8-4480-a27c-1207ad8d9eb9 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 3f425dfd-6c09-4f30-82dd-0bcba740b9d5 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | a7a8d9aa-41ea-44df-bfdb-b88cbe9b95fe |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | c7126ea5-2202-48cf-9268-7f81006cc7ed |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 72ec79a7-ba17-47f8-99bb-6ce34c18e1d4 |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | 149eb114-29f7-4942-a935-16c820f2bd7e |  | checkpoint | Welded pipe joints are completed
checkpoint-status | 69fa57be-4d3a-47f5-98d0-b36cc87669b1 |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | b42aeca5-906d-41e9-9c0b-ca67d0d28ee3 |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | 7227d359-858e-4de6-a7da-0b30341d8f99 |  | checkpoint | Meter manifolds & frames are firmly bracketed & installed in sizes, quantities & locations as per design
checkpoint-status | ec7e2c16-1197-4d48-93b0-a7bdcba7ae0c |  | checkpoint | PR valves are installed. Pressure rate & flow correct
checkpoint-status | 6bb8421a-7f75-408b-8c93-f1f94ce1d128 |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | e0a10e9f-6615-4a06-a534-9a6b9cdcb835 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | e2660bb1-9f15-494e-b881-e8e98b221c5e |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 7c5e38de-25d0-4694-b393-7700b9ec0979 |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | 52e1e0eb-4ce7-43e9-8152-67ee582e05af |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | cc295f97-b04b-485e-8c42-3c6582ef6da4 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | ef48e7a9-5a28-4e11-81aa-eb9a684fa0a8 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | e6981bcb-0101-424c-aef7-1ba1e3887eb4 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | d0d2d4f7-a322-46ca-b655-3aa486473641 |  | checklist | TST Testing Roof Downpipes (Water Test) |  |  |  |  | Yes | TST Testing Roof Downpipes (Water Test) | 3ae5ae58-4b45-49aa-ab11-0d8ce68c679b
checkpoint-status | 62cf6ab6-07d4-4313-8f3f-ca1f83e7cc1d |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.3 (2018)
checkpoint-status | 5d067915-1e4f-4c9d-9ff9-7324d9532676 |  | checkpoint | Ensure bore is completely free of any blockages, constrictions or debris
checkpoint-status | 23f8695d-6562-48b2-9942-2153a289596b |  | checkpoint | Ensure pipe-work is securely fixed to eliminate movement during pressure test
checkpoint-status | eb00178f-c2c1-4098-acc5-419f8124b901 |  | checkpoint | Temporarily plug & seal any open ends below the test point
checkpoint-status | 80f868c1-e15e-4bff-b642-a5bea1348e8a |  | checkpoint | Choke test to a head of 10 metres or if the downpipe if shorter, fill to its limit
checkpoint-status | e693062a-712d-4409-ae97-2ad5e645e3d6 |  | checkpoint | Slowly fill the test riser with water until full and hold for 30 minutes
checkpoint-status | 1b59040f-5b2f-4390-97f4-ff1b46eaeab1 |  | checkpoint | Testing is deemed successful if the water level remains unchanged after 30 minutes
checkpoint-status | 976febd3-d471-49f4-8c23-94f0a77c58e6 |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral working conditions
checkpoint-status | f7a291a6-a5d2-4488-8a93-84854f099c7b |  | checkpoint | Test sticker on pipe 1500mm high facing a corridor or accessible wall
checkpoint-status | 18efd130-a386-40ab-9c6b-3c59ad8e71e5 |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | ac8b7088-aee6-4e92-b0e2-7e8dc834aa0d |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | 79ebb149-5ca5-452b-b160-298152fe4d59 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat | 4bb74aca-b76e-48ed-8a77-24fbf39d4ca3 |  | checklist | SW Downpipes/Overflows (Main Droppers) |  |  |  |  | Yes | SW Downpipes/Overflows (Main Droppers) | 3c3c4b4e-9a07-4d71-ac02-cfd29c43a3c9
checkpoint-status | 090dbbba-de07-4bdf-a051-225a017f90c5 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | ac128060-1ed4-4f8f-b458-34c35f890dd9 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | 68d36df3-fbaf-42d5-bb07-61f98ff72c5d |  | checkpoint | Pipe materials are correct for application
checkpoint-status | e8c112b8-74e4-421b-bb98-488764ba36b6 |  | checkpoint | Downpipes are installed
checkpoint-status | a5aa4868-45ea-47e1-9663-515be2480cb4 |  | checkpoint | Overflows are installed
checkpoint-status | 24aa1744-ab54-4ddf-9ef1-db2fc9d4cf8c |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status | dbbfba4f-6fb7-40cc-a3de-7d047d385ae2 |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status | 76ac9ab9-77b4-4bad-9244-f931f4484b1e |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | e68c0790-5d45-4ab7-9dfa-f95228f678f6 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | e848d0b7-201d-41f3-b8a8-726e41b44869 |  | checkpoint | Penetrations are installed
checkpoint-status | 1d3ba217-9783-4e89-beb9-8674f9e56deb |  | checkpoint | Drain penetrations are caulked
checkpoint-status | cf4f4e6f-c5df-4df3-91a8-8022504d1b23 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | 4e0eeea1-fe49-406b-b998-3e001ca25fa8 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 7422bb29-72e3-47e9-88cc-b10ca70dd039 |  | checkpoint | Roof/overflow outlets installed
checkpoint-status | 10396ee0-fd57-45e8-ac75-bd7668cbc5a6 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 2c0c558d-6e77-4a12-848c-3d526cad06ac |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status | 2fc73862-9b33-43de-84de-3cf637608c12 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 49225b1e-ede8-4ddf-9457-51b0292658c6 |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status | 542ab373-3401-48cc-8f78-49f3ac378cc9 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | c0966762-f057-4c2c-bf19-3c19611042a1 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat | 109c880a-f42c-47c6-b6e7-a66c4211e643 |  | checklist | PE Hot Water Generating Packaged Plant |  |  |  |  | Yes | PE Hot Water Generating Packaged Plant | 3c3d15e3-c785-44e6-a676-e0cc6a3a7c0a
checkpoint-status | 65ae2020-5caa-4f8c-addb-f2b3cb816ffb |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | 6d721781-f5b3-4cf4-b74a-4da1e8b61965 |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | fcfe837d-0985-4d76-91d6-83647c87d735 |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | 8ebe4a23-7a1a-48bf-855f-de0e4c032490 |  | checkpoint | General visual check for damage, etc
checkpoint-status | a6a68229-4c6f-41e0-b884-89e295a29cd0 |  | checkpoint | Visual check for water leakage
checkpoint-status | 743f3cd2-0bdf-4c79-ae4c-143eaa7af602 |  | checkpoint | Perform natural gas leak detection procedure
checkpoint-status | dba89218-7d6f-49a1-8315-38a9d1077ea8 |  | checkpoint | Mountings fixed & torqued down to plinth
checkpoint-status | 9df29ef3-3d9d-4cf8-a919-4ce5f588937a |  | checkpoint | Cold water check meter is installed & connected
checkpoint-status | a0d3f634-e59c-4b10-a13c-276de7338af8 |  | checkpoint | Natural gas check meter is installed & connected
checkpoint-status | b83e2c01-707c-4824-826a-9627d2ba7423 |  | checkpoint | Cold water inlet pipework is installed & connected
checkpoint-status | 7d49f697-f012-4abf-afb4-144cbfd38e9c |  | checkpoint | Hot water outlet pipework is installed & connected
checkpoint-status | 6ab72879-bd4c-4f86-b97e-30c32758b27a |  | checkpoint | Hot water return pipework is installed & connected
checkpoint-status | f11efb5f-5529-4a4d-8441-e33f1d647afe |  | checkpoint | Hot water pipework is thermally insulated & correct weight as designed
checkpoint-status | 5b8ec57e-5e7f-4ddb-94aa-eb214f67f2f1 |  | checkpoint | Exposed hot water pipework is completely sheaved & weather proofed
checkpoint-status | 2f6d0bf0-c656-4861-8e47-b3ea87f3e082 |  | checkpoint | Natural gas inlet pipework is installed & connected
checkpoint-status | 7135d68f-7814-4bea-855c-1d46c32c1a71 |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status | 8207582f-b793-42ee-b4f0-e3b9d727f39f |  | checkpoint | Hot water exhaust pipework discharges over dedicated hot water tolerant drain point
checkpoint-status | 201ab46c-cae7-4f27-ae5d-085973aa4c42 |  | checkpoint | Electrolysis prevention in place if required
checkpoint-status | 3b8d192d-7c91-4c78-9394-e6a02e9bb836 |  | checkpoint | Electrical cable is installed
checkpoint-status | 877dc67d-748f-400c-a7c8-3a1509670075 |  | checkpoint | Power flue is installed & terminated as per design
checkpoint-status | 6e3fa903-0307-4b09-9be2-fea50da9b5c0 |  | checkpoint | Control panel is installed
checkpoint-status | ff3d7b9c-2165-4b07-a2eb-543efd6bb8b0 |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status | ea6e582e-ece0-4bfa-b18a-cb7b0f9e63bc |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status | a5742d57-5e4b-4009-8973-ac83baf6b3a8 |  | checkpoint | Pumps cycles set & test run & certified by pump provider
checkpoint-status | 1ea9ac52-ac20-4fce-85e5-0a4682a7e729 |  | checkpoint | Pressure gauges installed & running within operating limits
checkpoint-status | 4a716abb-5d9e-467a-aa0b-fa0c22525223 |  | checkpoint | Flow & return temperature gauges installed & running within operating limits
checkpoint-status | 725aefa4-8c49-4fce-a929-1b3cda21da69 |  | checkpoint | Hot water plant provider has fully commissioned & certified the plant
checkpoint-status | 54b8e18f-3dea-4c82-b4e2-3745c987f3f7 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 6f55e169-c52a-4921-8e67-54cd5a82f098 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | f9709404-465a-48b5-b950-71373bb3a405 |  | checklist | SYP Syphonic Downpipes/Overflows (High Level) |  |  |  |  | Yes | SYP Syphonic Downpipes_Overflows (High Level) | 472a7e11-ef99-440e-b155-9b67a53f35dd
checkpoint-status | f4e732ed-c454-401b-9dc5-9cc9ce88c7a4 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | c2fad174-caa0-4487-9f87-68ea239eaee3 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | 5ade3f39-f302-4328-b817-4ab7f816bb3e |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 0784520c-9c8b-4fde-9311-859defb01a36 |  | checkpoint | Downpipes are installed
checkpoint-status | ab5d95dc-8970-4792-8b81-de924f5fb323 |  | checkpoint | Overflows are installed
checkpoint-status | d883d41f-5994-4546-a7cc-530b859239db |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status | b31b764f-7daf-44b3-a7a6-b67af8b2acc6 |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status | 426b48a9-4ba9-4d51-807f-c9aad037680d |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | fceb4029-20e0-4b1a-af77-c4fabd113364 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 52b9d3ce-cdfe-437b-91c7-d4e0a3a56198 |  | checkpoint | Penetrations are installed
checkpoint-status | 4c320c3d-d9ba-4cba-be9b-2c4ccb386862 |  | checkpoint | Drain penetrations are caulked
checkpoint-status | b9fec945-25e9-44e7-bc19-42d00819d237 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | f027b6b8-22ef-4e97-8351-e99c9517760b |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 398e76be-05df-40b1-baab-b2535dac0860 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 965d9777-6ed3-421f-96a0-30bcdbe290bd |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status | b38ece19-cd13-44d2-98cd-6f8f270fec76 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 36681eb3-9df9-48d2-8596-7671d65fb205 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 5bd487b5-35d3-48b9-8645-b355791a93c9 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat | d3b5d811-570b-455d-abae-716a8af4acd0 |  | checklist | TMP Temporary Plumbing Services |  |  |  |  | Yes | TMP Temporary Plumbing Services | 48df5bce-c777-4429-aeb7-32b99db12d94
checkpoint-status | 7172c8f1-a2af-40c7-b399-43fb1cef56ce |  | checkpoint | Work Completed (As per below)
label | d89903d8-a81e-5065-a488-4e1d9425de71 |  | note | Add Comments/Photos below as applicable
button | 08ac1e61-f6d2-5a70-99c6-fcac632c8420 |  | button | Installer is a Registered Plumber/Apprentice (VIC) | N/A, No,Yes
button | 7074cdb8-d8b9-5cac-a3fe-b3c70a653e9c |  | button | Installer clearly understands the task to be undertaken | N/A, No,Yes
button | 97332af3-ca1c-5eba-b425-24cb7c04fe83 |  | button | Ensure installation materials are used in accordance with manufacturer instructions | N/A, No,Yes
button | 3d946780-3170-5168-9f50-1cf01a6f43ae |  | button | Check for damage or leaks to the installation | N/A, No,Yes
button | 599bfe0d-30db-5484-8a4e-b33e6095939c |  | button | Check pressure pipe joints are installed correctly | N/A, No,Yes
button | 782d0596-8257-5689-9bb3-27bb6c302aa8 |  | button | Check PVC joints are cleaned & glued (no duct tape) | N/A, No,Yes
button | 7e65ee57-9f11-5f14-8671-abedf4d8da32 |  | button | Ensure all waste/rain water discharges to a live drainage system | N/A, No,Yes
button | 1d7377b7-c206-56ab-bb7a-5817064ec75d |  | button | Ensure all pipe & fittings are not reused | N/A, No,Yes
button | fcb86749-abc2-544c-bf1f-e5fcf798858c |  | button | Check cross connections between reused & potable water | N/A, No,Yes
button | 6e45d6ec-29fc-51cf-a410-84dff12224b8 |  | button | Check Jump Form temp connection when jacking | N/A, No,Yes
button | ef9afda6-ad31-54ab-ba05-5354d03d046d |  | button | Check any open ends are sealed and/or capped | N/A, No,Yes
checkpoint-status | 9af164ea-ed50-40a6-938d-1d990f92b789 |  | checkpoint | Final sign off - Pass when Work completed to specifications/drawings (Any issues please comment & Add photo's below)
boolean | 0d562912-1ca9-5e36-b904-908d04bce234 |  | tickbox | Area clean
checklist-flat | 32181fcd-e9c1-405b-b901-4accd0270fe3 |  | checklist | New Task: |  |  |  |  | Yes | Add New Task | 4bd67ba7-cb35-4dbe-ac34-a9e285fdc741
checkpoint-status | 911e3ad2-9021-413c-a5f3-9fb56f1c6d17 |  | checkpoint | Task completed
checklist-flat | a5446e89-e336-4519-ba5d-d2f74fdff81e |  | checklist | TST Testing Natural Gas Service (Nitrogen/Air Test) High Pressure |  |  |  |  | Yes | TST Testing Natural Gas Service (Nitrogen/Air Test) High Pressure | 4ee9e62f-162e-4b71-b551-d3947c7c5df6
checkpoint-status | 9ae54806-6e4c-4a5f-a793-f066b7aae094 |  | checkpoint | This testing procedure conforms with that as set out in AS-5601.1 (2013)
checkpoint-status | dd006164-76d3-41a2-854a-4b9fcc5810fa |  | checkpoint | Ensure all valves dedicated to isolating the test zone are securely shut off & tagged
checkpoint-status | 5732ed7b-2182-4522-b797-1fb67065e2a6 |  | checkpoint | Nominate an air purging valve point
checkpoint-status | 52b9de8c-d781-4c26-bd5a-790a4dcb4205 |  | checkpoint | Nominate a pressure testing valve point
checkpoint-status | 1da7d467-b365-499b-9992-7e359935498d |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status | 8049cae8-a08d-420f-994a-33bef2e45664 |  | checkpoint | Ensure all terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status | 34204d52-c908-4637-9106-d17867612369 |  | checkpoint | Slowly open test feeder valve & fill the test zone with nitrogen/air until completely purged
checkpoint-status | b23a7543-2d7e-4650-b94e-40464c15b08a |  | checkpoint | Connect pressure testing device to the nominated test point
checkpoint-status | e184d6b8-e1bd-4930-945c-e6c6515874f9 |  | checkpoint | Shut off the gas feeder valve
checkpoint-status | 7e82d984-b77a-41a6-babe-ca79713d84f6 |  | checkpoint | Commence testing by slowly increasing pressure up to 1.5 kPa above working pressure
checkpoint-status | b837191f-a3fd-4ece-9582-86770107f157 |  | checkpoint | Testing is deemed successful if the pressure remains unchanged for 5 mins of every 30 litres volume of pipe
checkpoint-status | 45405978-ed7d-4721-855f-4da2cf4b7eae |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status | 2cb5b463-2c27-44a6-906a-1fcd0045b797 |  | checkpoint | Test sticker in visible location
checkpoint-status | a18db677-d18c-4e54-852d-4b86ea2b6cfa |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | 5c18bd07-f729-41bc-8dfb-91add8fdf872 |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | 27b7a3ae-b039-4103-84b0-f7f3b93db87d |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat | 23a97c24-fdf6-446f-8b09-551205beeb53 |  | checklist | TST Testing Sewer Drainage (Water Test) |  |  |  |  | Yes | TST Testing Sewer Drainage (Water Test) | 4f1fb02d-3e69-48d0-ae0d-a774c03c1115
checkpoint-status | df073688-d844-4380-99ab-eb7c3ea313fb |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.2 (2018)
checkpoint-status | 6a4e53ee-896d-4cd6-983c-f43748b1fe5a |  | checkpoint | Ensure bore is completely free of any blockages, constrictions or debris
checkpoint-status | 5934a0a9-4aae-472e-a682-2bba74de1a8a |  | checkpoint | Ensure pipe-work is securely fixed to eliminate movement during pressure test
checkpoint-status | 1bb5a494-f36c-4b85-ae57-fa7703f4fc72 |  | checkpoint | Temporarily plug & seal any open ends below the test point (i.e. floor or shower wastes)
checkpoint-status | abb14718-e199-47d8-b657-3e4eebae900f |  | checkpoint | Extend a temporary test point riser to a height of 1 metre above the highest overflow point
checkpoint-status | 24bddb2c-b26a-423d-8a49-1ad12c3d24aa |  | checkpoint | Slowly fill the test riser with water until full and hold for at least 15 minutes
checkpoint-status | 85b5f8a5-b96e-45e3-b3ff-04106b6ed1e6 |  | checkpoint | Testing is deemed successful if the water level remains unchanged after 15 minutes
checkpoint-status | 8859a627-9973-4b25-9c12-1b24b7171501 |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral working conditions
checkpoint-status | a979dbc0-32d4-4405-9c98-dedc442b6793 |  | checkpoint | Test sticker on pipe 1500mm high facing a corridor or accessible wall
checkpoint-status | b35f3e95-ef7b-484f-bb89-576bbc4674fe |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | fac3671f-ddf5-45d1-bd3d-83509aac5bdc |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | 03865c12-6c85-496c-bf68-43764919b4d1 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat | 57a61d17-1a49-4c34-962c-8f8467dcf4a3 |  | checklist | CW Cold Water Meters |  |  |  |  | Yes | CW Cold Water Meters | 506027ec-32c3-4c58-a7ce-78e61bf82948
checkpoint-status | 57665d3a-08f3-4230-85b3-651cec68f2ee |  | checkpoint | Water Meter Details:
text | 4d1a8338-3dce-5266-9b5d-c8672d970b56 |  | textbox | Meter No:
text | a426ba8d-c781-5e2d-b2dd-e4c5664dafd6 |  | textbox | Level:
text | b940cbec-f7ec-5034-a7cf-006ae60238d1 |  | textbox | Meter Size:
checkpoint-status | f4aadea4-0035-4b73-a049-bd3be07a34be |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 475f3f7e-60dc-4d99-9b19-f0a6073b7cbc |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | 077b4a6b-f7da-4d8a-89f5-1f6bb8972b74 |  | checkpoint | Meter bracketed
checkpoint-status | 988e8c9a-14a9-4164-954d-07815091d69d |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | 802fdd79-12a9-45d7-bc22-802b7152f075 |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | 13f42ef4-bf74-4a74-94bd-f6a3718fd17e |  | checkpoint | Pulse rate value is correct
checkpoint-status | 66aa9461-c9a9-46d7-a818-738e4f04e581 |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | fc8f00de-12f1-479c-bff8-7a13f7371d39 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | 21e016ff-bb59-4a5d-b753-65b6db121e60 |  | checkpoint | Flow direction is correct
checkpoint-status | 6594e313-c788-43fc-b48e-b7d11cb4f12b |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 63f8c1d7-3423-4eca-81f3-9b084193436c |  | checkpoint | Record installation by photo & time/date
checkpoint-status | af245b03-147a-40bd-b9e9-111cc8582088 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 83f1e51f-5ec1-40c2-84ef-07130760427c |  | checklist | COM Commission Fixture Groups |  |  |  |  | Yes | COM Commission Fixture Groups | 54b93f12-9632-4f80-b6c9-aa51086a31ae
checkpoint-status | 99519f19-a9a1-479b-b8e4-9cc9d6ba7dcd |  | checkpoint | Confirm the installer is qualified & trained to carry out the task as assigned
checkpoint-status | 2156416a-6fec-4668-8df8-d71ad6d2cc6c |  | checkpoint | Ensure all sewer drainage pressure tests have been successfully carried out & recorded previously
checkpoint-status | 08d40142-fa77-4a90-9e6b-9a5e44731b66 |  | checkpoint | Ensure all down-pipe drainage pressure tests have been successfully carried out & recorded previously
checkpoint-status | 6f9b681f-4521-4c79-8390-b957bc1bd231 |  | checkpoint | Ensure all water pressure tests have been successfully carried out & recorded previously
checkpoint-status | 8e05253d-d5aa-4d76-b051-88422fe94ca9 |  | checkpoint | Ensure all natural gas pressure tests have been successfully carried out & recorded previously
checkpoint-status | 6b318466-30c8-4fd0-a894-2da03f9fb09a |  | checkpoint | Confirm the fixtures/tapware/appliances installed conform with the contract & specification docs
checkpoint-status | 3cdc1e5d-b712-484c-b12c-dc16b4ab15eb |  | checkpoint | Ensure the fixtures/tapware/appliances installed are un-blemished & fit for hand over
checkpoint-status | e0170610-c4c6-4478-b5ef-41b3cc231429 |  | checkpoint | Ensure the fixtures/tapware/appliances are installed level, square & centre of position
checkpoint-status | 75ef2068-1af7-4af6-a56f-37f621a5df35 |  | checkpoint | Ensure the fixtures/tapware/appliances are neatly & firmly fitted
checkpoint-status | ed918126-74fe-4cd1-b5b6-4344c2ba8f75 |  | checkpoint | Ensure the wall/splash-back materials & clearances conform with AS-5601
checkpoint-status | 7759a974-d729-4b43-a551-dd4d60f169bc |  | checkpoint | Ensure the range-hood height clearance conforms with AS-5601 & manufacturer tolerances
checkpoint-status | be7b2264-e601-46b9-87f7-b1e5fcf2eb8f |  | checkpoint | Check gas appliance burner operation for functionality & complete combustion
checkpoint-status | 39107580-bb5b-412f-b70a-4831c2d7c6f4 |  | checkpoint | Check installation of correct pressure reduction valves on dish washers, fridges, etc.
checkpoint-status | 9b2a8a37-3d34-4e17-9f82-55799abcb8ca |  | checkpoint | Check all valves, unions & regulators are fit for purpose & not leaking
checkpoint-status | 71ed4f68-1945-4981-8500-d56093b27b83 |  | checkpoint | Check for installation debris, glue, cleaner & set-out marks. (remove if necessary)
checkpoint-status | 6fc05388-1964-4ac0-887f-a2326f82c938 |  | checkpoint | General visual check for signs of water leakage
checkpoint-status | 676d76a6-0871-4773-8897-c7489d162b45 |  | checkpoint | Check cover plates have been installed
checkpoint-status | c560a844-56e7-4b7a-bd92-f4d7a3a0593d |  | checkpoint | Check mini stops have been installed
checkpoint-status | c726a584-6824-4737-9ecf-470cce321ee0 |  | checkpoint | Check flexible water/gas connections are fit for purpose with no twisting or kinks
checkpoint-status | ee22a489-3ee5-478d-9c62-40d2a4310bf3 |  | checkpoint | Check dishwasher hose for connection with no twists or kinks
checkpoint-status | 7fc22857-4abf-4c5a-b665-011291348360 |  | checkpoint | Check waste trap & associated connectors are installed with nuts firmly tightened
checkpoint-status | 53404143-c07a-406d-9cc8-ca2355577036 |  | checkpoint | Check all fixture & floor waste traps are clear of debris & free flowing
checkpoint-status | 49bab921-553f-4b49-bb20-c211840e1b6c |  | checkpoint | Check all balcony rain water outlets & overflows are clear of debris & free flowing
checkpoint-status | 3febeccf-388b-48ef-b268-70d5b22e4741 |  | checkpoint | AAV location & height is code compliant
checkpoint-status | 883a4067-e5d1-49de-822a-f8c79f97045e |  | checkpoint | Operate each fixture/tapware/appliance through its operation & functionality sequence
checkpoint-status | 3451652c-ef4e-4b8d-b24f-3876d75938a5 |  | checkpoint | Check hot water delivery time & temperature against contract specification requirements
checkpoint-status | 98545afb-63ff-4bf6-af25-c752f5bbe4a2 |  | checkpoint | Visually check inside traps & floor wastes for possible debris & ensure free flow of waste water
checkpoint-status | 7092a259-c3ba-4041-a79f-d097a57b87c9 |  | checkpoint | Check hot water thermostatic control valves (TMV) for correct function & delivery temps ≤ 43°C
checkpoint-status | 2c2d3372-d5d5-4c68-be93-c9c7b124ac4a |  | checkpoint | Check hot water temperature control valves (TCV) for correct function & delivery temps ≤ 50°C
checkpoint-status | 55ff24ca-37af-4c11-953d-83a7a4a6262a |  | checkpoint | Check location & functionality of any balancing or straining valves
checkpoint-status | a6479e2b-4488-4bc9-a0c9-1c639b723888 |  | checkpoint | Check correct operation & connections to all tundishes
checkpoint-status | 708eade8-e5c2-4626-9b46-5d40f2c47c73 |  | checkpoint | Check RPZD fitting is installed on balcony tap if required
checkpoint-status | 7d078610-c762-4986-ba6e-d95fca07d6f9 |  | checkpoint | Check quality & application of caulking is fit for purpose
checkpoint-status | 85124822-9ea8-469d-8749-c051d62b8905 |  | checkpoint | Check flood stoppers if in use on CWM stops
checkpoint-status | 9dd76828-d939-4993-9ec0-2f13c878c157 |  | checkpoint | Seal or cap off any open ends if required i.e. CWM stops
checkpoint-status | 487ec06d-9d44-470d-838d-e2fb18caadfd |  | checkpoint | Check valve tag numbers match their allocated location.
checkpoint-status | c2e2d075-ed2a-43ab-af4e-8ad4d9842af5 |  | checkpoint | Check flow meter numbers match their allocated location.
checkpoint-status | d05104d5-d816-4065-9c0b-1e02e52b0721 |  | checkpoint | Test sticker in visible location
checkpoint-status | cf3f5216-0a0b-4dc1-b426-82863a88f40a |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | 54504cc7-5905-4e42-bc74-43a398f3e39a |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checklist-flat | 2d05a7ac-03f9-4758-91a4-40c29c0b309c |  | checklist | FO Irrigation/Hose Taps |  |  |  |  | Yes | FO Irrigation/Hose Taps | 55096593-54cf-4fd9-a8aa-2776a2a7cdd8
checkpoint-status | 277b4a6d-9980-4a82-8d03-a909c5581784 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | d61db411-8673-46fd-b29b-f055ecac7d02 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | a151dc5c-4ba1-469f-bfc3-cf9ad9108a49 |  | checkpoint | General finish & alignment both level & centre of tapware
checkpoint-status | c09d263c-6684-422a-9a78-816c2d4f570c |  | checkpoint | Screw-on RPZD fitting installed if required
checkpoint-status | e1286726-1437-4eae-9580-963e12a2feba |  | checkpoint | Solid installation & mounting of tapware
checkpoint-status | bda86704-3717-485d-9bcc-469b7c5a009f |  | checkpoint | Check cover plates are installed
checkpoint-status | d8906a42-6bae-4d6c-8c78-4f2252f92221 |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status | 3d43ac0b-934c-4383-b81f-828c12028474 |  | checkpoint | Valve tag or signage is installed if required.
checkpoint-status | 6ca4d82c-46f1-44ca-87f6-47e9490fdee8 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 67afe977-be65-40b3-8bbc-a8e26c99d903 |  | checkpoint | Valve is securely turned off (if required)
checklist-flat | 75b264d2-d29f-41bd-8963-8a5749362ca9 |  | checklist | CW Rough-in (Low Level) |  |  |  |  | Yes | CW Rough-in (Low Level) | 565c3967-c77c-4e41-8622-2037b0e97b30
checkpoint-status | 42eb4eb1-4f56-4818-a2a4-d20ecfb9867d |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | c0e69a6e-bb96-4e00-ba16-7231204c5c9c |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | 4014d8a5-e39c-43a5-b90e-6c7ea97f5f73 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 65751e39-1161-4104-b7a2-2daf27a52b70 |  | checkpoint | Check silicone applied to studs
checkpoint-status | 7c4e17be-9eea-4ace-9dec-3433f75e17fb |  | checkpoint | Check TCV/TMV in wall box correct location & securely clipped
checkpoint-status | c89a5a8c-5036-4860-affd-8487a5a14a10 |  | checkpoint | Check RPZD in wall box correct location & securely clipped
checkpoint-status | ba03eb0a-2e88-437c-b0aa-d9504f71e741 |  | checkpoint | Check in-wall noggings are installed to correct locations
checkpoint-status | b9fd2279-8361-48ef-a7f7-5d6792a1c604 |  | checkpoint | Check In-wall mixer bodies & lugged elbows are installed to correct locations
checkpoint-status | 7ea716f2-1e3a-474d-8d5d-cf430aa42aec |  | checkpoint | Check in-wall pan/cistern brackets are installed to correct locations
checkpoint-status | 939441e4-1a24-489f-b126-73b2b9ddb181 |  | checkpoint | Check for possible cross connections
checkpoint-status | 4594c1f1-f504-454a-a823-1bb055669dac |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | 1bf3433d-5ca3-4ac6-a709-04274e2efba8 |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status | 44e4211c-0ab2-4614-95cf-67861a9e8191 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | f29a1c18-5a5e-4df2-8082-d650896ef3fe |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 85129786-e004-4352-ae61-16e4d3951011 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 294bb7c6-91aa-4352-a5b9-55d637203801 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 2546b2bd-5dcb-47f4-ae8e-dc48247d2a05 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 0b8dabc8-34bf-44a5-b0dd-a4f61842fe4e |  | checklist | FO Tempering Valve (TV's) |  |  |  |  | Yes | FO Tempering Valve (TV's) | 589a0933-6774-4c79-b4f2-ea69905bab56
checkpoint-status | 01b7c9d8-0b3c-4826-b9d3-71035fe4cd9e |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | cd34427f-b83d-4bf5-8ff5-83adec32bdc0 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 714f0bd4-613e-47c1-8ef6-69a0f6344ec0 |  | checkpoint | General finish & alignment both level & centre of tapware
checkpoint-status | 020d7a5b-b93d-47d1-b28b-6c141c3d9a2e |  | checkpoint | Solid installation & mounting of tapware
checkpoint-status | 30a5f0b1-2d13-4bc9-8b36-b5770f781106 |  | checkpoint | Check cover plates are installed
checkpoint-status | cbe50f0e-3f04-498c-886b-b432f49d91da |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status | f45f6889-6a26-4bc4-acf3-fd046e996c5f |  | checkpoint | Valve tag or signage is installed if required.
checkpoint-status | 45dd5fe8-22e5-4072-bbe5-c0c27da88161 |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | d371c445-3b39-481f-acb8-e83b0fabe804 |  | checkpoint | Temperature test warm water to ≤ 50°C
checkpoint-status | 15a2d69f-6efc-46a8-b5da-d5a26e37cc8f |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 9f8985c7-c516-4c46-8575-91d05497b337 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 67d6e940-5733-46d1-b994-8a56b01031b3 |  | checkpoint | Valve is securely turned off (if required)
checklist-flat | 170272e9-ea3b-42ef-90f9-23f16c3b6141 |  | checklist | FO Install Cold Water RPZD |  |  |  |  | Yes | FO Install Cold Water RPZD | 59c4c234-45e0-48a7-83a1-c27e2d0f4096
checkpoint-status | 071d129b-eb5a-48c0-b6d7-653bba0291c1 |  | checkpoint | Pipe-work installed & sized as per current documentation
checkpoint-status | a5f66cac-fc70-4dfe-a9a3-ff6c45684998 |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | 3599d17a-c800-452f-894d-301aaaba638a |  | checkpoint | General visual check for damage, etc
checkpoint-status | e14b3ff9-3390-4e87-b66b-74f063ac668e |  | checkpoint | Visual check for water leakage
checkpoint-status | 6d246c39-815f-4782-825c-1235bddbc444 |  | checkpoint | Mountings fixed & torqued down
checkpoint-status | 9cb177ab-1ef3-4e02-b975-d65c9ddaaaaa |  | checkpoint | Inlet pipework is installed & connected
checkpoint-status | 1fb60340-fb23-4551-a8df-218e76b274d3 |  | checkpoint | Outlet pipework is installed & connected
checkpoint-status | cbcd6499-4e9d-46fd-a6ac-f5cdd6d3f36f |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status | e17c449d-7947-4923-a8e3-dfadeb80d49c |  | checkpoint | RPZD tested & certified buy qualified practitioner
checkpoint-status | dbe04a42-cddb-4a02-86b2-01b475508b03 |  | checkpoint | Testing by pressurized Water or Air as per RSG procedure is completed
checkpoint-status | 5d2cf724-2c41-4573-a33d-64e44ad385b7 |  | checkpoint | Test result is compliant with AS3500 (Record test by photo & time/date)
checklist-flat | 92ace3b4-d13a-4cdb-ac0e-02597502dd6c |  | checklist | SD Sewer Drainage (In-Ground) |  |  |  |  | Yes | SD Sewer Drainage (In-Ground) | 5c05c3eb-bd40-4d3e-a6d7-e7cef120d9fd
checkpoint-status | b1d3dd73-ba1c-46c0-879a-fd56b9b253aa |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 07e87e26-da9e-49ca-8e2d-0cb76644e37d |  | checkpoint | DBYD received & verified before commencement of work
checkpoint-status | d7d230ac-6f82-4412-a10c-f66cfd4f8370 |  | checkpoint | Authority sewer drainage applications & start work notices accepted
checkpoint-status | 29ba736b-b628-44f7-ba79-11106da404d8 |  | checkpoint | Authority connections installed by certified contractors
checkpoint-status | 190680df-46d1-455f-bd13-9d9320f03d70 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | f4385bcd-8c55-4b53-be70-19f15ba9814d |  | checkpoint | Sewer instection chambers are installed in sizes & locations as per design
checkpoint-status | 26a3a95f-e55e-4eae-b12b-8c7c12053bf2 |  | checkpoint | Sewer Boundary Traps are installed in sizes & locations as per design
checkpoint-status | 6056fa37-14ae-4825-9a05-740beebc76ac |  | checkpoint | Sewer reflux valves are installed in sixes & locations as per design
checkpoint-status | 39a6790a-85c5-446d-8efd-0c1c1a0bc0c9 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 9271ad58-918f-455b-92ec-5d396b957886 |  | checkpoint | Ensure all grades are correct
checkpoint-status | 08d5a3f8-fcbd-49c0-a8ea-62b3bab2307a |  | checkpoint | Ensure all invert levels are correct
checkpoint-status | c38f099a-d9ba-441a-86b5-b8a5247c06cf |  | checkpoint | Sewer vents are installed
checkpoint-status | 97a9c6d6-a7a3-489d-a5af-14e7add76ada |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 195cc7f5-c3a6-45da-a02e-851bdf3432b5 |  | checkpoint | Clips & Shanks etc. are completely corrosion protected by use of "Denso" type wrapping & sealing
checkpoint-status | 826ab118-0f38-43b4-a53c-520e91207d0a |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 420be83d-6944-402a-a2a1-fcf3b38c4422 |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status | f704e963-c796-4243-ae62-40c3ccbed253 |  | checkpoint | Spoil is removed
checkpoint-status | 87ad58d9-db00-448c-b27c-4005e2696f50 |  | checkpoint | Vents are installed compliant with AS3500
checkpoint-status | 9b42e580-2543-45f9-bb1c-37fcbc6b2953 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 570aa84d-b73a-41c8-9787-76e402fec88d |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 727eee80-1afd-4aaa-bf3f-89ebe5f727bb |  | checkpoint | Check traps are correct locations & clear of debris
checkpoint-status | ab22ca06-7b3e-4b8d-955e-e0fd1e92cb2e |  | checkpoint | Check trap grates are at correct finished heights
checkpoint-status | cc6da2d7-c2b5-4393-8e37-b3a8c47488d6 |  | checkpoint | Rising mains installed & connected if required
checkpoint-status | ffcfb893-13cc-4481-a6d4-ff4e7e666bbd |  | checkpoint | Marking tape installed
checkpoint-status | 52537a18-9943-4630-8043-c82803b96526 |  | checkpoint | Drain penetrations are caulked
checkpoint-status | f98b488f-9e26-4035-a01d-89151bc63f4f |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 7261a2ac-228e-41ef-b8b5-ddc1118cca64 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | b63cd8e1-c17d-4646-aa34-6c22273e2ce8 |  | checklist | FO Wall Tundishes |  |  |  |  | Yes | FO Wall Tundishes | 5d79e369-c6ed-4035-86c6-b584c456a477
checkpoint-status | 0c4a5705-d7ef-42e2-9d13-b7f13cc04379 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 89f1f112-b341-4444-ac88-7247f67464c8 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 309b64d8-8c38-402e-8703-9d62ead0a431 |  | checkpoint | General finish & alignment both level & centre of tundish
checkpoint-status | 3bb70134-0eb4-46a5-bd02-b06e567e4d7f |  | checkpoint | Solid installation & mounting of tundish
checkpoint-status | 21585d77-e1e8-48ae-bf5a-d5c55816268d |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checklist-flat | 298a6c3d-5436-4b50-95e6-87034de06869 |  | checklist | HW Rough-in (High Level) |  |  |  |  | Yes | HW Rough-in (High Level) | 5eebadc7-7084-4f8a-87af-3fe395aac5df
checkpoint-status | d6249d97-e714-44f5-9e7b-9a7eff558384 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 1f177dd8-c7e7-4945-be36-f5d9eacbb613 |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | 855e0bfb-607d-4930-99b7-b5439c24b6b5 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | a2cef182-6397-419f-8dee-51aa33b58d87 |  | checkpoint | Check silicone applied to studs
checkpoint-status | b8cb8694-6184-4c5d-bb47-aba1b99d7c5c |  | checkpoint | Check TCV/TMV correct location & securely clipped
checkpoint-status | 308cf113-f1aa-4a50-be4e-77ff80f737e0 |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 5691c747-2996-4091-acbd-8a219c651a05 |  | checkpoint | Check for possible cross connections
checkpoint-status | 7f655edb-2c0d-4d60-979b-b0e46ce7705b |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | 2a036e99-cbc4-4492-b390-5bb4d7ca9729 |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status | 2da43c4b-ae18-483d-b23c-16b83325c07f |  | checkpoint | Heat trace installed if required
checkpoint-status | 8b5dcc99-dfd3-42a7-ac09-6bac22ab512d |  | checkpoint | Thermal insulation installed & correct weight as designed
checkpoint-status | 2e64e8c8-9378-47be-b35c-710e90e46ef5 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | d81e844b-c63c-4971-a7b2-33c027842142 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | a6b32ae7-425a-4fdb-9c34-d738b1ce0272 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 3e8d6bc3-701d-4909-9056-3587f9f922ab |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | d15ce357-1c66-4b30-a1f2-f455a4362019 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | def1af9d-395e-47cf-888a-77d5a79adc6f |  | checklist | FO Dishwashers |  |  |  |  | Yes | FO Dishwashers | 644607bd-534f-42d5-b8c9-a00d8fd8d0b5
checkpoint-status | 8b0d876b-188d-4c7f-a5dd-a23ffb1123b7 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 9f6d09de-183c-46ff-856a-7dc02e3ead61 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | d95ea681-8444-4d6a-9df6-ae9949ff8a92 |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status | 4ea31663-cf27-4072-8451-4a145d69657e |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status | d525a8d2-b700-4cde-bd84-9ca569d056ef |  | checkpoint | Check mini stops for operation & leaks
checkpoint-status | ea17893c-4b2b-46eb-a03d-36e919153c75 |  | checkpoint | Check pressure reduction valve if required
checkpoint-status | fa48fdbd-4125-4f31-8fe9-140ef079d0a8 |  | checkpoint | Check flexible CW connection for kinks or twisting
checkpoint-status | 2e511908-6faa-48ba-8973-12a7c6f54afa |  | checkpoint | Check flexible waste connections for kinks or twisting
checkpoint-status | 818331dc-ff52-4003-845d-2117f2d161b2 |  | checkpoint | Check dishwasher cycle
checkpoint-status | 2cac0c53-5dbb-4c4b-97cb-199e9ef7bafd |  | checkpoint | Check for evidence of leakage
checkpoint-status | 785d2cd4-87e5-4e83-a17d-43f2d79fb77f |  | checkpoint | Check flexible waste connection to trap is tight
checklist-flat | 7608ada5-6b63-4100-8dcc-2bd94bf04961 |  | checklist | TST Testing Thermostatic Mixing Valve (TMV) |  |  |  |  | Yes | TST Testing Thermostatic Mixing Valve (TMV) | 6b214445-af23-4274-b4ea-065236e670b6
checkpoint-status | 5b37c52b-0a40-4c7e-a483-5999c499b60f |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.4 (2018)
checkpoint-status | a5aa4118-ab8e-4768-9aa7-df3f5a22e85b |  | checkpoint | The tester is qualified & trained to carry out the testing procedure required
checkpoint-status | d5e0ee52-3ff0-4f34-a9b5-f6492d03bb9f |  | checkpoint | Engage a certified/licenced specialized sub-contractor to perform & document this test
checkpoint-status | e32c6bd7-77a4-49dd-951f-8f921dd739da |  | checkpoint | Request & receive a signed certificate of successful test result
checkpoint-status | 84a37fd6-5d9c-4786-a362-a642ee0d2f8c |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status | 1af3f868-b3e2-4d28-8e8e-f5ad98d5231f |  | checkpoint | Test sticker in visible location
checkpoint-status | c15d4090-c83a-4c98-a23b-7031bab39a58 |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | d9330416-555a-4de8-9d57-4d480b4067f0 |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | 7bc34e42-02c5-4bf4-864a-eccd9a4961b4 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat | 602924f9-b6ed-440c-934a-91337137d69b |  | checklist | HW Risers (Pumped or Mains Pressure Risers) |  |  |  |  | Yes | HW Risers (Pumped or Mains Pressure Risers) | 6d3948fd-3723-474d-8f7d-9470b2ee034e
checkpoint-status | 0ab25228-abed-4b1f-ab40-b1b673659abc |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 9bea115d-600c-43fe-8eb3-742ca5927106 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | ab2198b7-1ad3-4f4e-8703-4c43bcec7467 |  | checkpoint | Penetrations are installed
checkpoint-status | 61199243-d00c-4112-a80c-b7dd3a735813 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | d443c1a1-73a8-4514-8831-a26577288236 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 4c7c2317-90f0-43ba-a3c9-66bde2c29711 |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 15515f46-ec98-4cb1-9ecf-0f87e8f35fe3 |  | checkpoint | Ensure all risers are installed professionally with no abnormalities
checkpoint-status | 95aaf836-e6d5-4f06-9631-1d35714c8d0e |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | e06c42d2-0d8a-4a0c-86c2-ddc903f17f6a |  | checkpoint | Welded pipe joints are completed
checkpoint-status | 0b6485dd-9f08-4832-95c3-89944b95f360 |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | c7b9bf2c-cc70-4337-8802-9ead705b7882 |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | 320fa33c-af42-4c8b-b1ac-5c5f89a759fc |  | checkpoint | Pipe penetrations are caulked
checkpoint-status | 2f04bda6-f66b-40b3-8e33-fb2d1fb0bb5b |  | checkpoint | Anchors are installed as per manufacturer instructions & compliant with AS3500
checkpoint-status | fb8f09d5-62b1-4199-aefe-f2a102992af9 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | f661dad1-43ae-4024-b581-6f4a27923dfa |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | ef1d7044-88d3-4dad-8ea5-b059f1d4a976 |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | 5841ebad-66ef-45fd-939d-61dec9677f8d |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | 49b62134-f984-47c7-9328-c12cf3adaf19 |  | checkpoint | Heat trace installed if required
checkpoint-status | a1ca2685-a85b-4cb3-ab0f-28b988881396 |  | checkpoint | Thermal insulation installed & correct weight as designed
checkpoint-status | 2da5efed-b9c9-4815-9f77-578235a0522b |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 9ab7176e-9e53-421a-afc3-425e7959385c |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status | 82cc12bf-96ee-4f58-9245-970400b16a18 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 536e0972-1e09-47d0-9501-993b0579f63f |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 304c881b-d2ec-4a29-93f8-22284147212f |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 00800e05-f67d-4146-8011-3201bc6e6a5d |  | checklist | FO Flood Stop Valve |  |  |  |  | Yes | FO Flood Stop Valve | 7509bb4c-8eee-47b8-8413-2649f598d36b
checkpoint-status | 75bef93a-4aef-4ad7-b239-92b541ccef63 |  | checkpoint | Pipe-work installed & sized as per current documentation
checkpoint-status | 628c5639-9eaa-4119-88b4-051d216ad5c7 |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | ffea3703-51bf-4828-8bd3-8089b4022a90 |  | checkpoint | General visual check for damage, etc
checkpoint-status | 9ffcfa3e-4052-4b92-8d04-ebdb35ac82dc |  | checkpoint | Clipped & mounted securely
checkpoint-status | 57723551-1880-4192-9db5-306d29d88683 |  | checkpoint | Inlet pipework is installed & connected
checkpoint-status | 75d149c3-dcad-4290-a759-0dd1fa7a211b |  | checkpoint | Outlet pipework is installed & connected
checkpoint-status | 7b257c82-dcad-47c5-9f89-c9b6e42e268e |  | checkpoint | Batteries are installed correctly
checkpoint-status | 60bebb01-78b7-49d8-b4a0-e9f5a16e77ac |  | checkpoint | Control LED lights are all in the Green
checkpoint-status | a13f281f-a96a-4521-914a-caa6deed4053 |  | checkpoint | Test result is compliant with AS3500 (Record test by photo & time/date)
checklist-flat | 904f2be2-5959-4181-8636-4b5e8d5734d0 |  | checklist | MT Hot Water Meters |  |  |  |  | Yes | MT Hot Water Meters | 7fbdf2da-f292-4246-83a5-195bc504a247
checkpoint-status | b949901a-9165-49df-846a-ba05bf451e86 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | c2358fa1-c83e-4c23-9225-347395791821 |  | checkpoint | Water Meter Details:
text | 03dffddc-6315-5771-99e7-14e12461fce2 |  | textbox | Meter No:
text | 36d6298d-9acf-5553-a167-0cbe179add4a |  | textbox | Meter Location:
text | 1e3d8c62-66db-5893-85e8-8d789a604d16 |  | textbox | Meter Size:
checkpoint-status | 3812f87e-a1ec-420e-8ada-eca40b61efad |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 79bf6613-027e-4923-b253-59339871512d |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | 6b124238-dfb8-4c16-88f0-f3fe78101ff1 |  | checkpoint | Meter bracketed
checkpoint-status | 5314eb3c-2334-404b-8cea-6fdfcf45c9fb |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | a47a0584-c451-4665-8c95-0963755a374f |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | 6986e591-9477-4930-bca7-c0e9d59c446a |  | checkpoint | Pulse rate value is correct
checkpoint-status | a7116d4d-8655-44fb-ac8b-64f5b6666e62 |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | 50f611f7-6b9e-4722-8a28-252dfaca7314 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | 4014a84c-bebe-4ef5-99fb-f414eb30d161 |  | checkpoint | Flow direction is correct
checkpoint-status | 83d417ef-be8e-48b0-8051-c98730f14cdc |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | d61c252e-eab2-414a-af6e-174084c280b7 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | c7836cad-8660-434c-bc95-c1799c5050c8 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 29bad66a-930a-4480-b2e1-77ae0050e3cb |  | checklist | AU Notification to Commence Works in Vicinity |  |  |  |  | Yes | AU Notification to Commence Works in Vicinity | 817d9713-ab21-4f96-af90-e2f1b2264f39
checkpoint-status | 3a2338b1-f4a9-413c-ba6c-4f9c54320e08 |  | checkpoint | Dial Before You Dig
checkpoint-status | 3ecbc806-6e54-4bcd-b18b-0c30efcaac5b |  | checkpoint | Council/Municipality
checkpoint-status | 3ed5914e-22eb-4993-b6b4-cd536631a845 |  | checkpoint | Storm Water Drainage
checkpoint-status | 67d19618-18c1-4826-b1f0-ff1a199cc36c |  | checkpoint | Sewer Drainage
checkpoint-status | 52086a10-5748-4100-aeb6-dace6cddd825 |  | checkpoint | Water Supply
checkpoint-status | 04dc7c3c-83b8-460f-8454-e61524acaf7a |  | checkpoint | Natural Gas Supply
checkpoint-status | 1ed27e9a-0e77-425c-ade2-3f770f92f293 |  | checkpoint | Communications & Data
checkpoint-status | 15f39f5a-257d-479e-bd54-5168565aa16d |  | checkpoint | Electrical Power
checkpoint-status | 19f163a7-bfcf-4962-8722-40d583a17502 |  | checkpoint | Metro Rail
checkpoint-status | b26d2139-a763-4547-b52b-a4c588eef5f4 |  | checkpoint | Metro Trams
checkpoint-status | fb4fbdcb-9240-4dd9-82fa-6264f1f23b82 |  | checkpoint | VIC Roads
checklist-flat | 9af6b9d3-d39c-4fa0-a639-bb4000f8c6cc |  | checklist | NG High Level/Corridors |  |  |  |  | Yes | NG High Level/Corridors | 82d12fd3-f0b2-45c9-a262-eb29b47f8464
checkpoint-status | 05399499-554f-4835-809e-9f3ce745d215 |  | checkpoint | This installation and following checks are to comply with AS-5601
checkpoint-status | 775a2f70-a3d9-427c-884c-fd440eedaca2 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 862f2275-510b-4f94-9870-1775083e5127 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | aaa4c0f4-6803-4559-bfeb-5512033a1366 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 7a727447-3230-49f7-ad28-ac7256587561 |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | f5ffeab5-eebe-490b-a6f4-727025559201 |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | f91de869-2ffa-475e-89a6-599b60194899 |  | checkpoint | Welded pipe joints are completed
checkpoint-status | 73cbd02b-8a81-41a3-9a78-7cc77fe0d146 |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | 8ccc52b5-f7d8-46c9-88ef-0806529f2a5c |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | 7d06afc3-7d78-4b2a-aab7-cd4b46e60518 |  | checkpoint | Meter assemblies correct & bracketed
checkpoint-status | 3bd29a4f-5fbb-4372-b6b1-6040b835d4a2 |  | checkpoint | PR valves are installed. Pressure rate & flow correct
checkpoint-status | 81289f3f-6dba-4a9c-9d45-78331f0f4e2d |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | 1e596d8d-f5ee-4eb4-af14-00daefededf8 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 199449af-b42b-405e-ae92-dfa90f1cb1d1 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 82a6b89e-6a08-41ab-8d94-7622a3bcb247 |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | c0c71c2c-74c3-4626-8288-2ed146259971 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 6587befd-91ca-4b0a-ac48-2407e6dea113 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | c3ea197c-8bb7-4833-8529-e2865d8a9c17 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | a10d9803-7494-412d-800d-d7a8a8781e06 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | f2beab3f-9826-423d-8419-16b1dedb6532 |  | checklist | FO Gas Appliances |  |  |  |  | Yes | FO Gas Appliances | 860cf017-7028-4207-880c-333a63960678
checkpoint-status | 0b545e84-c894-40fc-a825-0e13cd5ff979 |  | checkpoint | This installation and following checks are to comply with AS-5601
checkpoint-status | 989b3b51-4c07-498e-b77f-5834992813a2 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 859937c4-60c0-45c3-af74-8621a8d21879 |  | checkpoint | General finish & alignment both level & centre of cook top
checkpoint-status | 73e7bdbb-a33b-461f-9042-96abcb21d93b |  | checkpoint | Ensure wall & surrounding joinery material is fire rated & compliant with AS-5601
checkpoint-status | fcc21e33-34c0-4d85-ae0a-ce9bb365f688 |  | checkpoint | Solid installation & mounting of cook top
checkpoint-status | 224e1c05-b1c1-4e8b-856a-d59df78b8af5 |  | checkpoint | Check in cupboard for signs of gas leakage
checkpoint-status | 7c440baa-cecf-46db-bcce-82038cc312fb |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status | 85a276d6-a571-4907-94f2-ad4174c3c6c3 |  | checkpoint | Check cover plates are installed
checkpoint-status | 9a0e8b42-6543-423f-a160-591ecc856236 |  | checkpoint | Check gas valve for operation & leaks
checkpoint-status | 6bddb163-ab61-4b9d-96f0-4fc7be099855 |  | checkpoint | Check gas regulator for operation & leaks
checkpoint-status | c433cca9-fa44-4ec5-8363-a99868e7f482 |  | checkpoint | Check flexible connections for leaks, kinks or twisting
checkpoint-status | f01edac7-fdc5-44d8-955d-35d458c9504c |  | checkpoint | Test operation of all burners from low to full to off
checkpoint-status | 9884ecdc-6fdb-4f3b-bd8c-1724e46e283b |  | checkpoint | Test flame for complete combustion
checkpoint-status | a26d7b63-9fbb-4978-a93f-db5ee0931982 |  | checkpoint | Range hood height is compliant with manufacturer recommendation
checkpoint-status | 63e8acb2-6dd5-468e-9cb0-8495438becf7 |  | checkpoint | Test sticker to be adhered to pipe inside cabinet in a visible position
checkpoint-status | dca5bdb2-4884-4cc6-9eaf-212469ca7c35 |  | checkpoint | Check caulking is correct
checklist-flat | 04cb4105-4a38-4c9b-ae0d-27b5cfa7229a |  | checklist | PE SW Downpipe/Syphonic Diversion Valve |  |  |  |  | Yes | PE SW Downpipe/Syphonic Diversion Valve | 88d3d32e-35a2-49e7-b524-c6ec662d3142
checkpoint-status | 8afdfdf0-4f78-4b85-ad25-dfd641dd86ff |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | e87ea839-15da-48b4-a028-59f324802726 |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | 4bfb7185-6fd2-43f7-a9c9-8a52298d767e |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | b366df14-be46-45c2-b2d8-d3e83559a0e6 |  | checkpoint | General visual check for damage, etc
checkpoint-status | 4a47d353-0411-499a-8f7d-50e194ce01e8 |  | checkpoint | Visual check for water & oil leakage
checkpoint-status | a8452c84-08b5-46b0-95b2-10a0327e6f0a |  | checkpoint | Mountings fixed & torqued down to plinth
checkpoint-status | f43b2941-ab26-4160-8ff4-fd69c90a0acc |  | checkpoint | Inlet pipework is installed & connected as per design
checkpoint-status | d6255960-b54c-4c75-8b2b-465e36e21a90 |  | checkpoint | Outlet pipework is installed & connected as per design
checkpoint-status | 88645359-e678-4258-9816-524c98cb5c5b |  | checkpoint | Diversion pipework is installed & connected as per design
checkpoint-status | f5ad01e6-8e0f-4ed8-ad1c-9b19080ebcca |  | checkpoint | Connection flanges fixed to manufacturer specification
checkpoint-status | 7f189098-fee6-45d1-b1c1-493d8f515b5e |  | checkpoint | Ensure data wiring is connected between control panels & operating to the manufacturers specification
checkpoint-status | 75715d57-7368-4489-b08f-fdf79a8d4f0f |  | checkpoint | Ensure electrical connection have been completed & certified by a licenced electrician
checkpoint-status | cd2586ec-ebc7-43e1-aa3f-82656abd9835 |  | checkpoint | Ensure the pnuematic pump is installed & operates to the manufacturers specification
checkpoint-status | 46396244-dfe8-42fd-b26a-e34063377124 |  | checkpoint | Provider to check the valve actuates correctly & test cycles the valve several times
checkpoint-status | bf2b96fd-c491-4a2d-9edb-d8945f52321d |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | c3daff71-0074-4b6b-b7e3-a007c36af750 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | ca1f9f2e-d469-4ed7-ab8c-1aa03bfdbb12 |  | checklist | SW Downpipes/Overflows (Grated Outlets) |  |  |  |  | Yes | SW Downpipes/Overflows (Grated Outlets) | 8cf98079-5c89-4fa7-87b2-6762594a1242
checkpoint-status | 139632d0-9941-44df-a0e9-f4750cf748e3 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | efc2a072-57cf-4cfc-a664-c68369476fe0 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | 8b7e6002-a799-45b0-b172-08195d2ba67a |  | checkpoint | Balcony (BO/OF) grates & bodies are installed in sizes & locations as per design
checkpoint-status | 6d29b237-9377-46d8-8293-f12bc1ed9d5d |  | checkpoint | Trench channels & grates are installed in sizes & locations as per design
checkpoint-status | 02c59c4c-1149-4a27-a249-020b0b2749c7 |  | checkpoint | Cast-in round/square (RWO/OF) grates & bodies are installed in sizes & locations as per design
checkpoint-status | bf1acc4a-dd50-4b8a-8d26-2a21ea631c33 |  | checkpoint | Cast-in planter box/tree grates & bodies are installed in sizes & locations as per design
checkpoint-status | 6355ad2b-1170-4cfc-b6cd-f9bb716737d5 |  | checkpoint | Downpipes are installed
checkpoint-status | 5ae1413b-7b35-4a35-819b-b00644106981 |  | checkpoint | Overflows are installed
checkpoint-status | 53103665-aff1-4134-9e6a-c542c9d595c1 |  | checkpoint | Penetrations are installed
checkpoint-status | 0d9e8db1-aa53-4b71-9f8e-e0e27ae916cd |  | checkpoint | Drain penetrations are caulked
checkpoint-status | b6c7516e-0d9e-4aaa-97a4-21ca7bf811bf |  | checkpoint | Trench channels & grates are installed in sizes & locations as per design
checkpoint-status | 10542f97-c53d-456e-9d91-7f462d6bfab4 |  | checkpoint | Cast-in round/square grates & bodies are installed in sizes & locations as per design
checkpoint-status | 00f719c7-d7d0-4362-8c4e-265c8069dd99 |  | checkpoint | Cast-in planter box/tree grates & bodies are installed in sizes & locations as per design
checkpoint-status | f9d4da3c-28b3-4029-9f85-68b979a97d51 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | 65f1c80a-2eda-4739-a266-f9b472e112d1 |  | checkpoint | Check inside trap for signs of debris etc
checkpoint-status | 5ada9ab1-358a-4977-a962-1685c9add4f6 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | 9b72104e-0a8e-4f22-bdcd-8e6de671e75b |  | checklist | FO Showers |  |  |  |  | Yes | FO Showers | 908c2c6c-910d-4871-8d62-2b5d61aa8549
checkpoint-status | a39513ee-167a-4d59-86dc-304fd88e3fae |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | d4910cae-7e92-492c-9e8b-14790c235933 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 05ec5230-667f-486b-98d3-c0c1e4d26e70 |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status | 570dd1b0-bf54-4c35-b750-c45f52539c78 |  | checkpoint | Solid installation of wall mounting plates, levers, wall rails & sprays
checkpoint-status | eb44ee61-139c-4b88-abcf-52fe12290939 |  | checkpoint | Check floor grate or channel for flush fit & alignment
checkpoint-status | 1df1e37c-2ba7-49a0-8518-5ded83004b94 |  | checkpoint | Check for flexible hose leakage
checkpoint-status | ce7e65c3-b8a1-4aee-a398-814986322aaf |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | 9901ad1f-42ff-41a7-b491-23113eb923b2 |  | checkpoint | Check inside floor waste for signs of debris etc
checkpoint-status | 6b3b1987-9243-45ac-af41-c6602c9edd49 |  | checkpoint | Operate mixer & discharge to floor waste
checklist-flat | 43822bf8-0e0b-4fa7-b6d3-3faccbd13ae0 |  | checklist | FO Thermostatic Mixing Valve (TMV's) |  |  |  |  | Yes | FO Thermostatic Mixing Valve (TMV's) | 9259be96-55b7-4c87-8280-229b0f4196fc
checkpoint-status | 2302f8e5-1534-4287-b432-d9bc7b4c92a9 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 1553a07a-6370-4a4e-86e2-841593b7c72b |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 416ecf6f-f9b1-4eff-8402-90874342fb3d |  | checkpoint | General finish & alignment both level & centre of tapware
checkpoint-status | d51f505a-eb77-49c3-bc83-675b7cdf66d6 |  | checkpoint | Solid installation & mounting of tapware
checkpoint-status | e99bf9cd-e9e6-4840-ae88-998645244aec |  | checkpoint | Check cover plates are installed
checkpoint-status | b97b8fe5-4fc8-46ff-af9d-f9671520990f |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status | dbd69e55-27c3-4bb6-906b-558efca9dc85 |  | checkpoint | Valve tag or signage is installed if required.
checkpoint-status | 9061ad88-8c77-4f7c-b828-932bfd1e5653 |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | c35c9a6c-8803-4675-8c5e-6136afec56d4 |  | checkpoint | Temperature test warm water to ≤ 43°C
checkpoint-status | 5b699cec-cf49-435b-b301-9419df02c979 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | c6ed048d-a5a0-4725-aeff-8fd7d1b31493 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 5a75e9f8-b58f-447c-b91b-3dfe0e55cd70 |  | checkpoint | Test sticker to be adhered to pipe inside wall box or in a visible position
checkpoint-status | 117e5a3a-efe8-4aad-b03f-bea0bd852920 |  | checkpoint | Valve is securely turned off (if required)
checklist-flat | 6cebf7f5-4f1f-44b6-9d1e-92c745a96446 |  | checklist | TST Testing Roof Downpipes (Air Test) |  |  |  |  | Yes | TST Testing Roof Downpipes (Air Test) | 95bc8d7a-020a-4a09-aaae-99fb2ae0069b
checkpoint-status | 4407e1be-c60f-4d9b-ab01-7765bf0871e0 |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.3 (2018)
checkpoint-status | 7c3d8e8e-f367-4bb9-a3c1-c79bb3dc086f |  | checkpoint | Ensure bore is completely free of any blockages, constrictions or debris
checkpoint-status | 94dcc042-a003-4e87-96c9-26e81a9ac7a1 |  | checkpoint | Ensure pipe-work is securely fixed to eliminate movement during pressure test
checkpoint-status | 04cc8620-9750-4295-9c85-fb8d1a07b45a |  | checkpoint | Temporarily plug & seal open ends of pipe-work section to be tested
checkpoint-status | f1dadf99-e09f-481d-b663-9015e5853af5 |  | checkpoint | Provide a temporary valved test point with union fitting
checkpoint-status | 68424959-63da-42f6-a680-3c23665cca19 |  | checkpoint | Connect pressure testing device to temporary valve point
checkpoint-status | acb671be-11b4-4288-b96f-33c410b930ef |  | checkpoint | Commence choke point testing by slowly increasing pressure up to 30 kPa
checkpoint-status | 7a2c54ea-3515-405c-af2b-66e8bdf4a7ea |  | checkpoint | Hold test at 30 kPa for 3 minutes
checkpoint-status | d977f713-c1ee-44b1-a0b2-8842e98d101e |  | checkpoint | Testing is deemed successful if no pressure drop is recorded up to 3 minutes
checkpoint-status | faaa8b52-cd02-4659-9911-369d6a4e2bbe |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral working conditions
checkpoint-status | 5a5d6bfc-96a6-46fe-8e55-54b5eb2caa64 |  | checkpoint | Test sticker on pipe 1500mm high facing a corridor or accessible wall
checkpoint-status | 1b899ced-cd69-4522-bbb6-ebed2dccae62 |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | 29cf61cf-9150-4652-8aa4-ef970f1756da |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | ed5b8522-b3a1-433b-b59f-b2e41d91d227 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat | b3091020-c148-4cb0-b716-f9bdef1e6ebf |  | checklist | SW Stormwater Drainage (In-Ground) |  |  |  |  | Yes | SW Stormwater Drainage (In-Ground) | 9c001e6d-8ce2-4335-8de2-01a66e88f36f
checkpoint-status | b8365a0f-4937-496e-92ef-f63fc1e63d03 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 513944d8-ecb7-4247-9092-74daf11497f0 |  | checkpoint | DBYD received & verified before commencement of work
checkpoint-status | a6b17e5c-b740-4849-9bc8-462acc5070e9 |  | checkpoint | Authority applications for stormwater drainage & start work notices accepted
checkpoint-status | afcb4eab-1390-4892-b00b-a8427df972ff |  | checkpoint | Municipality connections installed by Richstone
checkpoint-status | 85040453-cc71-4851-bf85-73038730525c |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | 8529ac57-8a5e-4ee0-99ed-ba3098c80178 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 069df380-c34b-4f27-abfc-e851043ad2a7 |  | checkpoint | Ensure all grades are correct
checkpoint-status | 80e6f829-4fee-4e51-9a48-22568e9e2b35 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | d1e94e9f-3397-4d0e-8bd9-0302f585e88a |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 962d3107-fd6a-45c9-8c4b-92bda242b7f6 |  | checkpoint | Clips & Shanks etc. are completely corrosion protected by use of "Denso" type wrapping & sealing
checkpoint-status | 571bfdfa-9dee-4e4c-a502-390b4c76845b |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status | f5f0a31f-4c35-49e7-bb71-ee8a121cbed9 |  | checkpoint | Spoil is removed
checkpoint-status | 5906c341-517d-4e37-ba24-4e62281d78cc |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 5e77ea1c-419b-4b56-8646-5b573154c8bf |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | dcc2401a-e48e-4eda-a630-4339d2b690c8 |  | checkpoint | Check traps are correct locations, finished heights & clear of debris
checkpoint-status | dfc3a690-9479-4c61-848b-7418aec73a86 |  | checkpoint | Rising mains installed & connected if required
checkpoint-status | 7fdb2f9d-c092-4cae-adcb-7a9e7f2d132e |  | checkpoint | Marker tape installed
checkpoint-status | 1c3896ca-1f42-474e-a63f-6ddbb45f02e0 |  | checkpoint | Drain penetrations are caulked
checkpoint-status | 62142e56-22e4-4d12-ad2f-4d5f038784ba |  | checkpoint | Stormwater junxtion & grated pits are installed in sizes & locations as per design
checkpoint-status | 88012b0c-991e-4aa4-b607-2e7f4141f805 |  | checkpoint | Trench channels & grates are installed in sizes & locations as per design
checkpoint-status | 7c5488e3-bcf3-4cd7-869d-839164b7aa94 |  | checkpoint | Cast-in round/square grates & bodies are installed in sizes & locations as per design
checkpoint-status | 28528542-a917-4756-b4f1-01e8c64164a5 |  | checkpoint | Cast-in planter box/tree grates & bodies are installed in sizes & locations as per design
checkpoint-status | a6a8492c-1ed2-4d88-9028-712f161d8544 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | e5559603-6ad3-4805-835c-9633804f709c |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | 4498cf2c-1445-4bae-a2fa-c74d51e30bbd |  | checklist | TST Testing Reduced Pressure Zone Device (RPZD) |  |  |  |  | Yes | TST Testing Reduced Pressure Zone Device (RPZD) | 9fd0804b-389f-4709-8368-beccdd86bba0
checkpoint-status | d75c0c00-8c56-4696-b5d5-4c1403aea5a1 |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.1 (2018)
checkpoint-status | 630ca4ab-3ef1-425b-a226-286f5e34163a |  | checkpoint | The tester is qualified & trained to carry out the testing procedure required
checkpoint-status | afb54007-3de1-474e-bbb8-c1d12ab9ea99 |  | checkpoint | Engage a certified/licenced specialized sub-contractor to perform & document this test
checkpoint-status | 5d6fb3e1-38e2-4b01-b0fd-e5907e2659db |  | checkpoint | Request & receive a signed certificate of successful test result
checkpoint-status | 625fe90d-2d1f-4d2c-9ada-fd66c85fa946 |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status | 6a97b7ce-ea55-478d-b8a1-0416092242dc |  | checkpoint | Test sticker in visible location
checkpoint-status | 804274e4-8e0b-4767-aaa7-54332477689c |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | 28e92426-7cef-42a2-874d-22d9423d3d85 |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | 520a88b5-24bb-4dcd-bce9-832392886676 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat | ff956960-6e27-4227-bede-84ff8f18e39a |  | checklist | SD Stacks & Vents (Main Droppers) |  |  |  |  | Yes | SD Stacks & Vents (Main Droppers) | a2cd0e89-6009-4709-b978-254cb494faba
checkpoint-status | 7941410a-3c37-4764-8295-d8685904a9f2 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 0bf5d5e7-4b3e-4eda-8100-643cbcf9bcdc |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | 9e9b0deb-af77-464e-86d9-bc39fa1f910b |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 5df94118-fae5-47ee-bd5d-c2c65a6b41e1 |  | checkpoint | Sewer stacks are installed
checkpoint-status | 92bba95d-01a0-45d4-8194-2ea195b058e3 |  | checkpoint | Sewer vents are installed
checkpoint-status | 622c82f7-357a-4f21-a34e-6ffb1921cc46 |  | checkpoint | Cross vents are correct
checkpoint-status | 4efc1fba-9185-4a2d-a3bb-0c550507e0f3 |  | checkpoint | PAPA vents are installed (if applicable)
checkpoint-status | 0f313ecd-8542-424a-ac23-cee999c8286c |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status | 6c84ede1-4f9d-4252-bbf4-d81d02aed08d |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status | 44f3e762-d837-4bf9-b270-ef24d1984559 |  | checkpoint | Stack base I.O. is installed
checkpoint-status | 93ce5784-3d0f-42cd-82cc-67b73949735b |  | checkpoint | Stack bases supported correctly
checkpoint-status | 7b48acd5-5db6-4aec-b32a-be93332ef6d3 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 00148390-f71a-430c-b742-00bc50dc50b8 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 3d34168e-1faa-4944-83c3-b117c0289590 |  | checkpoint | Penetrations are installed
checkpoint-status | 17ae0545-37af-4c59-82cf-c6fc8ce70253 |  | checkpoint | Drain penetrations are caulked
checkpoint-status | fd0c08d2-355d-43d5-bec6-e861f0979851 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | 28d96a95-4ce8-4482-b49e-bc1064f61bcf |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 99a8002d-b7a9-4bc5-add3-9af9c82181cf |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | aa4a3e98-871d-4e2b-a5bd-10ffe8c21ecf |  | checkpoint | Check traps are correct locations, finished heights & clear of debris
checkpoint-status | 46a1fbc1-c953-4cf2-813b-e584503bc895 |  | checkpoint | Rising mains installed & connected if required
checkpoint-status | ec391417-091d-4965-a4cc-fb7634823e30 |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status | f40a5919-ae91-4829-ba93-a296e3bde413 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 9cd22b2c-7405-4c07-90a2-f8dd4ddccf57 |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status | 7022f71b-cd1e-41e5-a479-3073cd245874 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 6e14e3bc-2ee5-45e4-a372-3ca6bd980f21 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat | 7a119e10-93ae-49f1-a3a6-beaf6be2f7a4 |  | checklist | PE Above-Ground Rain Water Storage Tank |  |  |  |  | Yes | PE Above-Ground Rain Water Storage Tank | a6785ef9-8b47-42a1-a5ec-403671fff966
checkpoint-status | 2247d7ac-66bc-4b52-9314-63af84522c72 |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | 259d64be-1563-4b73-bf82-f1b207bd437d |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | 1d3d6a44-6044-4eb4-b592-464fed8ce987 |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | e62a7278-0322-48af-b7f3-99a8f04141f4 |  | checkpoint | General visual check for damage, etc
checkpoint-status | 2e42a238-cef1-4212-89b2-130332151b68 |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status | bca5bfba-7453-4490-90b0-d51ced0bbad8 |  | checkpoint | Vents are installed if required
checkpoint-status | b47c024d-da8a-4c95-8a78-e224b379f8df |  | checkpoint | Inlet drain is installed & connected
checkpoint-status | 6baf48f2-19bf-441f-bb18-0069a16803cd |  | checkpoint | Outlet drain is installed & connected
checkpoint-status | e220d33e-1833-4d63-9725-0a2e2c2ed0bf |  | checkpoint | Overflow drain is installed to discharge over stormwater pit
checkpoint-status | af9bf4b3-3925-4d2d-96c3-651b68cdd69b |  | checkpoint | Isolation valves are installed (if required)
checkpoint-status | bacb02bc-497e-412e-828f-cdb76b81c6b1 |  | checkpoint | Suction line installed & connected
checkpoint-status | c90f4f5c-78ef-4c92-8064-40e317da820c |  | checkpoint | Isolation valves are installed (if required)
checkpoint-status | c81aecd7-bf9c-4d82-8fcd-c30002f4c7f5 |  | checkpoint | Electrical cable is installed
checkpoint-status | 02e776b2-f024-4f3b-a473-6504fefedc2d |  | checkpoint | Control panel is installed
checkpoint-status | 4417ea46-4e3d-4ed4-bdc0-d383ace5e678 |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status | 8a0c6a07-2ca9-415e-b58c-052dfe98d0ef |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status | b3ce1d75-0ed5-4e24-9603-8d61a8c71e3d |  | checkpoint | Tank provider installation certification obtained
checkpoint-status | 28037e31-0493-408c-9b1f-83a0541a3136 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | b7069851-e9e1-4659-bf08-cfe3b3c4502c |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | c8b92ed3-193f-4219-ba2d-97014d5ba950 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat | f6aada93-a150-4f5c-ab8d-37238c410612 |  | checklist | NG Risers |  |  |  |  | Yes | NG Risers | a708366d-6a58-4e2a-9c0d-c5859e48b7a0
checkpoint-status | 8e9cf19d-3740-4095-a809-783dc51a8be2 |  | checkpoint | This installation and following checks are to comply with AS-5601
checkpoint-status | e9c1e589-1c5d-49a0-9916-ee9bb05e543e |  | checkpoint | Authority applications are completed for work to commence
checkpoint-status | 93d770e3-4381-45ce-8c94-36471fbdad00 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 13f0de7e-a714-4248-a272-06c59132bb13 |  | checkpoint | Penetrations are installed
checkpoint-status | 855635fa-749b-4adc-bce5-17f11163378e |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 1b0cc16a-c502-48b6-a9a5-373d67491e9f |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | ae814549-49ab-4b30-979b-65b71808d99c |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 447b343f-b68e-472b-8cc6-27c33a9e6a76 |  | checkpoint | Ensure all risers are installed professionally with no abnormalities
checkpoint-status | 239a3936-5597-4d4f-99ad-911406792375 |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | 8f48c33a-97c1-451a-a2a6-e911b9431d93 |  | checkpoint | Welded pipe joints are completed
checkpoint-status | 10645813-4546-4205-8b2b-52cafad75b7f |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | 0fb3474b-44d8-4f1b-84e8-4936b77aa47b |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | d3202c05-1c80-41ad-ae4a-4b8fc6ff9274 |  | checkpoint | Pipe penetrations are caulked
checkpoint-status | 53aa107c-c5ef-4100-b046-fb5382f072cc |  | checkpoint | Anchors are installed as per manufacturer instructions & compliant with AS3500
checkpoint-status | 5a38ccc5-7870-4cd9-ae3d-1fc67b315212 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | dc646945-1082-49cc-8c21-69c4e2c2bd56 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 5e0aab60-8b5f-4b08-a38f-c11ce3073959 |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | 7c9abfc3-2a48-48bc-8011-697106de547b |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | 228e1146-732c-4775-824b-658b50f43e82 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 68f6cabf-7219-427e-bfcd-1c64403a25ba |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status | 4754abc0-409a-4710-a2ad-9c9313dc1eec |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 8281face-b55b-4a14-9be6-2d93df7719cf |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 8a6cfdb8-aa9b-4f96-b538-2609b0fa2715 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | b208642e-dda9-41be-b93b-fee0637e06f7 |  | checklist | FO Drinking Fountain |  |  |  |  | Yes | FO Drinking Fountain | a9659aea-e8b9-4fbe-951f-d96265d505bb
checkpoint-status | 53b29557-010a-4a22-955e-9d844d67e530 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 445ca55b-d94c-4c5d-a5a6-11f237652248 |  | checkpoint | General finish & alignment both level & center of fixture/tapware
checkpoint-status | 28f1d815-f73e-43c3-b993-80fed1b94571 |  | checkpoint | Solid installation & mounting of cabinet, sink bowl & mixer
checkpoint-status | 2183d46f-f356-4738-bf75-ca94afc78077 |  | checkpoint | Check in cupboard for signs of leakage
checkpoint-status | e4e9fdde-962c-4f23-9cf4-cce5e0c7846f |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status | 32e34e67-9732-4aac-82d9-b1ac92c6b7d4 |  | checkpoint | Check mini stops for operation & leaks
checkpoint-status | e044d4d6-d4c0-4e57-99f9-175ff444b31f |  | checkpoint | Check pressure reduction valve if required.
checkpoint-status | 4b8958d9-b76d-4011-99ed-220c01f6be42 |  | checkpoint | Check flexible connections for leaks, kinks or twisting
checkpoint-status | 14a54af2-7448-4ab4-8736-75ae0cd892bb |  | checkpoint | Check trap is installed & nuts are tight
checkpoint-status | 85dc06d6-e7da-4ac5-9d8a-2e42724eb186 |  | checkpoint | Adjust & throttle water flow-rate if necessary
checkpoint-status | a3f998b8-6ba0-4c90-9d2d-493808f08c55 |  | checkpoint | Check trap & waste pipe connection for signs of leakage
checkpoint-status | 23f4e928-1a16-4509-bfa2-abdf33f79fa6 |  | checkpoint | Check inside bowl trap for signs of debris etc
checklist-flat | 852a84e3-b161-47bd-a95f-824fa20869e7 |  | checklist | MT Re-Cycled Water Meters |  |  |  |  | Yes | MT Re-Cycled Water Meters | acf1666e-2b56-42ee-9285-49e5fa409ec8
checkpoint-status | e3244d10-d284-4810-97aa-95df138651e7 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 2376ed94-c9d3-462d-a5e2-0a0d7f764355 |  | checkpoint | Water Meter Details:
text | 0b3b7f8b-4d64-5d05-938c-418b59d75565 |  | textbox | Meter No:
text | 07a2bc3e-35b6-5ecb-abb9-0bfa36f43e13 |  | textbox | Meter Location:
text | db04ee19-5823-560d-8e77-1f5e10647140 |  | textbox | Meter Size:
checkpoint-status | bd83844f-7135-40d2-9938-8e50e65a6a31 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 15017363-0efb-466d-96cd-075e089cec2f |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | 3e41572b-b13c-4fea-aa00-55bc1d8c7260 |  | checkpoint | Meter bracketed
checkpoint-status | a5182713-f909-4441-ab51-64b29e9de8d2 |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | 113a4131-fc93-4da3-a9fd-351c2158e541 |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | f94c06b3-72dd-47c7-acbf-c91ace7e36c7 |  | checkpoint | Pulse rate value is correct
checkpoint-status | ae3a0afd-e69d-47b8-adc8-9276bda4e3e5 |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | 848aeadd-3e37-413e-859d-e8084240bcf9 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | 990dc4e9-b95c-43e0-b6b1-5b71f3884cff |  | checkpoint | Flow direction is correct
checkpoint-status | f6021ffa-a1ed-4234-929f-6e2b8421d80b |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 70fe2cfa-3b6f-484e-97e0-42b25b33fe36 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 4f7e7d4b-8fa4-4250-a421-e268c34aecb3 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | e33df46f-2ba7-42c4-a844-d5ba772856e9 |  | checklist | FC Floor/Wall Penetrations |  |  |  |  | Yes | FC Floor/Wall Penetrations | afed1aaf-0bfc-45a4-82c7-09ffe7599260
checkpoint-status | 6e542ab9-2de5-42ca-b1fd-b76dfabaa949 |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | 58991598-97c2-4a44-9b40-b758eb11ae7a |  | checkpoint | Confirm all penetrations locations are as per current IFC documentation
checkpoint-status | faea985c-0a8c-4e61-9e4b-89276d2a89af |  | checkpoint | Check both alignment & height are correct
checkpoint-status | 02adecd7-eb1b-4f81-ad41-9b510ecd196c |  | checkpoint | General visual check for damage, etc
checkpoint-status | 1349e7f0-cb3c-4b47-801b-9a82dfd37f69 |  | checkpoint | Check (floor) fire collars are rated & sized as per current IFC documentation
checkpoint-status | 54a75285-8937-4813-8752-aa5e51dbf295 |  | checkpoint | Check (wall) fire collars are rated & sized as per current IFC documentation
checkpoint-status | 298add3d-7993-440c-935a-1739a70298c5 |  | checkpoint | Check fire wrap is correctly rated & located as per current IFC documentation
checkpoint-status | a735a07e-3c69-4bbd-accd-cdc17f1af4a7 |  | checkpoint | Check metal sleeve penetrations are sized & located as per current IFC documentation
checkpoint-status | f7f43e84-f263-4b14-9af6-9a19d43addfc |  | checkpoint | Check cast-in roof outlet/overflow bodies are installed in locations & heights as required
checkpoint-status | 1cd26d83-4093-4c3c-9632-c5b645344c90 |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status | bb439a32-9ba5-480b-92b2-0f50d8949fec |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 949e0ba6-8bba-4350-877b-64705773388e |  | checkpoint | Check all fire collars are Logged & Registered
checkpoint-status | b9574a27-84d8-4331-8a27-0ca5af05b3f0 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | cc7e5904-94b5-4485-b737-cb616db0166c |  | checklist | WW TMV/TCV Rough-in |  |  |  |  | Yes | WW TMV/TCV Rough-in | b123db2d-e198-4620-aa4f-71726c86dde2
checkpoint-status | 27b823bb-558a-4f22-8be7-e96c8ab62ce7 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 5eabc3d2-49cb-4ce9-b3fa-a1ba064ce728 |  | checkpoint | General finish & alignment both level & center of fixture/tapware
checkpoint-status | 206ea6fd-13cc-4665-b92b-486716f18b2e |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | e59105ba-0a41-4af9-8801-6b1e2896e616 |  | checkpoint | Check silicone applied to studs
checkpoint-status | 20f3a3ba-5cc8-4763-a9fb-0fb9b86338c0 |  | checkpoint | Wall box is installed if required
checkpoint-status | 0cc60f13-d595-4784-b831-1f88ef9f3895 |  | checkpoint | Check TCV/TMV correct location & securely clipped
checkpoint-status | e4fe5227-4642-4069-999f-aff68bcc54ac |  | checkpoint | Check for possible cross connections
checkpoint-status | b18c97fd-bd2c-4680-b7e4-ad7f2dfa0aaa |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | 489d89de-a1c1-4a50-b61a-6cca8754b3ca |  | checkpoint | Test result is compliant with AS3500 (Record test by photo & time/date)
checkpoint-status | 6ec7cf4b-1c11-40ae-a908-8a9dc5d39815 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 55dc583f-d65b-4a14-bf27-c038d6ea18f1 |  | checkpoint | Seal or cap off any open ends if required for security
checklist-flat | 4a491bdf-fe91-4904-8d7d-f41741ce776b |  | checklist | checklist |  |  |  |  | Yes | New Template | b4803b92-ceb7-4c39-be74-9c6d8db9f1da
checklist-flat | f8ace16a-6393-4e03-b05c-cf04aa7980a4 |  | checklist | TST Testing Potable Water (900 kPa Test 3) - [Island Sink] |  |  |  |  | Yes | TST Testing Potable Water (900 kPa Test 3) - [Island Sink] | b621280d-0401-4522-a615-425c60c6d227
checkpoint-status | 540198af-590e-4ce7-a645-37a27a38cbbe |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.1 (2018) &/or AS-3500.4 (2018)
checkpoint-status | 9cc75e12-d155-4078-bd40-679d5b921eeb |  | checkpoint | Ensure all valves dedicated to isolating the test zone are securely shut off & tagged
checkpoint-status | 0e59f5de-4b9c-4826-9e05-f7df39a683d3 |  | checkpoint | Nominate an air purging valve point
checkpoint-status | 42af5337-9ec6-4985-8158-619b4874ec1e |  | checkpoint | Nominate a pressure testing valve point (if none at meter manifold)
checkpoint-status | 56d23694-c620-4561-aaff-091a572bdb03 |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status | 12c3b941-66e7-4e77-8f42-d721a721d3f4 |  | checkpoint | Ensure all terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status | 2bd6478f-03b9-4496-95bf-7208904b1de2 |  | checkpoint | Slowly open a feeder valve & fill the test zone with water until completely purged of any air
checkpoint-status | 162e9c98-36ec-4f06-b6e0-86bc3c49aa44 |  | checkpoint | Connect pressure testing device to the nominated test point
checkpoint-status | 9144910c-3090-4b6d-acc4-89f3386e37e8 |  | checkpoint | Shut off the water feeder valve
checkpoint-status | 8cc8f244-0182-494a-8b09-abdbb6368de1 |  | checkpoint | Commence testing by slowly increasing pressure up to 900 kPa and hold for 30 minutes
checkpoint-status | 817f2a10-ff15-45f0-9d4f-42931bd192c2 |  | checkpoint | [For Couta System] Release pressure down to 500 kpa and hold briefly
checkpoint-status | ab80d119-bcf2-4238-8b0d-59e55342a82e |  | checkpoint | [For Couta System] Rapidly increase shock pressure back to 900 kPa and hold for test duration
checkpoint-status | e6637bed-01f9-4b2b-8eab-47399c44539d |  | checkpoint | Testing is deemed successful if the water pressure remains unchanged after 30 minutes
checkpoint-status | 66c4ef08-43a1-49fb-ae3c-204a66ecaa60 |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status | 8e633bc9-7c2d-441f-adcf-015298486fde |  | checkpoint | Test sticker in visible location
checkpoint-status | f42ea759-f5d8-4d76-aaa4-d60ccbd1d495 |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | 2b8955da-cd96-47c8-8f92-d82025d8733d |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | b4cfcfef-7c0b-4f8e-85a9-1336139cc098 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat | 6bab71a3-858f-4a08-9a86-6039e9b0646d |  | checklist | NG Rough-in (High Level) |  |  |  |  | Yes | NG Rough-in (High Level) | b6e58e87-0e3a-4956-9caa-a91439e15333
checkpoint-status | 8b9abd83-6fc9-480d-8a5c-33e35b6538a4 |  | checkpoint | container
checklist-flat | e681976b-4ad0-452c-b3ec-c99277f9dcd9 |  | checklist | PE In-Ground Stormwater Pump Station |  |  |  |  | Yes | PE In-Ground Stormwater Pump Station | b7213c4a-2cc3-43eb-abaf-10761d0fd8fc
checkpoint-status | 6095d800-a3e2-4aa3-ba78-cb385d194760 |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | f4bb1123-18b5-46ad-8a09-68acb49af26c |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | 29c37349-e102-4fd0-b81f-42eb4983cd86 |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | 46089c82-6558-46a2-a103-02e4aa4a2d2d |  | checkpoint | General visual check for damage, etc
checkpoint-status | faa0342e-6957-4345-960d-787f1e0d28cf |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status | e3df8eef-db9f-4fd6-a079-697bb65e4677 |  | checkpoint | Vents are installed if required
checkpoint-status | 86b27655-6447-48f1-9611-a213c919ce4a |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status | 6a25d2bb-fd51-4699-9ce9-d978f36812ab |  | checkpoint | Spoil is removed
checkpoint-status | 36c3dd18-6968-41c8-a32c-203bfcf871b9 |  | checkpoint | Inlet drain is installed & connected
checkpoint-status | a1d6c9e5-e606-4e72-ba53-edc56c7549b9 |  | checkpoint | Outlet rising mains installed & connected
checkpoint-status | d6dccf8b-8c1c-4bfa-bf38-d592c903a2a7 |  | checkpoint | Electrical conduit is installed
checkpoint-status | 9dde6184-5c56-40cc-85b3-63a7e97672f9 |  | checkpoint | Electrical cable is installed
checkpoint-status | 7892e77d-a2ad-4b9a-b30b-3b4a947b07f9 |  | checkpoint | Control panel is installed
checkpoint-status | 6a1a1f81-316e-4ded-9920-7dd63d8fa569 |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status | 3b7c5611-7633-461a-b986-9ac0d262dc70 |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status | d78dd29d-c8dc-400a-bee4-ee3a351288aa |  | checkpoint | Pumps cycles set & test run & certified by pump provider
checkpoint-status | b4f70a3e-0e1c-4c07-9d93-1ea5c3a48da6 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 4dffaec9-a6e8-4626-8ea8-ba2a451e099d |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | 77d551e9-5678-4f90-aeb1-1fdffe4ac0cb |  | checklist | Peno - Wall |  |  |  |  | Yes | Peno - Wall | b7c9408d-238c-45c1-b187-8f2878606cd5
checkpoint-status | a53ff6c4-89cc-4308-b297-d02524bfea5d |  | checkpoint | Installation complies with current IFC shop drawings
text | 1de11901-d881-5c25-9bb2-3efc22992481 |  | textbox | Document invert level wall peno has been installed at |  |  | mm
checkpoint-status | 04871f94-087b-4b4e-9be6-59250eb088c4 |  | checkpoint | Collars and sleeves are capped & sealed
checkpoint-no-status | 591c5895-2631-41ec-8aa9-d77eab96a34b |  | checkpoint | Concrete pour details
text | 8daada6f-e51d-5b22-b00f-21a4d4ae94ff |  | textbox | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | 93438107-2f43-4987-a004-75991fccc064 |  | checklist | PE In-Ground On-Site Detention Tank |  |  |  |  | Yes | PE In-Ground On-Site Detention Tank | c1446ec7-71a7-49f7-872e-20839849149d
checkpoint-status | a4e67305-52d5-4b6d-81a2-8e486ea819b6 |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | b2526c7e-cada-41ce-9127-d325003c04b8 |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | 5494983b-7424-4992-a60f-05d87635002a |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | a2583272-3335-4ad8-8de8-67179160945f |  | checkpoint | General visual check for damage, etc
checkpoint-status | 06349107-db23-4e19-8ffe-6c9aeb5b273d |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status | afe85473-48ad-4033-a0da-fe23d9557cb7 |  | checkpoint | Vents are installed if required
checkpoint-status | c7787664-8103-45cd-a739-f7caa22df562 |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status | 04f34623-0621-4408-81cd-c2b5559f6741 |  | checkpoint | Spoil is removed
checkpoint-status | e0fbbb3e-e7b6-47c7-9d54-ba51f5e2ffa8 |  | checkpoint | Inlet drain is installed & connected
checkpoint-status | 1e082e26-916f-4524-af0d-e7a7b5aa780e |  | checkpoint | Outlet drain is installed & connected
checkpoint-status | 8ec407fd-7364-458b-becb-6525e4e3cf6f |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 1ea271ab-c641-4bad-8d8f-2c92aaa197b5 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | e29035ef-6fbb-462a-ab2c-c1e6b88dcc90 |  | checklist | SW Downpipes/Overflows (High Level) |  |  |  |  | Yes | SW Downpipes/Overflows (High Level) | c3ee1bd8-2bf9-4250-b7b6-7460fd457964
checkpoint-status | 78af03ac-992c-42d4-a0ff-59d1c2efa0d1 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | c16c8a1b-53fb-4d5b-90a9-c6d30cfddee6 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | bed223e3-ad5b-4770-b434-f2ac1efef06c |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 49d4f8db-7b05-4df5-a2e1-87769de0aa06 |  | checkpoint | Downpipes are installed
checkpoint-status | 88e358c0-002d-42a3-861e-a32f656044b7 |  | checkpoint | Overflows are installed
checkpoint-status | 9bd7eb7e-1950-48e2-9166-07fc8b02254b |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status | 66d9e700-bbea-417e-b497-895ce132a86a |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status | b1b48c37-0299-4757-9097-d3aa1a975906 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 09a8cf2b-d72e-4ba7-bf86-7812ba7b357b |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 3976a576-d100-4b97-af9b-5ccd302e32a6 |  | checkpoint | Penetrations are installed
checkpoint-status | b8ad3d8e-6819-4c95-beb6-7d4e7bf23286 |  | checkpoint | Drain penetrations are caulked
checkpoint-status | 409101f9-d5d6-4878-9ad6-932262b7c653 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | 12d5da9b-357a-4992-84f2-b8ce28f79475 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 11423a9a-f342-4daf-8f59-9a812a31960f |  | checkpoint | Roof/overflow outlets installed
checkpoint-status | 18ee377f-b158-4174-a138-b07e0973de31 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 12f24b0f-411d-460a-82e1-5048ececc487 |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status | 6ed63db9-7548-4d3f-af92-0a49c066b387 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 0bc66fb8-2c9f-4c8f-9613-7ad59fda85e5 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | caf63ef2-89d2-455d-a56e-f2a6a4e0be86 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat | 266c4210-4dd7-4940-b40a-e45f185a55d0 |  | checklist | SD Wastes & Vents (High Level) |  |  |  |  | Yes | SD Wastes & Vents (High Level) | c541a97a-c81f-4376-8bbb-17ab7ee0b5d8
checkpoint-status | 8f8908d7-0ec9-4e9a-a167-55d8c5d41fda |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | db277a13-3ce9-4797-af73-2ffbf9e7ad8f |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | d17d5484-f1a5-4caa-85ca-b62ac5456a7d |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 45dc78fb-7b07-4e63-b1f4-412fb4c99339 |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status | cec293e0-a50e-4cd1-a09c-32b587c45385 |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status | e89ec3d9-97d5-4de9-a9cb-031d9d999871 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | d0f8669c-6dd6-452e-b46d-ea0b9a50ecd3 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 7ce66702-73ff-40fd-a2cd-5620a8247ed4 |  | checkpoint | Fixture vent, group vent or AAV is installed as per design
checkpoint-status | b2d3ef0a-2a52-4954-ac6b-e19aa7163a71 |  | checkpoint | Penetrations are installed
checkpoint-status | 32c78a62-a216-48ee-859e-262247463fb5 |  | checkpoint | Drain penetrations are caulked
checkpoint-status | 289318ca-81fe-4487-b6dc-830fa20f459d |  | checkpoint | Fire collars are installed & registered
checkpoint-status | cd4dab72-fcf3-4da2-a7e3-7b4c72bd36b0 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 60518aea-b070-423e-af0d-4b066ce800fc |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 6d96d086-18aa-4930-8669-fc29f2bb9d47 |  | checkpoint | Check traps are correct locations, finished heights & clear of debris
checkpoint-status | 262266a9-6d6f-470b-9a57-2625f3d2a7bb |  | checkpoint | Rising mains installed & connected if required
checkpoint-status | fa6f1557-f51c-44d6-bb80-d5d21471b0f6 |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status | 78c3d6ea-377e-4767-bcea-3d0eff543fa7 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | c9161ee8-f454-4c19-bb30-64a1e1e26f61 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 3b53dce3-141f-4a6c-a737-b9336cdec7e4 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat | 3f01773f-2642-4800-9e7c-9f96f0e59288 |  | checklist | MT Cold Water Meters |  |  |  |  | Yes | MT Cold Water Meters | c5db2115-999f-4eb3-9df8-e3d11cdb314c
checkpoint-status | 8533f8b7-09b5-40fc-9e1d-924ab1188146 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | bff55e62-b354-46e9-b68d-7db909a9c884 |  | checkpoint | Water Meter Details:
text | c8e478b3-0ff5-547a-8b05-3e38f7a25a88 |  | textbox | Meter No:
text | d966d79d-275f-56a0-af85-a2bafe1ad881 |  | textbox | Meter Location:
text | 6b4931a0-6245-56c4-9b12-1ff53e4714c3 |  | textbox | Meter Size:
checkpoint-status | adf61660-7b9b-4572-b31f-97864484273d |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | f4a0fc37-1db5-4645-b06e-f2a34c4bd5f8 |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | 1c12c5d8-1aae-457a-bd3f-0176f722944f |  | checkpoint | Meter bracketed
checkpoint-status | 0308d782-9300-41a4-88ef-4c6afc2ce2eb |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | cf772497-667f-4609-acb8-7abab64ea7d0 |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | 9cf737ff-7328-4191-b6d5-991cab841c7c |  | checkpoint | Pulse rate value is correct
checkpoint-status | 4f64a605-56fd-4539-a5f0-95a2d40770c9 |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | 176e9c5c-577a-4fcf-ad01-00c2dae00a23 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | 9208746c-8599-41f0-adce-c98cc70483b2 |  | checkpoint | Flow direction is correct
checkpoint-status | 9b83986c-32fa-4ed8-8ef1-db0b55ce1552 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 67e9aa3a-2476-4338-bbc7-afe434e7331b |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 839d76ff-eed3-4d2f-b985-fda84b1fdc37 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 1c2915eb-5071-442c-bf55-da52b92dcecb |  | checklist | PE In-Ground Sewer Pump Station |  |  |  |  | Yes | PE In-Ground Sewer Pump Station | c823c564-abf5-44d7-9dd5-84cf8f92eb37
checkpoint-status | 319f65ee-a82a-406f-bd86-c830a2aa06fb |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | f7abb189-83b6-4a6d-a945-a9758f9962cb |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | 11ac37bd-53db-41ad-b5b8-b247a234cefa |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | 58d18dd2-92a4-4f74-92d0-00c555593b62 |  | checkpoint | General visual check for damage, etc
checkpoint-status | 7bd8cb26-73a3-4d8e-aa3e-06c7efb6e0b9 |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status | ed53daf7-b26d-4ec9-b703-3082a0772c26 |  | checkpoint | Vents are installed if required
checkpoint-status | 6449a620-a553-45fb-84ac-988e1fc15f84 |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status | e1b95dbb-5853-43f9-b9f5-546d7e02bc68 |  | checkpoint | Spoil is removed
checkpoint-status | 16ff8d8f-a269-46e9-8942-04d35fabc214 |  | checkpoint | Inlet drain is installed & connected
checkpoint-status | c19644a0-d4a0-4364-bc18-7e8b88053a63 |  | checkpoint | Outlet rising mains installed & connected
checkpoint-status | 330cf135-a2bc-4b1a-93e3-4f8bb674621d |  | checkpoint | Electrical conduit is installed
checkpoint-status | eb236ccd-f71b-4d56-b529-48170e0480e3 |  | checkpoint | Electrical cable is installed
checkpoint-status | 59e8e31f-c6ff-4627-9409-5f1efd66edd7 |  | checkpoint | Control panel is installed
checkpoint-status | 470751c2-1980-4651-a771-e33b1e98d95c |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status | f5f09f07-269d-4894-9ef3-6db1a63d8aa7 |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status | 47cfd242-15f3-49dd-9651-e46601303f95 |  | checkpoint | Pumps cycles set & test run & certified by pump provider
checkpoint-status | fc2c8e69-39d8-40f4-8b79-32b512ae5086 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | e424278f-32fe-413c-abde-0d69ac441abb |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | 05f90333-6bad-45b7-b051-05a26d42a25b |  | checklist | TST Testing Potable Water (1500 kPa) |  |  |  |  | Yes | TST Testing Potable Water (1500 kPa) | cc38e78d-76b2-4410-8990-148fbe4ab5d8
checkpoint-status | c280f7fe-a952-4180-83fd-753e2c64ce5e |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.1 (2018) &/or AS-3500.4 (2018)
checkpoint-status | 0cc0d62d-c320-47d2-bb33-db765877f376 |  | checkpoint | Ensure all valves dedicated to isolating the test zone are securely shut off & tagged
checkpoint-status | b5d68d34-9e15-4d70-a399-646dc8378a11 |  | checkpoint | Nominate an air purging valve point
checkpoint-status | 8a2bb612-6f05-4b49-871c-219a3c157ca4 |  | checkpoint | Nominate a pressure testing valve point (if none at meter manifold)
checkpoint-status | 05e61a94-4910-4878-9373-62742344bd02 |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status | 0d4fec3a-7f75-41bc-9dbe-e214ef3a62ac |  | checkpoint | Ensure all terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status | cc166192-8c70-4ab5-8645-36a5a31105b9 |  | checkpoint | Ensure all in-wall mixer assemblies & pressure sensitive meters, etc are isolated/removed from the test zone
checkpoint-status | 7c292632-19bb-4185-a170-9ca52bee860b |  | checkpoint | Slowly open a feeder valve & fill the test zone with water until completely purged of any air
checkpoint-status | 6dbae139-4943-448a-869e-acd3a2ffa646 |  | checkpoint | Connect pressure testing device to the nominated test point
checkpoint-status | 09a6d2e5-78d9-44cc-8586-4d8c79ed0dda |  | checkpoint | Shut off the water feeder valve
checkpoint-status | b91a3f22-3a36-42ce-a7f7-21257d150150 |  | checkpoint | Commence testing by slowly increasing pressure up to 1500 kPa and hold for 30 minutes
checkpoint-status | 108344ff-9535-4ba9-872e-a67a8fb72e78 |  | checkpoint | Testing is deemed successful if the water pressure remains unchanged after 30 minutes
checkpoint-status | 00033189-574c-4e55-abc7-88c500d6663d |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral working conditions
checkpoint-status | edd51325-8933-4b66-a8ec-0c77c6d60f24 |  | checkpoint | Test sticker in visible location
checkpoint-status | ec38c39a-05b5-4e4e-b7a8-abc8a63e161d |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | 555414e2-7fb6-4844-b89d-08949e181aa2 |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | edc0a378-b742-414b-a42c-5aea6dd95015 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat | 6a59addf-7996-4c6f-b63d-467eddc0db90 |  | checklist | PE Above-Ground Large Hot Water Circulating Pump Package |  |  |  |  | Yes | PE Above-Ground Large Hot Water Circulating Pump Package | cf93b81c-6ff9-4e63-9089-1b96e646ef1c
checkpoint-status | f8c62dde-7e25-4288-a9f9-08164ac0affb |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | 1302e0c2-bd6e-4417-ae0b-dd5d0d17698d |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | 45781883-f86d-4f16-be5b-67c21ed09ea1 |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | 1c352714-70fd-49ff-87cc-dfc43b733687 |  | checkpoint | General visual check for damage, etc
checkpoint-status | 3c11b4ee-e5e7-4276-aeef-6ca887808256 |  | checkpoint | Visual check for water & oil leakage
checkpoint-status | b77f8aff-57ad-41b8-80fc-b013c9e82526 |  | checkpoint | Mountings fixed & torqued down to plinth
checkpoint-status | 0cb1c96c-9ef5-4e96-9fa2-ae22bf7fb3a8 |  | checkpoint | Inlet pipework is installed & connected
checkpoint-status | 2ba64e78-0fb7-4a36-8172-0922a718c3f0 |  | checkpoint | Outlet pipework is installed & connected
checkpoint-status | d6888f90-603e-4242-88c0-156bdbf4883d |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status | fca5d790-4668-4b42-a6b6-cea0d8c2ff9e |  | checkpoint | Electrolysis prevention in place if required
checkpoint-status | f6315781-8614-49de-a280-593e8ec895b0 |  | checkpoint | Electrical cable is installed
checkpoint-status | c56b18cb-72b7-41a3-b3d4-c077a092269c |  | checkpoint | Control panel is installed
checkpoint-status | 59aa8689-c0a1-4441-bc1c-14e191eb1875 |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status | 60af1fd2-60c4-431c-945d-484c71bd8b36 |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status | 2cf3d8dd-b883-4411-bf43-d0c07eb0796b |  | checkpoint | Pumps cycles set & test run & certified by pump provider
checkpoint-status | 1e4a3464-f4bd-4bd2-95e3-35af20a7b318 |  | checkpoint | Pressure gauges installed & running within operating limits
checkpoint-status | 76b4b318-df47-4bd9-b507-ef82ade1ce7a |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | d8e8af38-c5e4-4181-9c6a-51a39af063ed |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | c81faa0e-4e3c-4c6e-a132-2cd62786397b |  | checklist | AU Application for New Service Connection |  |  |  |  | Yes | AU Application for New Service Connection | d5cbae36-f24f-4de7-8181-fcadc999c064
checkpoint-status | 63202722-ddb7-4f3b-acfe-58897cac82a9 |  | checkpoint | Road Opening Permit
checkpoint-status | 4f3a9e38-b164-4a1a-91f9-f06e29639fe3 |  | checkpoint | Storm Water Drainage
checkpoint-status | 98262b79-b627-4d79-9baa-3fe0ae7e8583 |  | checkpoint | Sewer Drainage
checkpoint-status | 9c05d000-c544-4050-9cd0-fb4270e07127 |  | checkpoint | Water Supply
checkpoint-status | 4de82bc0-9716-4d21-ac34-a7d9ee5a35a8 |  | checkpoint | Natural Gas Supply
checklist-flat | 479e8223-3dc4-4ab3-8aa0-2ec8b64cac7c |  | checklist | FO Laundry Troughs |  |  |  |  | Yes | FO Laundry Troughs | d9c7dbca-9366-4711-b530-803f25ebc4ac
checkpoint-status | f6b3b926-5452-4861-988f-6523829dad78 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 011bafb5-984c-4b50-82e7-ff0dc0f4e756 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | a0a51384-9c09-49f9-9453-f81dfff64170 |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status | ab86f0f0-4bc5-4c19-aeac-72b1f60824d7 |  | checkpoint | Solid installation & mounting of trough bowl & mixer
checkpoint-status | 71fc92e2-8106-4468-a4f2-a3f29d3fb305 |  | checkpoint | Check operation of plug & washer
checkpoint-status | 19991366-948e-4f64-b722-8e199464f5eb |  | checkpoint | Check for evidence of leakage
checkpoint-status | 8103c10b-37ba-4a05-8408-97dbe35c7050 |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status | 18d0e8af-38f7-4e92-b9ab-2d185f4048be |  | checkpoint | Check cover plates are installed
checkpoint-status | 712a47e2-f8ea-416b-88b1-ea307d74b9bc |  | checkpoint | Check mini stops for operation & leaks
checkpoint-status | 5ffdb949-5c5b-455f-b013-c73fdc97dc62 |  | checkpoint | Check flexible connections for kinks or twisting
checkpoint-status | 4ceb4f7d-de28-4c6b-9391-8de276853515 |  | checkpoint | Check trap is installed & nuts are tight
checkpoint-status | e2ef7898-6f93-4c4e-8dcc-e12ec8c8cdb0 |  | checkpoint | Check AAV installation (if required)
checkpoint-status | 132f2ac3-c35d-4c33-939e-1eb1f155976a |  | checkpoint | Operate mixer & half fill bowl then discharge
checkpoint-status | 4d770028-ae6e-4973-a82a-487f120a0f82 |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | a8640459-30ca-4e52-8ff9-2af503534be9 |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status | 0732a9c9-33a9-481d-92d4-04b13909a081 |  | checkpoint | Check caulking is correct
checklist-flat | 317a61fb-66c2-4542-aa33-d642dc3db858 |  | checklist | CW Rough-in (High Level) |  |  |  |  | Yes | CW Rough-in (High Level) | e26e0e3a-2ee9-4c4d-9cc1-3db0497e624d
checkpoint-status | 4febba3e-254a-4cf1-a6de-23d960316ca6 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | decbaa89-e025-43bd-9577-157eb26633ef |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | 41461c29-e788-4c7f-9a29-7d4c929426da |  | checkpoint | Pipe materials are correct for application
checkpoint-status | b338e99f-16be-4e66-b849-e54cd0001f3d |  | checkpoint | Check silicone applied to studs
checkpoint-status | b316c8d5-9cc1-4283-9c7f-28e0aa27e255 |  | checkpoint | Check TCV/TMV correct location & securely clipped
checkpoint-status | 7baf7dbd-4548-4e13-bc8f-9b6feac7bf5a |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 893bd3a3-27c7-409c-a7ad-738ca44aeec5 |  | checkpoint | Check for possible cross connections
checkpoint-status | 2f541550-6057-4d46-8be6-a4195a698dcc |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | 738f5f82-7edc-4442-9f3f-e5cf3da3101b |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status | f8bbd45d-5a21-4b59-85bd-98f9ea603916 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | a5a70a7a-8ad6-4917-a994-2a55f44c1055 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 47353388-b8bb-4765-af52-689d8d648dd0 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 88b4115f-5be2-452a-8d37-8c7ab9af1da2 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 61a95dd8-0a66-4cff-a957-ee3409bfb3e9 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 6eae96cd-34d5-421d-8aea-0dc13821151f |  | checklist | Peno - Cast In |  |  |  |  | Yes | Peno - Cast In | e314223f-88bc-48fc-89f2-55a3f8d30bd2
checkpoint-status | 0b800f90-91a6-44e5-b937-6550ab578e9c |  | checkpoint | Installation complies with current IFC shop drawings
checkpoint-status | c74b6969-04a6-4be5-a83e-495b19abe884 |  | checkpoint | Collar & pre-fab elements free of damage prior to install
checkpoint-status | d1dec170-f25f-42fb-bad8-196ed77feec0 |  | checkpoint | Where practical, pipes water tested prior to the pour
checkpoint-status | dd8a1dd8-a76c-4584-ba49-2d74c33e9132 |  | checkpoint | Pipe grades and size have been checked
checkpoint-status | 72edaf9d-8540-4c73-8597-d1a559837ecb |  | checkpoint | Invert levels and finished levels have been checked
checkpoint-status | 74ec447d-b992-44e9-bc5d-e8b79801d799 |  | checkpoint | PVC has been lagged (add photos)
checkpoint-status | 1f182a49-dda1-4bef-a943-9c02304849a4 |  | checkpoint | HDPE fusion welds are witness marked
checkpoint-status | 329c3e3a-4e58-442d-8d48-da054b825065 |  | checkpoint | RWO body installed level
checkpoint-status | 72df4363-9875-49cf-98dc-21ff0ad5a357 |  | checkpoint | Clips, fixings & anchor points are correct and secure
checkpoint-status | a8b6d5fb-2ce2-4888-ae50-49c95dbc1c07 |  | checkpoint | All cast in elements are clear of debris, securely capped & sealed prior to pour
checkpoint-status | 1c44af43-8ee8-4190-bc69-1a2451add19d |  | checkpoint | Water has been poured into PVC for deep beam/thick slab pour
checkpoint-status | 20e93eb8-d6dc-4b05-b78f-1bf293aa08f8 |  | checkpoint | Unfixed pipes are tied to reo (where necessary)
checkpoint-no-status | f969b0eb-e295-4b66-8210-ae36c4497460 |  | checkpoint | Concrete pour details
text | 7e763907-1221-52e4-8f7c-684cc44330a0 |  | textbox | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | 14ea98d9-de68-4517-a2bc-086b98d74442 |  | checklist | Incomplete or Delayed Works |  |  |  |  | Yes | Incomplete or Delayed Works | e86632a0-7f26-43d5-9ebd-63e4c5b29cf7
checkpoint-status | ecbdc03e-6897-4ced-a830-85136cb07d2b |  | checkpoint | Incomplete or Delayed Works Details:
text | ec46fe0d-a73c-5d4a-b6ca-5fef6003f277 |  | textbox | Detail:
checklist-flat | ead0cd33-da45-4047-997a-29c7164db499 |  | checklist | CW Risers (Pumped or Mains Pressure Risers) |  |  |  |  | Yes | CW Risers (Pumped or Mains Pressure Risers) | e884fc68-9e4d-480f-840f-225e71fb690b
checkpoint-status | d96c60c8-b339-4dd3-adf6-bd5655d1b624 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | cd22172b-6b27-4d4a-a384-d9837ff35e79 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | e66fdcfe-42a4-4934-bfe3-3e6265a82139 |  | checkpoint | Penetrations are installed
checkpoint-status | 44d3bb3f-4c64-4c32-8146-0937ac3660d9 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 7a137a6d-69f1-4661-baf4-cefcb4b21492 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | bedd0e43-d2d9-47c0-a033-4c583d29bffe |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | e91b6ab8-b954-4d8d-8350-b09053a18f31 |  | checkpoint | Ensure all risers are installed professionally with no abnormalities
checkpoint-status | 6d06500e-d347-4784-8318-4fcc618d399d |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | c7772602-7747-4894-a01b-8e6e984aea77 |  | checkpoint | Welded pipe joints are completed
checkpoint-status | cbf3afac-88a3-4a3c-8a2e-85113cc854ed |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | b7a2ae79-40cc-4c62-9c18-d6b47f7aa0a5 |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | d866e64b-12e4-4672-beea-637238fb0732 |  | checkpoint | Pipe penetrations are caulked
checkpoint-status | fb95b0a6-97d6-497c-96bc-653c19387d1f |  | checkpoint | Anchors are installed as per manufacturer instructions & compliant with AS3500
checkpoint-status | 428a14af-2770-4b63-8ddc-dc174ff253b3 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 368127d2-36cc-4c20-9af3-683730fef22a |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 4a29a372-8616-45c1-86f2-b60defa2d062 |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | 165782c1-c196-4d19-a55e-cd0e5011177c |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | e4dd0230-7909-4ad8-a81a-8425cc848f14 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 537a57d0-ad0f-44c9-b15d-df5f11691b9d |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status | bd4c51e4-c63d-4dd9-8c7b-e6e760304b35 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 482a44e7-e346-4f57-87ab-4350413bf0e9 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | ab7ca4e5-e379-4348-8539-abc4cfa9f4cd |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | fcc12517-6a20-46a0-93c0-86d007210b28 |  | checklist | SYP Syphonic Downpipes/Overflows (Grated Outlets) |  |  |  |  | Yes | SYP Syphonic Downpipes_Overflows (Grated Outlets) | e9ddb64e-aa87-43b6-b4e6-01ff70243ad2
checkpoint-status | f038bd67-7e13-4beb-8285-7401dfe9d659 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 958da979-e848-4b96-9cf3-d9739e5bfbb4 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | a73db63d-af91-4335-87af-7475eef4719c |  | checkpoint | Balcony (BO/OF) grates & bodies are installed in sizes & locations as per design
checkpoint-status | 4d358ccb-b547-4aa6-bc92-63241783d77c |  | checkpoint | Trench channels & grates are installed in sizes & locations as per design
checkpoint-status | 973c394b-f653-42a8-9358-b1eaaee30cd7 |  | checkpoint | Cast-in round/square (RWO/OF) grates & bodies are installed in sizes & locations as per design
checkpoint-status | a7b4c76f-f49a-410f-afb2-7defdddd8ee6 |  | checkpoint | Cast-in planter box/tree grates & bodies are installed in sizes & locations as per design
checkpoint-status | bc739b70-e1de-4569-a3cd-91f5f5b4a4d0 |  | checkpoint | Downpipes are installed
checkpoint-status | e3513615-ac96-4d2d-8018-d5deb4a4d31e |  | checkpoint | Overflows are installed
checkpoint-status | 173e9f68-5869-46de-baac-693002245e78 |  | checkpoint | Penetrations are installed
checkpoint-status | 80e73a5d-72d5-4f7e-8342-f815a0e5609e |  | checkpoint | Drain penetrations are caulked
checkpoint-status | d65b8191-a2df-4172-8b71-4c500597769b |  | checkpoint | Trench channels & grates are installed in sizes & locations as per design
checkpoint-status | 842ef5cb-6592-4b4b-a137-bad5a39c4875 |  | checkpoint | Cast-in round/square grates & bodies are installed in sizes & locations as per design
checkpoint-status | 0ca4b50d-15e8-47cd-9bc3-36336f474a9e |  | checkpoint | Cast-in planter box/tree grates & bodies are installed in sizes & locations as per design
checkpoint-status | a6aa6353-e73a-42c1-b72a-f053422fd933 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | 0aeda3ad-e34e-4b66-8aea-8624b4b8e355 |  | checkpoint | Check inside trap for signs of debris etc
checkpoint-status | dfff1166-01bd-4331-a668-f5c227c9460b |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | 2621f28a-16ed-4cb6-a8c7-2b0d04f2effc |  | checklist | FO Wash Basins |  |  |  |  | Yes | FO Wash Basins | eb5c9d47-c46a-48f6-9d3e-18b9b5c18623
checkpoint-status | a5cf5286-a124-430d-b18b-1e1f30a5dd9a |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | d3f104b2-51bb-4ee4-8d13-fd4be7fed049 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 2c893281-2829-4039-8e7b-9b26132b98ee |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status | fc8aff1d-97f2-4f94-80dd-22bd3004c382 |  | checkpoint | Solid installation & mounting of basin bowl & mixer
checkpoint-status | 6c2ad2bd-8e4b-4334-83a2-e368c0792e4d |  | checkpoint | Check operation of plug & washer
checkpoint-status | a1ab04b6-15b5-4dd2-bc05-c4d85a9bed76 |  | checkpoint | Check for evidence of leakage
checkpoint-status | ede52012-7f3e-4e7b-b5cb-d375ed9af3b7 |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status | b283b46e-baf6-4dcb-abcc-97add8a3a608 |  | checkpoint | Check cover plates are installed
checkpoint-status | cec46ea2-0c6f-4e88-b74f-2af11161342e |  | checkpoint | Check mini stops for operation & leaks
checkpoint-status | 33d8dc8c-0b07-493a-b347-0bd839b0fc42 |  | checkpoint | Check flexible connections for kinks or twisting
checkpoint-status | 832c3585-81ab-4f56-a9d9-047b66eb17bf |  | checkpoint | Check trap is installed & nuts are tight
checkpoint-status | 2132aa53-9eb4-4dce-bbb5-19552d58bc30 |  | checkpoint | Check AAV installation (if required)
checkpoint-status | 8bc537bd-9e36-4eaf-8dba-ea99475e3e45 |  | checkpoint | Operate mixer & half fill bowl then discharge
checkpoint-status | 8defba0a-95c8-4ce2-94ec-1a69080874c7 |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | 320d36a6-cfc0-44de-a18d-a396c9eb6108 |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status | 21dd1305-255c-45b3-abbc-efae17edaae0 |  | checkpoint | Check caulking is correct
checklist-flat | 4c1dc7d7-d88e-48e8-a3a8-8a13e4e0bc60 |  | checklist | Modular Bathroom (Pod Unit) Connections |  |  |  |  | Yes | Modular Bathroom (Pod Unit) Connections | eb858476-1fe5-4302-80da-bbce368a18d2
checkpoint-status | 59caf3ad-f632-4fa7-9547-9bb8a502547e |  | checkpoint | Confirm Pod Unit supplied & installed as per contract specification
checkpoint-status | 4d8e8bc8-f84e-4a2d-a1e6-5c1aff1e0fab |  | checkpoint | General finish & alignment of Pod unit is level & centred
checkpoint-status | 5d004951-9e0a-4278-b18f-19894920f053 |  | checkpoint | Check condition of all Pod Unit fixtures/tapware
checkpoint-status | 22638500-2d1b-4bb1-8513-0f2cbf4c846a |  | checkpoint | Check that the Pod Unit sewer drainage is connected to the building system
checkpoint-status | 6645d8c4-7534-4117-8637-f0e60f63c97b |  | checkpoint | Check that the sewer pipe-work is acoustically lagged as required
checkpoint-status | 15c1112f-8c30-4245-9c63-00c3a3cdbcb2 |  | checkpoint | Check that the Pod Unit cold-water pipework is connected to the building system
checkpoint-status | f4582fe1-0093-49a5-80e4-1528327501d6 |  | checkpoint | Check that the Pod Unit hot-water pipework is connected to the building system
checkpoint-status | 89777261-60bb-400d-b30a-08fcddcb38e6 |  | checkpoint | Check that the hot-water pipe-work is thermally lagged as required
checkpoint-status | 8f04d5be-e688-429b-97e2-5d7d31ea751c |  | checkpoint | Check the Pod Unit is provided with an in-built Temp Valve or Thermo Mixing Valve
checkpoint-status | 732632dd-987b-4902-890d-4d7df2cdb909 |  | checkpoint | Check in cupboard for signs of leakage
checkpoint-status | d36dc2d9-c11a-4428-9303-63e8fe1ac914 |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status | 1952ce65-aabe-4888-951d-ae45352a2c8a |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | bd1b282b-2996-433b-aa67-fdbe98d71d3f |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status | ad19d4bf-1b52-428e-a60f-d266e58950d5 |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | 27d0de1d-13df-49a9-a6c4-15286403b0ec |  | checkpoint | Temperature test warm water to ≤ 50°C
checkpoint-status | fe4323f8-e10d-46e2-900d-d9914c7f80a0 |  | checkpoint | Temperature test warm water to ≤ 43°C if Pod Unit is DDA compliant
checkpoint-status | e628fb36-b6a1-4f3e-a807-332ba1ac8d7e |  | checkpoint | Test result is compliant with AS3500 (Record test by photo & time/date)
checkpoint-status | 6e1c5161-d4b1-4faf-b29b-763650e9b45c |  | checkpoint | Valve is securely turned off (if required)
checklist-flat | 7e842858-79d9-4833-ad7c-f92ad001aa73 |  | checklist | CW Cold Water Tapping to Meter Room |  |  |  |  | Yes | CW Cold Water Tapping to Meter Room | ebe4e682-29e4-483a-a94d-c0239935b851
checkpoint-status | 8528278d-b66f-4ba9-891a-460e3dd9af56 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 70265ef3-746b-429b-9ea5-f2475f82706d |  | checkpoint | DBYD received & verified before commencement of work
checkpoint-status | 916ec1f2-e71d-4258-adfe-4f0c78b6955a |  | checkpoint | Traffic management plan in place & approved
checkpoint-status | 3378ff3f-3ff8-4792-874c-cfd4f3bf1f8f |  | checkpoint | Authority water applications & start work notices accepted
checkpoint-status | 10672f58-07f1-420a-bd26-cf1e52a158bc |  | checkpoint | Municipality asset opening notices placed & accepted
checkpoint-status | 4c35712e-6c66-49d4-b347-e84982c3288a |  | checkpoint | Authority divide valve assembly or tee insertion installed by authority contractor
checkpoint-status | 34b981d3-8aa9-4f98-be6e-05fab056bb86 |  | checkpoint | Sluice valves installed including flanges bolted, torqued & denso protected
checkpoint-status | 1491b884-2f14-4ecf-a6f0-200b45537910 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | 76d2745a-0dcf-48dc-9557-af20d7c4b311 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | c1fc07ed-e934-4699-a878-1711e3e1329e |  | checkpoint | Location & levels are correct
checkpoint-status | 4a617154-d3fd-443b-ba94-aacf38038ae4 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | e52cb5b1-f715-4518-91c8-3322b529f9e4 |  | checkpoint | Incoming pipework is installed & layed to meter room
checkpoint-status | 69af53c8-e410-4eb5-821c-5e6c24e7254c |  | checkpoint | Pipe sleeve installed & sealed if required
checkpoint-status | 0b4c921b-8266-4ea9-8e00-6b73d24eb7f1 |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status | 265b69da-22a9-48ec-af13-73cefc27e777 |  | checkpoint | Electrolysis prevention in place if required
checkpoint-status | 980a235d-5a3e-449c-b3cd-4840197232fb |  | checkpoint | Marking tape installed
checkpoint-status | 6f7cda74-9a51-40da-911e-80666334ad36 |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status | 8804c83f-ac34-4402-8856-045207f93d93 |  | checkpoint | Spoil is removed
checkpoint-status | e5469ebd-9664-4645-aaa6-471a787c25d2 |  | checkpoint | Temporary top-dress of trenches with cold mix etc.
checkpoint-status | f3c7d6a3-f9c8-410e-b0a5-f587329e1d0c |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | a0ba3fc2-e8aa-46df-abcc-652cad52d688 |  | checkpoint | Clips & Shanks etc. are completely corrosion protected by use of "Denso" type wrapping & sealing
checkpoint-status | 7145ae1b-83a1-4b41-a768-021410b7b5ce |  | checkpoint | Pipe penetrations are caulked
checkpoint-status | a8584a05-300b-471f-9c23-2bf2c27f1c99 |  | checkpoint | Above ground pipework fixed & pipe I.D. labelled compliant with AS3500
checkpoint-status | 496f2e99-41a5-4a9f-ab36-4de811ac6943 |  | checkpoint | Main meter inlet valves installed & locked off
checkpoint-status | 2b51d6f8-2402-4648-ba64-1ea746d13e35 |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status | 13847041-566b-49d3-bf40-8525adbb6ced |  | checkpoint | Authority main meters installed & secured as per authority installation guide
checkpoint-status | 78ced649-d032-448d-9038-11e745b75f90 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | bf67f5be-1c8b-492f-9d63-765acc4b140a |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | e3a16824-66b8-444b-b932-6157e00760b2 |  | checklist | NG Rough-in (Low Level) |  |  |  |  | Yes | NG Rough-in (Low Level) | ec75d7e2-e905-4553-869a-a672e7ff92ca
checkpoint-status | 9aabebd9-2be5-438e-b4a0-ab51575cf344 |  | checkpoint | This installation and following checks are to comply with AS-5601
checkpoint-status | 77e50b7e-fd44-464b-85d8-6febc2ae701e |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | 4f99aaec-b8cc-461a-8fc5-29620cba72a7 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 9332272a-defe-436b-8776-9be09b38618f |  | checkpoint | Check silicone applied to studs
checkpoint-status | f58ab7bc-56d0-4961-84a8-92a10783b412 |  | checkpoint | Check in-wall noggings are installed to correct locations
checkpoint-status | 6eaadfb5-cf34-4ad2-bce6-f856f8ebf3ea |  | checkpoint | Check In-wall lugged elbows are installed to correct locations
checkpoint-status | 19b0510b-a2f4-42a6-ad4e-19e9ad7b7812 |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | 8b452ee8-175a-499e-a57a-219c7d04d467 |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status | 0f683da0-7096-4963-b275-3a4b66351f58 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 7a1b5f46-ef35-4490-b8fb-25d7152a030c |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | f96ce4b9-e89d-4542-8ba7-a19c3171b47f |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 0d96660f-49e3-4a31-96f7-9e387921208b |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | bd044203-ac68-485f-821c-0f9cc82cbd30 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 7c24b739-5e5e-4af4-ab0c-ad22011e2251 |  | checklist | CC Concrete Coring & Cutting |  |  |  |  | Yes | CC Concrete Coring & Cutting | ed455c4c-f25f-474c-8b79-6475017c64a3
checkpoint-status | 15e9a927-14fd-4aeb-aaf5-d600fac089cd |  | checkpoint | Structural Engineer has been consulted & certified the proposed cutting
checkpoint-status | 74c27774-9f7f-4733-86c4-5897f73f6a2c |  | checkpoint | Post tensioning design has been overlayed
checkpoint-status | de5dc733-c0fc-43d5-a1b4-13c3b9bf509e |  | checkpoint | Electronic/Sonic survey has been completed & certified
checkpoint-status | fdbe9a16-3695-4d60-9f5e-e8cac8c65a8f |  | checkpoint | Safety procedures have been certified & work area is in compliance
checkpoint-status | 49d84437-b04c-4d54-b9c7-d5184f917e91 |  | checkpoint | Installed & sized as per current documentation
checkpoint-status | e32ff4ad-a1be-4e03-beec-656c4688c52e |  | checkpoint | Covers installed if required for security
checkpoint-status | 29f9b308-f1d1-4ac5-94c7-a4e27ea35661 |  | checkpoint | Record installation by photo & time/date
checkpoint-status | 4bb4c53d-7c87-4de8-8405-5567f81c5f2e |  | checkpoint | Check cast-in roof outlet/overflow bodies installed in locations & heights as required
checkpoint-status | fddabea0-79c2-46fb-ba83-0849a21fe4d5 |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status | cf0f70e1-0e82-4ce3-b087-5f644c88a6ec |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 1a48747c-883a-4d70-9df0-402e8cfb0072 |  | checkpoint | Record installation by photo & time/date
checklist-flat | 34f1d5db-fd6f-4ddd-bf7e-a03611053f5e |  | checklist | FO Toilets |  |  |  |  | Yes | FO Toilets | ef011454-8ae5-4976-aa62-c587c6a359ae
checkpoint-status | 5f91e575-181f-4315-89a8-8241bfcc1b54 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 714e56d6-4c0f-4254-a6fe-56e12b1edfbd |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 0e212eb8-1e99-4fd7-91a2-40d3267fc21d |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status | ac85a536-2f4c-46ac-80d7-1e4cc1007044 |  | checkpoint | Solid installation & mounting of pan, seat, cistern & button plate
checkpoint-status | c9c00658-5774-4031-9a8a-91372d44ec37 |  | checkpoint | Check for evidence of leakage
checkpoint-status | 6241395c-0a10-4e8a-b554-0b394006a829 |  | checkpoint | Operate both full & half flush & check for internal overflow
checkpoint-status | 96d079fc-0106-421a-a368-1fe47a63321e |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status | 65330522-891b-4b90-a470-0db16b4235fc |  | checkpoint | Check caulking is correct
checklist-flat | d88ad4bb-8d0c-4a0b-b6c0-208ffb30c767 |  | checklist | NG Natural Gas Meters |  |  |  |  | Yes | NG Natural Gas Meters | f073ad15-5be3-4edc-b438-01424290b9f0
checkpoint-status | ee0ab9b9-54d0-4659-9319-f5d85be827df |  | checkpoint | Water Meter Details:
text | 6e087735-9bc3-52b0-bf18-0581bfac45a2 |  | textbox | Meter No:
text | 0fb89f5e-24c3-56dd-8703-34a44ef8f349 |  | textbox | Level:
text | ab09a87c-914a-5741-8ed0-41e7360df1e2 |  | textbox | Meter Size:
checkpoint-status | 23e77c86-0e0b-44dc-a140-e68576b2b7d6 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | ed287a05-da94-4ae9-a8a7-fde00facc4fe |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | c5efcbdd-8213-44be-a92a-711075e29123 |  | checkpoint | Meter bracketed
checkpoint-status | f38c1178-3e0d-4d05-a461-6303b64e6868 |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | b5668587-6b31-4b5a-bd2f-1a0e63280f03 |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | cfbb6db4-3494-4fcf-bd63-4e9c556bb26c |  | checkpoint | Pulse rate value is correct
checkpoint-status | ddcdb926-9b5c-447e-b06a-d934f5bc7d65 |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | a093004a-172b-42a4-b0f3-0212c347ccb2 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | c52ba520-59e8-4827-bf32-0fef590a0c96 |  | checkpoint | Flow direction is correct
checkpoint-status | 0db3bcfc-f5d5-41a5-8b62-2bddf757464d |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | bbb0c906-86d6-4301-b111-323c1e2f9cd0 |  | checkpoint | Record installation by photo & time/date
checkpoint-status | 8cad8cf9-53f2-4d7f-9a58-85eab17352b0 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 4908bd2c-b83e-400d-a255-9eff6b37cdcc |  | checklist | Peno - Floor |  |  |  |  | Yes | Peno - Floor | f0855c49-4d54-4d11-9027-245d738f5664
checkpoint-status | 4f3de2ee-ccb0-407b-9f55-b63e849e3254 |  | checkpoint | Installation complies with current IFC shop drawing
checkpoint-status | 12669f1c-2cbc-40f8-8917-5f1098d1ee9b |  | checkpoint | Floor fire collar types & sizes are correct against IFC shop drawing
checkpoint-status | 04d1c707-89ad-4879-b5c9-9702f9a03699 |  | checkpoint | Top and bottom of peno/collar is capped & sealed
checkpoint-status | 8dd4d621-0b57-40fa-bfcd-da2d13f422bc |  | checkpoint | Collars are firmly secured into formwork
checkpoint-no-status | 82774d2d-df88-4e7e-90b5-6367f534c105 |  | checkpoint | Concrete pour details
text | 756ad826-067d-521e-87b9-1bfce5473522 |  | textbox | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | 37f26242-42c2-4a62-9fc0-f7ef81325618 |  | checklist | SD Wastes & Vents (Low Level) |  |  |  |  | Yes | SD Wastes & Vents (Low Level) | f2b11cdd-f44f-41d0-b70b-be94b0902263
checkpoint-status | 0d064349-bb5a-42bc-a3a4-983243197133 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | ec39b847-a9b8-481b-899a-691d13a90ec4 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | d10ad83d-25f4-4d69-86b9-638fb259718b |  | checkpoint | Pipe materials are correct for application
checkpoint-status | cf6eeed1-76ba-41e8-87cd-1db7ef2153db |  | checkpoint | Check in-wall noggings are installed to correct locations
checkpoint-status | 0ec0e095-cb41-434f-a993-a1574b8173cd |  | checkpoint | Check waste pipes are installed to correct heights & locations
checkpoint-status | 81825e49-4400-455e-b103-5f8751885051 |  | checkpoint | Check AAV installation (if required)
checkpoint-status | ff1254ed-7e89-444e-8665-f53a377fff0c |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | cc51d20b-c79b-43ed-ba25-9a6a7d219618 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 018216ba-a84b-462d-9964-0c80c7ee090c |  | checkpoint | Penetrations are installed
checkpoint-status | 37f25a09-a0c6-4c00-b759-dcd71f943447 |  | checkpoint | Drain penetrations are caulked
checkpoint-status | 313f9a78-ac9d-4f12-8589-daf1c9fd2725 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | 84e7172a-6df9-4392-b052-6fc50f1187e4 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 62bfa711-beb9-43f9-8838-6e82c8e103fa |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 21a0a5e8-e3fd-4b35-b723-55825decdb39 |  | checkpoint | Check traps are correct locations, finished heights & clear of debris
checkpoint-status | 034077b2-0f5b-4ffa-9dcf-4e6b18e17fa2 |  | checkpoint | Rising mains installed & connected if required
checkpoint-status | c0fc399d-f87c-4192-95c9-e1e9e74d0ffe |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status | 1adaa4e7-7d2c-4f02-ace7-3f368e058278 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | bc6699a0-519f-4cd6-be3d-7f96c5e71e43 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 2a29f700-e421-4329-980e-d11b54b6b8d2 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat | aadb5aa4-833c-41fa-880f-1cbdf8d86e67 |  | checklist | Pour Sequence Layout Checklist |  |  |  |  | Yes | Pour Sequence Layout Checklist | f316003f-bc53-42e4-8e8b-2556d99ce5b5
checkpoint-no-status | 31093558-174b-4e00-8306-d371b6246586 |  | checkpoint | Pour sequence layout reference attached
checklist-flat | eb7c4ec3-05dd-4804-abd3-6334b67ac00b |  | checklist | SYP Syphonic Downpipes/Overflows (Main Droppers) |  |  |  |  | Yes | SYP Syphonic Downpipes/Overflows (Main Droppers) | f81e69d3-0d47-488b-989e-1038f52e2a80
checkpoint-status | c82ad264-3aad-4421-8b97-d1f832ca1e0b |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 245f131b-eb74-4b8b-90ac-c84834dd7e1f |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | 5c8e0edd-0df3-4f85-b947-fc252fa5c60b |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 0a3cec5a-0592-4f8e-ad57-1db3bf293495 |  | checkpoint | Downpipes are installed
checkpoint-status | 6277b43f-5a00-4beb-82aa-8c02d7144417 |  | checkpoint | Overflows are installed
checkpoint-status | b4b89140-7370-4526-8877-a6dfd384e58b |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status | 3fd97d6f-12a9-4c0c-b0db-8c925e546965 |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status | 60e68993-8ee3-4b6e-b78b-a95ffefb5561 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 79dad772-ce6d-4ecd-ac59-83c0efe6b07c |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 09e8cc27-400a-4ec3-b8ce-daee17fad53e |  | checkpoint | Penetrations are installed
checkpoint-status | 6dc6777b-0c3f-4089-ba7b-a155d412c91f |  | checkpoint | Drain penetrations are caulked
checkpoint-status | a32705e0-e30e-49b8-b062-b002cc572607 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | fcd15b94-bf08-435c-b412-f0be60ca7442 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | e7463696-3e36-4e7b-9554-40907f7d62a8 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | b42fec64-aa30-4eaf-a14b-9b187997146f |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status | 180995ee-8055-4a4a-8262-b573e959a429 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | ff99860d-ff87-43ab-b2f3-460b3fe73a6b |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status | db88d7c8-e942-465d-a8f5-59e45ed983a4 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | b3492878-1a9a-452d-a708-c658065e8b50 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat | 592558d1-3bd4-44a8-aef3-4bf93deae2e2 |  | checklist | TST Testing Potable Water (900 kPa Test 2) |  |  |  |  | Yes | TST Testing Potable Water (900 kPa Test 2) | f938733d-accb-48de-9695-8152a2abe497
checkpoint-status | 92180c66-e9f0-4055-a1a4-6305ff80efd1 |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.1 (2018) &/or AS-3500.4 (2018)
checkpoint-status | 38a43369-8c4a-4b1b-b3d1-7b5b0dd01d19 |  | checkpoint | Ensure all valves dedicated to isolating the test zone are securely shut off & tagged
checkpoint-status | dba9ca20-ed74-4dea-a921-3a375f805d2e |  | checkpoint | Nominate an air purging valve point
checkpoint-status | f61d4418-ca26-4100-9de0-b68822381359 |  | checkpoint | Nominate a pressure testing valve point (if none at meter manifold)
checkpoint-status | bdec5106-f762-4e4d-9b9d-a34e0776886f |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status | 3ddc551c-8018-47a9-90cc-0fb490dfc05a |  | checkpoint | Ensure all terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status | 0bdbb971-6e3c-4d0e-81c1-37f7b8929dfa |  | checkpoint | Slowly open a feeder valve & fill the test zone with water until completely purged of any air
checkpoint-status | 265ce4c8-fe86-4286-99da-50be65c2c419 |  | checkpoint | Connect pressure testing device to the nominated test point
checkpoint-status | 12b4ab85-a273-481f-95b7-cc626c0989fe |  | checkpoint | Shut off the water feeder valve
checkpoint-status | 6c14702b-346a-4342-89a0-dce3d3e01f2e |  | checkpoint | Commence testing by slowly increasing pressure up to 900 kPa and hold for 30 minutes
checkpoint-status | 0c5645a0-7e80-4868-88ca-c08ac1f264b5 |  | checkpoint | [For Couta System] Release pressure down to 500 kpa and hold briefly
checkpoint-status | 60545919-ed95-432d-a5d3-7f9d8081a38c |  | checkpoint | [For Couta System] Rapidly increase shock pressure back to 900 kPa and hold for test duration
checkpoint-status | 1fe7d052-9bb7-4a97-b1a8-cc8c2df44d75 |  | checkpoint | Testing is deemed successful if the water pressure remains unchanged after 30 minutes
checkpoint-status | 339b24fa-3e69-4330-a926-7e5f479dec10 |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status | 18e82550-a068-420b-95b2-921ece4cc147 |  | checkpoint | Test sticker in visible location
checkpoint-status | b25a5ea0-3877-4089-bf36-e864b93c151d |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | b6b7b3fe-78df-4763-b3db-6d62ca7c4033 |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | 0c93be56-8eb4-4144-b996-4eac3a3410f8 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat | d4205060-a0ae-4247-8bf0-780eaa39623f |  | checklist | FO Kitchen Sinks |  |  |  |  | Yes | FO Kitchen Sinks | f974822d-f5fb-4eb9-b4e6-ac208c62e380
checkpoint-status | 96f7cb8f-69ae-4d6a-a229-797dae78ddcf |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | ce628496-bc5b-45d5-a50a-32e6249cea37 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 70961ac6-758c-4cf5-8085-c61d25ad2bd2 |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status | 04724081-01e1-412e-b8bf-eef20a02499f |  | checkpoint | Solid installation & mounting of sink bowl & mixer
checkpoint-status | 9f14ddbf-ebae-4cab-a698-00dc5a2a1416 |  | checkpoint | Check operation of plug & washer
checkpoint-status | 5da08c81-4815-4fdc-a4ee-bb53cf2b07dc |  | checkpoint | Check for evidence of leakage
checkpoint-status | 42d78458-6f56-46dd-bb77-8ffec3c8b49e |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status | e51fcf0e-101a-4ac1-a73d-2d41a129dc15 |  | checkpoint | Check cover plates are installed
checkpoint-status | acb841a0-8e2c-4c27-a076-010d2eeccae8 |  | checkpoint | Check mini stops for operation & leaks
checkpoint-status | d2af9941-b87b-4856-925f-326acb081f39 |  | checkpoint | Check flexible connections for kinks or twisting
checkpoint-status | 61141f05-b0e6-4ad2-91e8-2d4c239226cd |  | checkpoint | Check double bowl connector & trap is installed & nuts are tight
checkpoint-status | 0173bb2f-e415-4cbc-9800-7b9c1d7afb66 |  | checkpoint | Check AAV installation (if required)
checkpoint-status | 9fce44e4-6dce-402d-b3f1-def014c52483 |  | checkpoint | Operate mixer & half fill bowl then discharge
checkpoint-status | 069d328a-64db-47da-83ca-6c67823fd4e3 |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | 4156bbfc-0e2d-4ba6-9d28-6b5dab46d2be |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status | 6fcb6224-1fd1-4ab3-8b82-50e7031aaffb |  | checkpoint | Check caulking is correct
checklist-flat | eb2c6937-e45b-4b6f-9e40-27eda939ced9 |  | checklist | TST Testing Natural Gas Service (Nitrogen/Air Test) Low Pressure |  |  |  |  | Yes | TST Testing Natural Gas Service (Nitrogen/Air Test) Low Pressure | ff092e08-8b63-4fd2-aa17-bdb231a44b06
checkpoint-status | 01b94993-31a6-4ce4-be9e-1b264f05a7cd |  | checkpoint | This testing procedure conforms with that as set out in AS-5601.1 (2013)
checkpoint-status | cefd50b9-29df-4a6a-b03f-65c605448236 |  | checkpoint | Ensure all valves dedicated to isolating the test zone are securely shut off & tagged
checkpoint-status | 55762a80-c691-4d3a-918d-4f4b23e23fd9 |  | checkpoint | Nominate an air purging valve point
checkpoint-status | 2660c54f-73d0-4011-914d-8bd6e90caf70 |  | checkpoint | Nominate a pressure testing valve point
checkpoint-status | f787082a-6b04-43b4-b323-80461d35c97e |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status | a4586d4d-77fd-45b2-8023-9becc3b74d3d |  | checkpoint | Ensure all terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status | 3c07dc20-9606-422f-b3b9-5bf504c72787 |  | checkpoint | Slowly open test feeder valve & fill the test zone with nitrogen/air until completely purged
checkpoint-status | 59d86380-fd45-4ddf-ab86-90ffe3fed153 |  | checkpoint | Connect pressure testing device to the nominated test point
checkpoint-status | dc8f2167-b573-4200-b4e7-73052cd11ba6 |  | checkpoint | Shut off the gas feeder valve
checkpoint-status | b0dc1ff6-f12b-4ec7-b55f-906f8248d9b7 |  | checkpoint | Commence testing by slowly increasing pressure up to 1.5 kPa above working pressure
checkpoint-status | 2502bd84-5fa9-4166-9b3b-044f64846991 |  | checkpoint | Testing is deemed successful if the pressure remains unchanged for 5 mins of every 30 litres volume of pipe
checkpoint-status | 174f13a4-1249-4e4c-a966-4386e10e9f8a |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status | a17a2a28-f4d2-4be6-b9db-2ddf7e26b01b |  | checkpoint | Test sticker in visible location
checkpoint-status | ac5de83e-355a-4a74-8a8d-4c68caa2c8ab |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | 9adbfd3c-7223-47d1-a564-8f2e9cca04a6 |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | 097fa124-6cbd-4b2b-851d-23fca800ce97 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation