## ITP Cover Page
Gargan Road & SH29 - Watermain Inspection and Test Plan
Project: Tauriko Enabling Project
Number and Revision: DN1210-SP2 - ITP 021-001 - Rev 1
SECTION 1 – GENERAL DETAILS
Project Name: |  |  | Tauriko Enabling Project |  |  |  |  | ITP Number: |  |  | ITP 021-001
Project Number: |  |  | DN1210-SP2 |  |  |  |  | ITP Status: |  |  | Draft
ITP Description: |  |  | Gargan Road & SH29 Watermain |  |  |  |  | Revision: | 1000 |  | 1
Contract Number: |  |  | 8287 |  |  |  |  | Drawing Sets: |  |  | 2-32735.02-WSP-DR-WAT
Customer: |  |  | Waka Kotahi |  |  |  |  | Specification: |  |  | Section 22
Quality Specified: |  |  | ISO 9001:2015
Review / Update History | [9 empty] | Verification Activity
Rev: | Status: | Date: |  | Reviewed By: |  | Revision Details: |  |  |  | Activity Key |  |  | Responsibilities Key
0 | Draft for Approval | 2025-06-03 |  | Cordelia Girdler-Brown & Nick Adams |  | CWP Section 4.2 PE welding Please give chainages for each section to be drilled/open trench. Each pipe section between valves/hydrants etc. should be listed as a stage. - added stages to cwp. CWP Section 9.1 How do you propose to maintain the continuity of potable water where we have a lift and replace methodology? - CBC have submitted a bypass methodology to TCC which they have had approval for. The stages have been added to CWP. ITP Section 3.18 Note that if sand is to be used, it has a different grading. Refer to Table G3 of AS/NZS 2566.2. - added the correct grading for sand from that standard. ITP Section 7.5 What is meant by 'treatment for corrosion resistance' on butt welds?? - this has been removed. ITP Section 9.3 Shear vane for site won material should be: Structural fill - min 125 kPa Landscape fill - min 80 kPa - changed ITP Section 12.3 PS 16.5.12 refers to pumice sand. Please refer to the testing schedule for compaction requirements for AP65 - Removed PS 16.5.12 and added appendix XVIII ITP Section 12.4 PS 16.5.12 refers to pumice sand. Please refer to the testing schedule for compaction requirements for AP65 - Removed PS 16.5.12 and added appendix XVIII ITP Section 12.6 Item should reference DR-WAT-0320, not stormwater specs - Added DR-WAT-0320 ITP Section 12.7 PS 16.5.12 refers to pumice sand. Please refer to the testing schedule for compaction requirements for AP65 - Added appendix XVIII ITP Section 15.1 Refer to TNZ B/02 section 7.6 for pavement compaction - Added TNZ B/02 section 7.6 ITP Section 15.2 Refer to TNZ B/02 section 7.6 for pavement compaction - Added TNZ B/02 section 7.6 |  |  |  | A | Action |  | ENG | Engineer / Engineer's Rep
[10 empty] | B | Report by Breach |  | CR | Customer Rep
[10 empty] | C | Check |  | PD | Project Director
[10 empty] | D | Dimension Inspection |  | PM | Project Manager
[10 empty] | E | Examine |  | OP | Operations Manager
[10 empty] | HP | Hold Point (Engineer) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) |  | HSE | HSE Manager / Rep
[10 empty] | H | Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) |  | PE/SE | QA Manager / Rep
[10 empty] | I | Inspection (Formal inspection activity to be undertaken and recorded) |  | PE | Project Engineer
[10 empty] | M | Monitor on Random Basis |  | SE | Site Engineer
[10 empty] | O | Operation |  | QE | Quality Engineer
[10 empty] | R | Review |  | SUP | Superintendent / Supervisor
[10 empty] | S | Subcontractor |  | SV | Surveyor
[10 empty] | V | Visual Verification |  | ITP | Third Party Inspector
[10 empty] | W | Witness Point (Review of text reports/records or other evidence of compliance) |  | SPEC | Specialist
SECTION 2A – ITP Approval | [7 empty] | SECTION 2B – ITP CLOSEOUT
Position |  | Name: |  |  | Signature: |  | Date: | Position |  | Name: |  | Signature: |  |  | Date:
Downer PM |  | NICK ADAMS |  |  | #VALUE! |  | 13/06/2025 | Downer PM |  | NICK ADAMS
Downer QM |  | CORDELIA GIRDLER-BROWN |  |  |  |  | 13/06/2025 | Downer QM |  | CORDELIA GIRDLER-BROWN
Client (If Applicable) | [7 empty] | Client (If Applicable)

## ITP Master Body
Gargan Road & SH29 Watermain
Tauriko Enabling Works
DN1210 - SP2- ITP021-001 - REV 0
Item No. | Inspection and Test Point | Detail / Activity | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Testing Quantity Required (based from schedule qtys) | Verification Activity |  | Downer Conformance of Compliance Signoff
[7 empty] | Activity | By | ConQA Signature | Date | Comments / Closeout Details | ENGINEERS COMMENTS - Date: | DOWNER RESPONSE - Date:
3 | PRE-CONSTRUCTION HOLD POINTS - MATERIALS/TESTING, PERSONELL & THIRD PARTY APPROVALS
3.1 | Pipe Installation | Method statement | As Per Specification and IFC Drawings | PS- 22.3 Appendix V | Watermain Construction Work Pack Sign off | Prior to Construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.2 | Pipeline Pressure Testing | Method statement | As Per Specification and IFC Drawings | PS- 22.3 Appendix V | Watermain Pipeline Pressure Testing Work Pack Sign off | Prior to Construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.3 | EF pre construction Weld Tests | Use the designated welding equipment and the approved WMS. On the largest size of PE pipe used in this Contract | ISO 21751 (strip-Bend test) or ISO 13954 (Peel-decohesion test) WMS Report TCC approval is required before works start | PS 22.9.6 (b) | Laboratory Test Report Visual Inspection | Prior to Construction. One test welds per operative(Welder) | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.4 | Butt-Fusion pre construction weld test | One weld on the most common size of pipes used for the project. One weld on the thickest wall (highest PN) pipe | ISO 13953 for tensile strength and failure mode. WMS Report | PS 22.9.6 (a) ISO 13953 Standard | Laboratory Test Report Visual Inspection | Two test welds per operative(Welder) | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.5 | Extent of Line Setout | Ensure line and level of Watermain has been marked out and agreed with Engineer in accordance with Watermain drawings. Identify any clashes before construction. LOT- markup | As Per Drawings & Markup drawing | Design Drawings. 32735.02-WSP-DR-WAT | ITP Sign Off / Mark-up | Prior to Construction & Every Revision of IFC Drawings/Data. | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.6 | Pipe and fittings. | Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | Design Drawings. 32735.02-WSP-DR-WAT | Delivery Dockets / Inspection Checksheet (DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.7 | Valves, Adaptors, Flanges, Caps and Fittings | Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition. | Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition. | PS-22.4.2 | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.8 | Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65) | Confirm Specification and material in good condition. | Confirm Specification and material in good condition. | PS-22.4.1 | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.9 | Bidim/Geogrid | BIDIM A29 Durogrid 30/30 or similar. | Site Engineer Approval | PS-22.4.1 | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.1 | Pre-cast Manholes | Confirm the class and type as shown in the drawings, and fittings required for MH is same | Confirm the class and type as shown in the drawings, and fittings required for MH is same | 32735.02-WSP-DR-WAT | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.11 | KWIK Spacers | Confirm Specification and material in good condition. Spacers for DN315 pipe and DN560 sleeve. | Model: HDXT43 Height: 43mm Spacing: 1.5m Installation: Centred and restrained | Manufacturer’s Installation Guide. 32735.02-WSP-DR-WAT | Photographic Evidence | Every spacer | W Review of text reports/records or other evidence of compliance | SE
3.12 | DN560 Sleeve | Confirm diameter, class & jointing type as shown on the drawings, and that the sleeves are correct and in good condition. | Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | Design Drawings 232735.02-WSP-DR-WAT (Sheet #0312) | "Delivery Dockets / Inspection Checksheet (DG-QA-TP019)" | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.13 | DN400 Sleeve | Confirm diameter, class & jointing type as shown on the drawings, and that the sleeves are correct and in good condition. | Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | Design Drawings 232735.02-WSP-DR-WAT (Sheet #0312) | "Delivery Dockets / Inspection Checksheet (DG-QA-TP019)" | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
3.14 | Material grading: Materials (GAP65/AP65) | NZS4407:2015, Test 3.8.1 - Particle Size Distribution | No Particles >200mm Maximum fines 10% passing 75micron sieve | PS 22.13.1 Appendix XVIII PS 16.5.5 Appendix V | Lab Test Report NZS 4407.3.8.1 | Stockpile Size (m3): 0-400 - 2 tests 400-1,500 - 3 tests 1,500-4,000 - 4 tests >4,000 - 1 test for each additional 1,000m3 Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.15 | Weathering index: Materials (GAP65/AP65) | NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate | AA, AB, AC, BA, BB, or CA | Appendix XVIII PS 16.5.5 Appendix V | IANZ Accredited Report | 2 Tests Per Material, Per Source Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.16 | Crushing Resistance: Materials (GAP65/AP65) | NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load | >100KN | Appendix XVIII Appendix V | IANZ Accredited Report | 2 Tests Per Material, Per Source Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.17 | Maximum Dry Density and Optimum Water Content | NZS4402:1986, Test 4.1.2 - Heavy Compaction Test | Report Value Only | Appendix XVIII Appendix V | IANZ Accredited Report | 1 Test Per Material, Per Source Results to Engineer 2 wks before importing | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.18 | Material grading: Materials (GAP20/19mm chip/Sand SAP7) | Bedding/Side Zone/ Overlay Zone/Embedment Zone | Sieve Size % Passing 19.0mm 85-100% passing 9.5mm 25-55% passing 4.75mm 0-10% passing 2.36mm 0-5% passing 0.075mm 0-2% passing Sand: Sieve Size % Passing 4.75mm 100% passing 2.36mm 90-100% passing 1.18mm 85-100% passing 0.600mm 70-100% passing 0.300mm 50-100% passing 0.150mm 0-40% passing 0.075mm 0-5% passing | AS/NZS 2566.2 (G3 - sand) PS 22.4.5 | Lab Test Report NZS 4407.2015 Test3.8.1 | 0-400m3 2 Test 400-1500m3 3 Test 1500-4000m3 4 Test >4000 1 Test Additional 1000m3 | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG |  |  |  | Note that if sand is to be used, it has a different grading. Refer to Table G3 of AS/NZS 2566.2 | Added - Sand: Sieve Size % Passing 4.75mm 100% passing 2.36mm 90-100% passing 1.18mm 85-100% passing 0.600mm 70-100% passing 0.300mm 50-100% passing 0.150mm 0-40% passing 0.075mm 0-5% passing
3.19 | Pipes (PE) | Manufacturer's record and location of extrusion plants. Name of the proposed PE resin, the manufacturer, production information on the properties of resin. Full Traceability information and certification of analysis for the resin batch. | Full Traceability information and certification of Material and resin. | PS-22.4.1 (d) | Full Traceability information and certification of Material and resin. Delivery Dockets | Prior to construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.2 | Valves, Adaptors, Flanges and Fittings | Have a pressure rating no less than the designed pressure. Mechanically, chemically and electrically compatible with the class and material of the pipe. Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose. | Engineer approval AS/NZS 4129 | PS-22.4.2 | Delivery Dockets | Prior to construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.21 | Fusion Joint Compatibility | Confirm pipe and fittings compatibility for fusion welding | No defects, compatible resin types per NZS/AS 2033 | NZS/AS 2033:1980, Clause 4.2 | Test Report | 1 per material type | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | ENG
3.22 | Horizonal Directional Drilling | Detailed methodology of directional drilling | Engineer Approval | PS 21.6.6a | Engineer APPROVAL | Prior to construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.23 | Exisiting Watermain system | Confirmation of existing watermain network | survey informations | Appendix XI | Survey data. PIck up existing watermain with survey | Prior to construction | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | SE
3.24 | Grouting Methodology | Cement grouting the sleeve annulus | Enginner Approval | PS 21.6.6g | Engineer approval | Prior to construction | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | ENG
3.25 | Pavement reinstatement - Asphalt type to confirm | Prior to construction, TCC will provide what asphalt to use. Testing required too | TCC confirmation and approval | TCC T460 | Engineer approval | Prior to construction | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | ENG
4 | CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE INSTALLATION - Excavation and Laying
4.1 | Foundation Compliance | On Granular or Cohesive Material | Granular Material: Scala 3 blows/100mm (Or) Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa | Appendix V Table 21:11 | Scala/Shear test result | One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. | W Review of text reports/records or other evidence of compliance | SE
4.2 | Undercut approval | Trench Foundation | 300mm Max cut IFC Drawing Sheet 320 (Or) Engineers approval | IFC Drawing WAT. AS/NZS 2566.2/2002 | Lab Test Report / Watermain line record | If Undercut required | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.3 | Undercut Backfill Compliance | On Granular Material / On each layer as per specification / on the trench foundation. | Visiual Inspection | IFC Drawing WAT | Lab Test Report / Watermain line record | Every Undercut | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.4 | Bedding Zone Compaction Testing | On Granular Material / On each layer as per specification (Imported Sand/GAP20/19mm chip) | Bedding Zone: 100mm minimum thickness (compacted) over the bottom of the trench. Minimum Compaction- 85%MDD Paeangaroa Sand: clegg of ave 9 CIV and min of 7 CIV. Wilson Sand No.2: clegg 4 CIV | IFC Drawing AS/NZS 2566.2/2002 | Lab Test Report | As per WM Specification. One test per 20m evenly spaced intervals. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.5 | Laying of Pipes | Lay in straight lines, beginning at the lower end of the line. Lay all pipe with manufacturing codes and class markings facing upwards. | As Per Drawings. Facing upwards | PS22.7.1 C | Visual Inspection / Watermain line record | Every Line | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
4.6 | Pipe Installation on Curved Alignments | All Industry Guideline PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202) | AS Per POP 202 | PS 22.7.1 D | Visual Inspection / Watermain line record | Every Line | M Monitor on Random Basis | SE
4.7 | Anchor block and to extend past edge of concrete | REFER to ANCHOR BLOCK TYPE TABLE on drawings based on pipe size | IN ACCORDANCE WITH PROJECT SPECIFICATION as per sheet 0321 | Project Drawings (232735.02-WSP-DR-WAT) | ER APPROVAL | SH29/Cambridge Rd | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
5 | CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE INSTALLATION - Directional Drilling
5.1 | Check levels while drilling | Inspection of Pipeline Inverts | Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance | PS- 21.7.6 Table 21.15 | Survey Data / As-built record | Pipeline invert to be surveyed at chainages as indicated in the drawings. | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
5.2 | Drilling Fluid Mix | Viscosity record | Viscosity record | PS 21.6.6 | Viscosity record /checksheet | Every shot | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
5.3 | Correct Reamer Used | Reamer size to confirm on site | Reamer size to confirm on site | PS 21.6.6 | Checksheet | 1 per drill shot | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
5.4 | Pipe Damage | Damage <10% of wall thickness | Damage <10% of wall thickness | PS 21.6.6 | Visual inspection | Each pipe | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
5.5 | Tracer Wire | Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings. Mark fire hydrant positions in accordance with SNZ PAS 4509 | Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings. Mark fire hydrant positions in accordance with SNZ PAS 4509 | PS 22.7.3 a | Visual Inspection / Wastewater line record | Every Line | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE/SV
5.6 | Drill Report | Drill report to be submitted | Drill report to be submitted | PS 21.6.6 | Report | Every Line | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
5.7 | Settlement monitoring and ground deformation (Baseline measurements) | Topo survey completed before and after drill shot | Topo survey completed before and after drill shot | PS 21.6.6 | Survey data | Every 6m | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
5.8 | Cement Grout - Annulus | The sleeve annulus are to be cement grouted after installation to prevent settlement. | The grouting mix is to be: 1. 1:1 Sand/cement ratio 1 : 1 2. Water/Cement ratio 1 : 0.67 by weight | PS 22.5.8b | Visual inspection, lab report | Every Grout | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
6 | CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Joint and Connection
6.1 | Flanges | Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification. | Flanges to AS/NZS 4087 | PS 22.7.5 Appendix XXII | Visual Inspection | First flanged joint | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
6.2 | Bends | PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings. Fitting must meets the same PN rating as the adjacent PE 100. Fittings must be suitable for producing the joints shown on the Drawings. | PIPA POP 006 and AS/NZS 4129 | PS 22.4.2 Appendix XXII | Visual Inspection | As per the IFC drawing | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
7 | CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Butt-Fusion Welding
7.1 | Butt-Fusion Construction Weld Test | Test at least two welds from the first 50 welds. One of the welds to be selected by the Engineer for satisfactory result. | Tensile testing and ductility of welds. 95% tensile strength; welds aligned | PS- 22.9.6 (a) (iv) | Test report | Two welds for the first 50 welds | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
7.2 | Butt-Fusion Welding | Use only semi-automatic or automatic welding machines. Maintain a site record for all butt-fusion welds. The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct. | Site Butt Fusion Welding record to be filled out. (Refer to CWP) WMS Report | Appendix XXII PS 22.9.4 C | Visual Inspection / Butt Fusion welding records checklist. WMS Report | Every Welding Point | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
7.3 | Survey | Inspection of Pipeline Inverts | Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance | PS- 21.7.6 Table 21.15 | Survey Data / As-built record | Pipeline invert to be surveyed at chainages as indicated in the drawings. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
7.4 | Photograph of Each Weld | Take sharply focused photo while clamped | Unique weld identifier visible | N/A | Weld Records; Photos | Each weld | I Formal inspection activity to be undertaken and recorded. | SUB
8 | CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Electrofusion Welding
8.1 | EF Construction Weld Test | EF weld quality to be maintained. | EF coupler and EF saddle testing | PS- 22.9.6 (b) (iv) | Test report | 1 test per 5 welds | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
8.2 | EF Welding | Required if Butt fusion welding cannot be perform. EF Jointing in accordance with PIPA POP 001. The lead welder or welding supervisor must verify on the site record form. | Site EF Welding record to be filled out. (Refer to CWP) and checklist. Photo of every weld. WMS Report | PS 22.9.5 Appendix 22 | Visual Inspection / Electrofusion (EF) welding record checklist. WMS Report | Every Welding Point | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
8.3 | Survey | Inspection of Pipeline Inverts | Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance | PS- 21.7.6 Table 21.15 | Survey Data / As-built record | Pipeline invert to be surveyed at chainages as indicated in the drawings. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
8.4 | Photograph of Each Weld | Take sharply focused photo while clamped | Unique weld identifier visible | N/A | Weld Records; Photos | Each weld | I Formal inspection activity to be undertaken and recorded. | SUB
9 | CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Backfill
9.1 | Emebment Zone - (Side Haunch Overlay ) | Granular Sand backfill Compacted in 200mm Layers. NDM/CleggTesting to be completed on maximum 200mm lifts of overlays . NDM BS to be Carried Out | In 200mm layers. More than 85% of MDD. Paeangaroa Sand: clegg of ave 9 CIV and min of 7 CIV. Wilson Sand No.2: clegg 4 CIV | IFC Drawing 0320-1 | Lab Report / Watermain line record | One test per 20m evenly spaced intervals. 200mm lift | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
9.2 | Pipe Markers | Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings. Mark fire hydrant positions in accordance with SNZ PAS 4509 | AS Per Drawings. | PS 22.7.3 a | Visual Inspection / Watermain line record | Every Line | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
9.3 | Backfill Compaction Testing | GAP65/AP65 Backfill Compacted in 200mm Layers. NDM Testing to be completed on maximum 200mm lifts of backfill. | GAP65/AP65 or site won material Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill. 95% NDM on Shared and Carriageway. OR 28% CIV For site won: Structural fill - min 125 kPa Landscape fill - min 80 kPa | PS- 22.13.5 NDM Standerd 25832 NZS 4402 Test 4.1.3 IFC Drawing 0320-1 PS 16.5.5 | Lab Report / Watermain line record | As per Specification. One test per 20m evenly spaced intervals. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE |  |  |  | Shear vane for site won material should be: Structural fill - min 125 kPa Landscape fill - min 80 kPa | Changed from: For site won min > 60kpa Ave > 80kpa. To: Structural fill - min 125 kPa Landscape fill - min 80 kPa. Added PS 16.5.5
10 | CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Inspection
10.1 | Pipe Inspection | Inspection of Drainage line | Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness | Internal | Watermain line record | Continious 1 per Line | I Formal inspection activity to be undertaken and recorded. | SE
11 | CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE TESTING
11.1 | Pressure Acceptance Testing | Backfill/cover with embedment before testing End caps in place, provision for filling the pipeline and bleeding air. | Potable Watermain Pipelines – 1250kPa Ensure the STP is not more than 25% above the rated pressure of any pipeline component. | PS 22.7.12(d) PS 22.7.13(b) | Test Report Pressure Log in.csv or .xlsx format | All Pipeline All valves | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
11.2 | Swab New PE Watermain | Swab to remove debris and air | Water running clear & removed entrapped air | TCC IDC TS-7 | Swabbing Check Sheet | All new pipe installed | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SUP/SE
11.3 | Pressure Test New PE Watermain | Conduct pressure test. Due to not commissioning the pipe until later in the project, CB will complete there own pressure testing upon installation of the pipe, with the full pressure testing and chlorination to be completed once the pipe is ready to be commissioned. | No leaks, no failure of any pipe, fitting or other pipeline component. | TCC IDC TS-7.1c Pressure Rebound Test Method; TS-7.1a Constant Pressure Test Method | TS-7.1a/c Pressure Test Method (Test Report) | All new pipe installed & swabbing passed | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SUP/SE
11.4 | Chlorinate New PE Watermain | Chlorinate watermain | 5+ pH on chlorine tester | TCC IDC IT-7.4.1 Disinfection Procedure | Picture; Signed Chlorination Check Sheet | All new pipe installed & pressure test passed | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SUP/SE
11.5 | E. Coli Test New PE Watermain | Test for bacterial contamination | <1 E. coli; <1 Coliforms | TCC IDC IT-7.5 E. coli Sampling | E. coli Test Report | All new pipe installed & chlorine test passed | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SUP/SE
12 | CONSTRUCTION ACTIVITY - WATERMAIN Manhole installation
12.1 | Foundation Compliance | On Granular or Cohesive Material | Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa | Appendix V Table 21:11 | Shear vane or Scala test result | 1 Test/Manhole | W Review of text reports/records or other evidence of compliance | SE
12.2 | Undercut Approval | On Subgrade | Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material. Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material. | Table 21.5 | Lab Test Report | If Undercut required | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
12.3 | Undercut Backfill Compliance AP65 | On Granular Material | Average 95% MDD, min >92% OR Clegg 25% CIV | PS- 16.6.4c Appendix XVIII | Lab Test Report | 1 Test per Undercut | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE |  |  |  | PS 16.5.12 refers to pumice sand. Please refer to the testing schedule for compaction requirements for AP65 | Changed from PS 16.5.12 to 16.6.4c and added appendix XVIII
12.4 | Bedding Compaction Testing AP65 | On Granular Material | Average 95% MDD, min >92% OR Clegg 25% CIV | Appendix XVIII PS- 21.6.11 | Lab Test Report | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE |  |  |  | PS 16.5.12 refers to pumice sand. Please refer to the testing schedule for compaction requirements for AP65 | removed PS 16.5.12 and added appendix XVIII
12.5 | Survey | Inspection of Structure | Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm. | PS- 21.7.6 | Survey Data | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SV
12.6 | Sidefill Compaction Testing | From the bedding layer to the overlay layer of pipe. | AP20/GAP20 Testing to be completed on maximum 200mm lifts of backfill - 85% MDD AP20/19mm chip | PS- Table 21.12 DR-WAT-0320 | Lab Test Report | 4 Density test per layer at Quarter Points around the Structure. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE |  |  |  | Item should reference DR-WAT-0320, not stormwater specs | Add DR-WAT-0320
12.7 | Backfill Compaction Testing | From Overlay layer to the subgrade layer | AP65 Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal. AP65-Clegg28%CIV | PS- 22.13.5 Appendix XVIII | Lab Test Report | 4 Density test per layer at Quarter Points around the Structure. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE |  |  |  | PS 16.5.12 refers to pumice sand. Please refer to the testing schedule for compaction requirements for AP65 | Added appendix XVIII
12.8 | Manhole | Confirm the class and type as shown in the drawings, and fittings required for MH is same | Confirm the class and type as shown in the drawings, and fittings required for MH is same | Design Drawings 232735.02-WSP-DR-WAT | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) Manhole checksheet | Each Delivery to site/ per manhole | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
12.9 | Installation of concrete chamber for Air Valves | New 1200mmØ precast concrete Manhole concrete cut a hole in the base of the concrete chamber to a suitable size as to fit the pipelines. Contractor to form hole in concrete chamber wall. Hole to be sized just enough for fitting size; repaired with Sikadur 42 or equivalent non-shrink grout and 2 layers of Malthoid placed around pipe. | TYPICAL IN-LINE DN50/DN80 AIR VALVE INSTALLATION as per drawings | Project Drawings (232735.02-WSP-DR-WAT) | MANHOLE CHECKSHEET | Per manhole | I Formal inspection activity to be undertaken and recorded. | ENG
12.1 | Installation of manhole vent offset in the berm | 50mmØ galvanised steel vent - to be set back in berm. Location in berm to be determined on site. | To be determined on site | Project Drawings (232735.02-WSP-DR-WAT) | MANHOLE CHECKSHEET | Per manhole | I Formal inspection activity to be undertaken and recorded. | SE
12.11 | Deep drainage sump installation | 150 x 150 x 100mm deep drainage sump fitted within DN80 PVC pipe piece 300mm long and cover grate. | As per drawings | Project Drawings (232735.02-WSP-DR-WAT) | MANHOLE CHECKSHEET | Per manhole | I Formal inspection activity to be undertaken and recorded. | SE
12.12 | 25MPa CONCRETE THICKENING, Corbels for the pipe entries/exiits | YD12 reinforced starter bars drilled 50mm into mahole wall and epoxy fixed. | As per drawings | Project Drawings (232735.02-WSP-DR-WAT) | MANHOLE CHECKSHEET | Per manhole | I Formal inspection activity to be undertaken and recorded. | ENG
12.13 | Installation of heavy duty chamber lid and backfill of manhole | Install the chamber lid onto the concrete chamber cover and frame as per the manufacturers specifications and backfill. | As per drawings | Project Drawings (232735.02-WSP-DR-WAT) | MANHOLE CHECKSHEET | Per manhole | I Formal inspection activity to be undertaken and recorded. | SE
12.14 | MH joints inspection | Inspection of joints | Right joint type used, no visual leak or breakage | PS 22.7.10 | Visual inspection | 1 Test/Manhole | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
12.15 | Inspection | Inspection of Structure | Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure. | PS- 21.6.11 | Manhole Record | 1 Checksheet per manhole | I Formal inspection activity to be undertaken and recorded. | SE
12.16 | Plumb | The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise. | The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise. | PS-22.7.10 | Survey Data | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SV
12.17 | Step Rungs | Step rungs evenly spaced at nominal 300mm vertical intervals | Lowest rung more than 450mm above floor highest rung not more than 600mm below the top surface of MH cover | PS-22.7.11 | Visual inspection | 1 Test/Manhole | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
13 | CONSTRUCTION ACTIVITY - AIR VALVES
13.1 | Valves/Fittings | Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition. | Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition. Air valve 10 & 11 is DN50 size. | PS-22.4.2 PS 22.5.10 | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) | PE/SE
13.2 | Installation of Isolation Valve | Verify installation per manufacturer’s instructions | Installed as per manufacturer’s instructions. Project Specifications | PS-22.4.2 PS 22.5.10 | Air Valve & Isolation Valve Check Sheet | Each isolation valve | I Formal inspection activity to be undertaken and recorded. | ENG
13.3 | Installation of Air Valve | Verify installation per manufacturer’s instructions | Installed as per manufacturer’s instructions | PS-22.4.2 PS 22.5.10 | Air Valve & Isolation Valve Check Sheet | Each air valve | I Formal inspection activity to be undertaken and recorded. | ENG
14 | CONSTRUCTION ACTIVITY - FIRE HYDRANTS
14.1 | Chamber Location | Location of fire hydrants and air valve chambers to be confirmed on site with the TCC engineer and offset as far back off the road surface as possible. | TCC Engineer approval | Project Drawings (232735.02-WSP-DR-WAT) PS 22.4.2 i PS 22.5.11 | TCC sign-off | CHECKSHEET | "HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point." | ENG
14.2 | Hydrant Surround Blocks, height to suit | Hydrant box with 150 x 150mm concrete surround to be finished flush with surrounding ground. | Typical FH SHEET 0322 | Project Drawings (232735.02-WSP-DR-WAT) PS 22.4.2 i PS 22.5.11 | CHECKSHEET | CHECKSHEET | I Formal inspection activity to be undertaken and recorded. | ENG
14.3 | Install ductile iron fire hydrant | Heavy duty valve box installed as per TCC's Code of Practice. | CONTRACTOR TO ENSURE FLANGE DRILLING ON DN80 END OF REDUCER MATCHES FLANGE DRILLING ON DN80 HYDRANT RISER | Project Drawings (232735.02-WSP-DR-WAT) PS 22.4.2 i PS 22.5.11 | CHECKSHEET | CHECKSHEET | I Formal inspection activity to be undertaken and recorded. | ENG
14.4 | Concrete Pedestal on offset bend | 3mm rubber seat between bend and pedestal. 25MPa concrete pedestal. | Typical FH SHEET 0322 | Project Drawings (232735.02-WSP-DR-WAT) PS 22.4.2 i PS 22.5.11 | CHECKSHEET | Per offset | I Formal inspection activity to be undertaken and recorded. | ENG
14.5 | Anchor block and to extend past edge of concrete | DN315 - Type 1 Anchor 2000(L) x 600(W) x 2500mm deep concrete anchor block | In accordance with project specification as per sheet 0307 | Project Drawings (232735.02-WSP-DR-WAT) | Engineer Approval | SH29 Rd intersection | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
15 | CONSTRUCTION ACTIVITY - PAVEMENT REINSTATEMENT
15.1 | Sub-basecourse layer | AP65-1 is to match the exisiting granular pavement depth. | Compacted in 200mm lifts. 95% NDM on Shared and Carriageway. OR 35% CIV | PS 22.13.5 TCC T460 TNZ B/02 section7.6 | NDM/Clegg test result | Every 50 metres | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG |  |  |  | Refer to TNZ B/02 section 7.6 for pavement compaction | Added TNZ B/02 section 7.6
15.2 | Basecourse layer | AP40 (M/4) 150mm | Compacted in 200mm lifts. 95% NDM on Shared and Carriageway. OR 35% CIV | PS 22.13.5 TCC T460 TNZ B/02 section7.6 | Compacted in 200mm lifts. 95% NDM on Shared and Carriageway. OR 35% CIV | Every 50 metres | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG |  |  |  | Refer to TNZ B/02 section 7.6 for pavement compaction | Added TNZ B/02 section 7.6
15.3 | Surfacing | Asphalt to match type, texture and thickness of existing surfacing | In accordance with TCC drawing T460 | PS 22.13.5 TCC T460 | Visual Inspection/Engineer Approval | Every 50 metres | I Formal inspection activity to be undertaken and recorded. | ENG
16 | POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
16.1 | Survey As-Builts | Quality Check on Nee pipeline and structure based on the tolerances in RITS | Meets spec as per drawings and capture any NCR or change to design. | Project Specifications | Red pen markup only | Post works completion of a lot | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE