## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Postfix
4fbd54b2-0d77-4aff-bc94-2ead00290ad8 | checklist | (Dental School) Add Pipework Pressure Test Sheet - Water/LPG |  | Pipework Pressure Test Sheet -
1c374302-74d0-4d17-9738-6ae514120507 | checkpoint | Details Complete
3eeab92b-d8d0-5e26-b66b-078a05ebce94 | textbox | Consent Number: ABA
ac4959d8-274b-5976-86bb-8344a4a179b5 | textbox | Location:
140f6d6c-d19c-572a-b73b-604afd0a1c08 | textbox | Drawing:
47463ec0-0319-5c2a-b8e6-a9d454bc8fc7 | textbox | Plumber:
aabe936a-0247-5257-8c14-40b02226ab32 | textbox | Date:
9f70e29c-0890-4bdf-9b36-40d5bc95bd7c | checkpoint | Testing
51a818a5-89f6-5cfd-8536-e7225fd33388 | note | Required Test Pressure: 1500kpa (min)
6b52b73f-3b3e-5e29-b8a6-9f8523685844 | note | Required Test Time: 15 min (min) (as per NZBC G12 and ASNZ 3500)
1a06f44e-b2ce-52da-b3bc-c0520f9f2aad | textbox | Date:
eae89c6e-4404-545b-a2ac-987874ad65da | textbox | Start Pressure: |  |  | (kPa)
18b5ccae-456a-5649-963c-83690b5b4bbf | textbox | Finish Pressure: |  |  | (kPa)
6d96e5e2-7938-4109-9a05-4aed9448ba4b | checkpoint | Signoff
6ae99aac-9c2f-4937-9b37-544e17010742 | checklist | (Dental School) Add Sanitary drainage/Suction Test Sheet |  | Sanitary drainage/SuctionTest Sheet -
aea33bcf-7f09-49d7-82d6-2aad1f90f9c7 | checkpoint | Details Complete
f5ecdabf-047f-5c8b-a472-d594dd0ee7e7 | textbox | Consent Number: ABA
b2ce2f2b-9bae-506c-a52b-a007d5ba73bc | textbox | Location:
cc43bc83-f39f-5aa4-a26a-f81f5294c6e0 | textbox | Drawing:
3356d684-2826-538b-924f-36332166f2ae | textbox | Plumber:
48aac326-9f1f-560d-9cdf-4e06ba327c1d | textbox | Date:
3d723a2c-e63b-4e79-8b72-8763cedd1cf1 | checkpoint | Testing
f9526e1f-918b-5b3f-9922-856c2915578e | note | Required Test Pressure: Static Head
0d8c2af2-f826-53c6-8451-adc35cec3510 | note | Required Test Time: 10 min (min) (as per NZBC G12 and ASNZ 3500)
459718e1-2a99-5cb6-b763-8ca075f79392 | textbox | Date:
77ab4d6c-fce6-59f8-b545-803072b94515 | textbox | Water Level Check 1
3a9dea37-e299-5f6e-8b9b-cf6a68971c55 | textbox | Water Level Check 2 |  |  | (kPa)
3fb1b6f6-e259-4b5d-ad76-cb4778ab78bb | checkpoint | Signoff
4c2e622a-94e5-4184-8002-4c9254d59798 | checklist | 1st Fix - LPG QA Sheet |  | 1st Fix - LPG
94aed48b-ac9a-4fad-9048-b82aec037955 | checkpoint | Check pipework is installed as per listed drawings
968f274c-426e-4f01-bfb5-65a0358d6e4b | checkpoint | Check that the correct pipe sizing is complete to each fixture
c269364a-dc3a-4423-a07b-715d897f2465 | checkpoint | Check that the wingbatts are installed at the correct height
c255a61a-b609-4984-ae84-5b548e97e7b0 | checkpoint | Check that seismic restraints are installed
f0848798-71c6-49f6-87b6-14341f77c1dc | checkpoint | Check that the fixing's are installed at correct height
d5c5e5a3-e275-4672-94e6-9c9e7af07255 | checkpoint | Check that the pressure test is complete
a40ce534-3d82-406f-9eed-e0f436f191cc | checkpoint | Check that the test sheet is filled out
a9ba2c00-9a0a-4740-9c0d-25810f34b40a | checkpoint | Check the pipe labels are on
c13c69f1-4d31-4052-ba99-98f16ca8d7e2 | checklist | 1st Fix - RO Water pipe work QA Sheet |  | 1st Fix - RO Water pipe work
3e5def7a-d147-4de9-a67f-3ff8849c608d | checkpoint | Check pipework is installed as per listed drawings
e821c85a-a684-466c-9a54-292e6e1c6dbc | checkpoint | Check that the correct water and pipe sizing is complete to each fixture
06b2997e-4d42-4ab3-8da6-1a1da4371183 | checkpoint | Check that the wingbatts are installed at the correct height
824a5752-6b01-4b9a-815c-ff36fe842aa1 | checkpoint | Check that seismic restraints are installed
be5becf0-2278-4fd8-a5b8-110669d71c7c | checkpoint | Check that the waste pipe is the correct location
4dbb85dd-5627-4ab2-9f7e-a95f4c4e1682 | checkpoint | Check that the fixing's are installed at correct height
b07c98bc-1deb-4a53-85e9-ce8833151812 | checkpoint | Check that the pipe insulation is installed
dfde2e08-07d0-46cf-bbb3-f087fe636a1b | checkpoint | Check that the acoustic insulation is installed
f7ed96b2-4df0-47e0-8162-35bfbb6f1e38 | checkpoint | Check that the pressure test is complete
76d8f5a5-9c84-4b9a-b1a6-7b13b7bcbb4c | checkpoint | Check that the test sheet is filled out
a8a31173-3147-46e3-9987-4b74d189d19e | checkpoint | Council inspection complete
a14741c0-46df-4cd5-af96-42b37c470a24 | checkpoint | Check the pipe labels are on
655b2390-9ffd-429f-ad20-e9a115605a36 | checklist | 1st Fix - water pipe work QA Sheet |  | 1st Fix - Water pipe work
c2342089-bdfd-4298-bff6-e7776b3c2241 | checkpoint | Check pipework is installed as per listed drawings
da69e755-11ec-45ea-9787-3e94e8d21222 | checkpoint | Check that the correct water and pipe sizing is complete to each fixture
62ffd305-182c-48f8-b5c7-41c220990d90 | checkpoint | Check that the wingbatts are installed at the correct height
23105dcc-a695-4c19-9de4-8df3b5362e7a | checkpoint | Check that seismic restraints are installed
966e8b87-4ed9-4776-9dc0-737da1e424d3 | checkpoint | Check that the waste pipe is the correct location
c52cc38c-1b43-44e2-982e-70712d7831a4 | checkpoint | Check that the fixing's are installed at correct height
ed706852-88c7-4b49-9918-820fb25a215e | checkpoint | Check that the pipe insulation is installed
8987034a-4393-4e59-a12f-4a223829563b | checkpoint | Check that the acoustic insulation is installed
b47ff244-b000-44f0-a0c1-1107e7dc6d28 | checkpoint | Check that the pressure test is complete
a3f86f26-eade-48d7-ad72-49fefb40d666 | checkpoint | Check that the test sheet is filled out
aec1cd22-0ba5-40f3-847a-a6c1ceccea97 | checkpoint | Council inspection complete
ca4fbbb4-e29f-4acb-97f4-ce2d28ed9dca | checkpoint | Check the pipe labels are on
c15f0c89-7888-4200-9611-66908d1577d8 | checklist | Add Demolition Fixtures Checklist |  | Room -
e4bdbbfe-594a-4109-94c6-a4ff4b9741d9 | checkpoint | Details Completed
ecfc0242-e90e-5988-a12b-0b736ee5fa71 | textbox | Location:
5bced3d3-83e8-588c-adfa-06df89dddf89 | textbox | Drawing:
b6979ed4-4f05-5e54-8024-a67b4345ca48 | textbox | Plumber:
ebe1831a-9c6d-5d60-a8e9-67503d7106cc | note | What area within space that can be demoed
57877f2e-e0da-5f25-b2d8-cdf8d8d03792 | tickbox | Ceiling Space
7acf3ef9-907f-5ee5-a60a-748413ed196d | tickbox | Room area
9bdc16c0-3ba6-4047-866a-7b07c0e7347a | checkpoint | Cold water services have been isolated and capped
a79cb994-e017-4e80-a04e-f1eafdf6ef2e | checkpoint | Hot water services have been isolated and capped
1dd931fb-8c98-47de-9529-4e565b97fa56 | checkpoint | Trap's have been removed and desposed of
b0b25888-4eec-4b42-a24a-9988e2f4835d | checkpoint | Waste pipes have been capped
59e5efcf-ff48-474a-b735-2115a5dd609a | checkpoint | LPG services have been isolated, purged and capped
c32a7b2d-6270-405c-b44e-071cb4d5afb0 | checkpoint | Compressed Air services have been purged and isolated
bab30ecf-069a-4b52-b4c8-1eb0e4542833 | checkpoint | All services have been isolated and all fixtures are now safe to be removed
2c310efa-fd5b-43a5-b6fe-e07bb52aac5e | checklist | Add Final Sign Off Slab Grids Checklist |  | Final Sign Off Slab Grids
9aa46add-df35-4d75-9db7-cbbfa3687715 | section | Slab Grids QA
4b222d2f-cb03-4126-acdb-c8f31d489eae | checkpoint | Steel clips ready for mesh tie down
483fe947-7e57-4379-988b-c69290a26766 | checkpoint | Pipe penetrations lagged to slab height
27025d9e-23dd-42de-9e77-fb62527a76a5 | checkpoint | Checked for damage at slab level all ok
d69bb58e-b8d2-4c07-811f-596c73ec1e34 | checkpoint | Water test holding
bde82168-c6d0-4891-909c-4a4ca2516640 | section | Sign Off
7c1b3691-5ef7-4acc-a28a-1b844a2ca9ad | checkpoint | Foleys Signoff
58df30f1-ab60-4ee9-8eb0-6ed3070a45f1 | checklist | Add Pipework Pressure Test Sheet - Water |  | Pipework Pressure Test Sheet - Water:
a3933c56-bff3-4ac0-b5bc-b1a8857ab0c7 | checkpoint | Details Complete
8ba575a9-ac6a-5c21-9ed0-191ccf8e7bc0 | textbox | Consent Number: ABA
972e0a88-62dd-5f08-bd95-279131547874 | textbox | Location:
ec111729-3336-5a29-b3be-117d705bfd89 | textbox | Drawing:
26bb339b-5e0f-52c2-b98f-0f73b45636f4 | textbox | Plumber:
4bd604a5-ae23-5763-ace5-e62a294c2403 | textbox | Date:
709db544-b1c2-415d-81c6-b878052e5d8e | checkpoint | Testing
90c86d43-4491-5b37-90f0-91e2af247c42 | note | Required Test Pressure: Static Water Test
fd244d81-9294-5e8e-8ab9-016ff5d53297 | note | Required Test Time: 1/2 hour (as per NZBC and ASNZ 3500)
23fd5b58-d81b-5b02-bcc2-7c2ba7d281c2 | textbox | Date:
d610bb5c-f728-59bf-907e-84895741a85d | textbox | Start Pressure: |  |  | (kPa)
41231202-8aea-522f-ae0b-e634d33fb3b6 | textbox | Finish Pressure: |  |  | (kPa)
a43d0a7a-6c59-47b3-a458-d6b6efd51e87 | checkpoint | Signoff
56fc0273-2a54-4eb4-95b1-e94870efc8f8 | checklist | Add Sanitary Drainage Checklist |  | Sanitary Drainage Below Slab:
6a5fc73a-d33a-4e86-aef5-9521e7894bfd | section | Details
bd271173-9379-4416-b52a-e31a0b46593f | checkpoint | Details Complete
152d4b14-840c-5253-b77c-3717d8cacb2c | textbox | Consent Number: ABA
3540a538-eb28-5239-aa32-8314638e247c | textbox | Location:
984e1fbf-f78a-5d3c-a492-a5503fabe5e8 | textbox | Drawing:
af461d2b-9134-590c-af87-7fa2120c0869 | textbox | Plumber:
636fa837-e1bc-50a2-9723-42a20bcfdb17 | textbox | Date:
6bbc4d8e-bb5a-4b6b-bd52-8c7515dbcd55 | section | Water and Waste Pipe Work QA
b9981172-7973-4cc3-a760-a66d0a7a1e09 | checkpoint | Area tidy and ready to start
324db00d-dadc-44b1-8878-9a8a7c80f711 | checkpoint | Check pipework is installed as per listed drawings
95ee67ce-dcf6-46b7-824c-468e358b7eec | checkpoint | Confirm Pipe bedding at least 75mm compacted thickness
35a13157-ae62-4a3a-9b3a-f58d1372316f | checkpoint | Confirm pipe bedding material AP20
47e0e983-5040-4df1-a35e-fab3833a15cc | checkpoint | Pipe work layed to invert and grades as per approved shop drawings.
1e0eb5b8-2795-4ddd-8afc-f0f0c37c6a4b | checkpoint | Check that risers are in the correct location and secure
1c4d1e06-fd51-44c3-9532-c731f1edf14c | checkpoint | Check that the pressure test is complete
38a46d07-6b13-465b-b596-a6da05f66f3e | checkpoint | Check that the test sheet is filled out
49b45661-ab8e-4e3f-999d-b7cd47ce10da | checkpoint | DCC inspection complete
3720e5a4-908f-4a95-bd3a-6490237e4ca6 | checkpoint | Trenches backfilled and compacted AP65. Marking tape installed
d58b8f78-9513-45ac-b1b5-eb3ee81b6614 | checkpoint | QA sheet completed and loaded in system
7ccd1627-4b0b-4f37-9319-7c5fcd920448 | checklist | Checklist - Backflow Preventer |  | Backflow Preventer
4a73cbbf-2f2c-451d-8c19-edcafc1592e1 | checkpoint-no-value | Backflow Preventer
3194238d-8f21-59ee-a069-d71df2dd615f | textbox | Date
16fd8028-041e-5335-a7be-5b1b1df451e5 | textbox | Valve Number
5ca008af-8048-559b-91e2-83dba2b3d974 | textbox | Location
ab0af96f-863e-47c7-b12c-8b4731e3d9ce | checkpoint | Result (confirm passed)
4b4e50bb-1da5-41c3-85b8-d573ab503e81 | checkpoint | Service label attached to RPZ
dcb08947-d469-44da-a678-0de2e44a4d30 | checkpoint | IQP certificate filed
53da0f50-1451-4e11-bcba-d16e4475d19e | checkpoint | Final Sign Off
0f04b8c0-c4d8-4c26-ba99-5d8ebdb1751a | checklist | Checklist - Demolition Fixtures |  | Room -
527b5350-6e57-4f93-afd4-0564102a3d46 | checkpoint | Details Completed
f4e2f08a-c3a5-5062-9eb5-ccb0cb542124 | textbox | Location:
7e7c1233-0d48-5aab-901b-cce355176b50 | textbox | Drawing:
2dcfcbd6-9fce-54a0-9ee7-edfc358e6cb1 | textbox | Plumber:
fc9523f7-5759-50d2-92c4-5cee53e57667 | note | What area within space that can be demoed
c1d19c60-cd32-537b-bdd9-73563f0cccd1 | tickbox | Ceiling Space
20042052-88e2-5c6c-94b0-b423d3e420ce | tickbox | Room area
a89d10b2-5b2e-4f26-8da6-1c6b7d530e8e | checkpoint | Cold water services have been isolated and capped
20527973-2182-4ac5-8d68-1a9351f3404a | checkpoint | Hot water services have been isolated and capped
622c0a9a-ab86-445e-acab-a66a6d495cf6 | checkpoint | Trap's have been removed and desposed of
d14dc945-e346-404d-8a2b-61fc29b2133f | checkpoint | Waste pipes have been capped
0f328296-4ab9-47d4-a5a2-21bbbc5f2bc3 | checkpoint | LPG services have been isolated, purged and capped
634c892f-4808-4cdc-986a-e39a10197b05 | checkpoint | Compressed Air services have been purged and isolated
181b8d85-bae5-43d2-858c-ea2776a2ebf7 | checkpoint | All services have been isolated and all fixtures are now safe to be removed
832b9498-ea2b-40d4-bab2-e9236d274db8 | checklist | Checklist - Flushing Valves |  | Flushing Valves
6f619941-6b6e-435c-aa94-615e2fc9d205 | checkpoint-no-value | Flushing Valves
480a52d0-3c92-58c1-b0eb-2d41d1761924 | textbox | Date
b88617a5-b0b3-512a-b643-e15dcab704b3 | textbox | Item
0b03c195-ea18-5653-a755-9e319c1e794c | textbox | Location
f07c615f-bef6-4f6b-9eae-f763a962d686 | checkpoint | Confirm Operation
b5816c86-2699-4fba-bb22-6ab55c995289 | checkpoint | GPF Flow Ring Installed (colour)
190afa6e-c40d-4564-b2fe-300e0c32874e | checkpoint | QA complete
b2085dfc-f419-4fb6-9f8c-95d5741d1df7 | checkpoint | Final Sign Off
763cb02f-79be-41a2-85cb-46c788f8537c | checklist | Checklist - Hot Water Balancing Valves |  | Hot Water Balancing Valves
fb1dc12d-7932-4d14-8435-4505d97acd4d | checkpoint-no-value | Hot Water Balancing Valves
5fd2904c-7f64-555a-a6bd-35d7c3df1996 | textbox | Date
508974ae-5b58-5b28-89a9-32f9fa6af0f6 | textbox | Location
d5493fa6-f866-55da-a03f-362ab77b3a71 | textbox | Valve Number
cc9d89fd-6533-41d1-a0b3-1e0d7125f990 | checkpoint | Hot Water Circulating
0a21f906-1740-47a3-9123-41dd879f3ba2 | checkpoint | Balanced Temperature
8c12f421-4448-42c5-a287-ce30517d7ab3 | checkpoint | QA Complete
ff7244f0-10af-4622-ae32-554a2c44392d | checkpoint | Final Sign Off
4afdb051-62a7-449e-bf89-2f56f8cadd8c | checklist | Checklist - Hot Water Clorafiers |  | Hot Water Clorafiers
23b1907b-68fe-4d6d-b6ce-f0165cb91bc0 | checkpoint-no-value | Hot Water Clorafiers
cb67ced5-6f4e-557b-9595-a73bfbef796e | textbox | Date
981eb858-c1ad-58aa-931a-eb0ecab1ee8c | textbox | Item
ca30164c-99d8-5814-8f5a-2e959d1b4f83 | textbox | Location
0c04e2a6-1637-44eb-ab22-74aa4ab5817a | checkpoint | Temperature entering
14ba39d2-7f2d-54b0-a455-b7a1383a5906 | textbox
e10fabcc-20cc-45a1-8670-41a36c7b17e5 | checkpoint | Temperature leaving
ecc4e79d-835a-5579-bcd1-3590f9d8d117 | textbox
873a0de4-f3c3-4958-8e52-21a983f254a0 | checkpoint-no-value | Sign off
79a2e261-98ff-5c39-8d04-a8cc053d1fba | textbox | Check time
1e319dc5-2f91-4172-bd5f-b6039a74ca74 | checkpoint | QA complete
7a7500cb-22e9-40fd-813d-578f2da1c8f6 | checkpoint | Final Sign Off
689e77f5-ac35-470d-a6fc-b2df70a3e717 | checklist | Checklist - Hot Water Return Pumps |  | Hot Water Return Pumps
a9bcac8f-6670-4a06-8a95-bd03331cf1d0 | checkpoint-no-value | Hot Water Return Pumps
60b09ce6-420e-5c13-bb72-d75cc2095dbc | textbox | Date
5414464c-baf5-51b7-89ba-8104a183e121 | textbox | Pump Number
a68c6d31-8783-5c8b-b57d-10a7241abb82 | textbox | Location
aadff8db-f26c-42ac-964f-98eb87fafa45 | checkpoint | Electrical Complete
858963d9-7892-4dc7-8ff9-88a7fcf33fb3 | checkpoint | Water Heating operating
8592a9d8-ea18-4e27-8c1a-6140ee34cc2f | checkpoint | System Balanced
b5dc24ef-651f-46c8-a57c-07f60c350107 | checkpoint-no-value | Sign off
9441ebff-e02b-5095-9e1b-20759e0e7af5 | textbox | Pressure diffrence across pump
c4e6a80d-6313-5994-879e-d05a63bf3d23 | textbox | Final Flow Rate
31539922-598a-4666-bc15-8b841cbe2940 | checkpoint | QA Complete
481bd779-6d0e-48fb-9a2c-8c0f92b66b19 | checkpoint | Final Sign Off
365fb79c-f8d1-46c0-af19-a8323d6c3428 | checklist | Checklist - LPG Meters |  | LPG Meters
696d7ab8-a2f2-4c7e-83fd-5807d6a0650a | checkpoint-no-value | LPG Meters
22099b9e-a97d-5765-9d79-0a3d4dcd1b0a | textbox | Date
3bc9afe4-720d-5001-95ad-07a60a59ac04 | textbox | Item
d519fb3b-e5a1-5d19-b2d5-ad75cb21727c | textbox | Location
62852b1a-92bc-4823-b044-465a7646a1f1 | checkpoint | Confirm operation with BMS
1ab96674-a5bd-4b8b-a370-487f87c3c2bd | checkpoint | QA complete
ebb6039e-c19c-4bd6-93b5-81c08f230645 | checkpoint | Final Sign Off
98406f5a-66b7-4904-b82f-d4f3f5c3229a | checklist | Checklist - LPG System |  | LPG system
0e347c93-fea5-4933-86fb-689e26ecf38e | checkpoint-no-value | LPG system
7bee12a4-a368-5f38-ab5f-7ca88bc235e7 | textbox | Date
fecb61ee-1d75-5c64-bfe9-d45c0f56114f | textbox | Location
58ce463a-45e5-4a01-96ce-477497acd754 | checkpoint | Test certificate filed
0a65ad6c-f3da-45ea-aea8-c664e9b37ff5 | checkpoint | Pressures set. Record below
1a632888-03b0-46db-a439-befc7af5b301 | checkpoint | QA complete
54a2e11e-ac0a-4bea-805c-f852bc5b2dff | checkpoint | Final Sign Off
eae25744-d4d9-4472-886e-655d940a570e | checklist | Checklist - Pressure Limiting Valves |  | Pressure Limiting Valves
9fcec5c7-8546-4647-8376-2b9830376bdb | checkpoint-no-value | Pressure Limiting Valves
ffb20c2b-9b78-5316-9e64-fb835837462a | textbox | Date
5fa412e1-8a0d-5e7e-b97e-a0ea7033a87c | textbox | Valve Number
5349901f-8cd6-5255-a3a0-dffa9a397249 | textbox | Location
fafd54fc-0857-4d53-a558-ae3985603b43 | checkpoint | Pressure Set
1425fa19-c994-4cbe-8523-6fa235d14579 | checkpoint | Set Pressure (KPA)
0d1da6a7-a226-5c2d-914b-5ca93878c40f | textbox
51df0d89-4d29-4cce-b78f-67375c424288 | checkpoint | QA Complete
7cbad0df-ec61-4011-8861-f9c3d41c55e9 | checkpoint | Final Sign Off
5f70f6f8-5cca-4259-9111-f386ccfc1bb0 | checklist | Checklist - Sanitary Drainage |  | Sanitary Drainage Below Slab:
a8b0acb9-9090-4625-bf82-5c96ba6313d4 | section | Details
ccaf2fee-138a-4ff8-9e34-766cb1c994e7 | checkpoint | Details Complete
9da87165-4fef-5d19-a788-a96c68fd7abc | textbox | Consent Number: ABA
3f0ca101-e976-5180-92b0-2ff60613f87f | textbox | Location:
1610a535-c6ca-5584-9b09-e27fdf12bc61 | textbox | Drawing:
4c6aa2a2-8dfd-5150-a377-c7e729719955 | textbox | Plumber:
d0fcfaca-3bef-5021-8dcb-c0e256755ddc | textbox | Date:
ad937907-3690-4ac3-b1bd-f24100a106ec | section | Water and Waste Pipe Work QA
8e198296-9b91-44e2-b931-7d9b78a24efb | checkpoint | Area tidy and ready to start
155ecdb6-d0a8-43f4-a8f9-0186a57838d4 | checkpoint | Check pipework is installed as per listed drawings
b67ed03f-7352-4425-98c6-ad1fd83530e9 | checkpoint | Confirm Pipe bedding at least 75mm compacted thickness
7f53b7b6-f3a8-4541-af40-1deffeb52c4b | checkpoint | Confirm pipe bedding material AP20
b118a5dc-bbd3-4dc5-a439-df9b9e2f4c56 | checkpoint | Pipe work layed to invert and grades as per approved shop drawings.
0f9b6329-8e8a-4d47-8673-59d82fcbad7f | checkpoint | Check that risers are in the correct location and secure
0e40a587-60f6-45c0-9efe-878a59a9c407 | checkpoint | Check that the pressure test is complete
97445c40-6861-475a-a2c5-a9c3bd1dfb55 | checkpoint | Check that the test sheet is filled out
d32a57f7-88a5-4250-8d7d-0a02eefbe3f9 | checkpoint | DCC inspection complete
d0f122e7-15e0-455c-bb15-f55f564da3b2 | checkpoint | Trenches backfilled and compacted AP65. Marking tape installed
7e4cc558-9fba-4f9e-a3e1-1c32c90c0755 | checkpoint | QA sheet completed and loaded in system
9a25f629-ca9b-476b-a708-5b9a56d70e64 | checklist | Checklist - Second Fit QA |  | Basin Sensor Taps
de8f588e-353e-47e2-a7a1-623e7ba230ea | checkpoint-no-value | Basin Sensor Taps
230dc699-ef49-5c0a-b472-2794d5338a2f | textbox | Date
97a83212-90a3-57d2-b7d7-0fc5a0604407 | textbox | Item
073c3c95-a4ca-5a2a-a4c3-3c5957e795de | textbox | Location
9373192b-2c89-463f-8819-373630dd390d | checkpoint | Confirm Operation
60880527-60b9-4be2-85e4-8c92acacfca3 | checkpoint | QA complete
467ab941-be9b-4920-93a9-f70b0ae5a0b4 | checkpoint | Final Sign Off
aeca8d3a-db2f-4d06-9d4c-6c71cd71108a | checklist | Checklist - Thermal Mixing Valves |  | Thermal Mixing Valves
d72ada3a-dd73-487c-ad0c-4fcc10d95c4a | checkpoint-no-value | Thermal Mixing Valves
141a5a50-eca4-51fe-804c-545b86d07ade | textbox | Date
5065fff2-84c1-5c96-986c-29eba3c252f6 | textbox | Valve Number
3d5a1cd6-79ed-5918-bc26-2cae753d67c2 | textbox | Location
e7ab7ac0-9ad4-43ef-873a-7ab40d5a07c4 | checkpoint | Set Temperature. °C
052e3811-4ec4-474b-a2d6-4e0b6d169df2 | checkpoint | Lock cap fitted
d29abcc0-d37c-4916-9a31-c32bebf18657 | checkpoint | QA complete
206373d7-bc3e-45a9-bf72-a46befa243b3 | checkpoint | Final Sign Off
e97df999-c601-4051-9849-5d3d384d9b68 | checklist | Checklist - Trap Primer |  | Trap Primer
0b84a91d-2ddd-4306-b835-dba282d10476 | checkpoint-no-value | Trap Primer
84d68375-e0fd-51cc-9792-e4d7b0eaf6dc | textbox | Date
e7c558e6-0816-52f4-8361-fa875ddddb17 | textbox | Trap Primer Number
790efe27-8b08-5a3a-ac58-3a3bbde131f4 | textbox | Location
49c166ea-fa4a-4708-b004-aade1d238ff0 | checkpoint | Water system complete and charged
45681aba-1ab7-409a-be24-8bcda31e44a5 | checkpoint | Electrical supply commissioned
8719024a-da05-476a-a755-331b6884ae0e | checkpoint | On/Off times set.(tick)
f8c6e415-e682-49b1-bded-6d433f01334e | checkpoint | "Test button" Press confirm operation.
8eafa8fe-b3a2-4793-b528-6fb86d4595a5 | checkpoint | QA Complete
a7dd733c-12bc-4f2d-a5c1-e1980e50ed79 | checkpoint | Final Sign Off
1fa859df-cb62-4149-94c4-f4f10490583c | checklist | Checklist - Water Meters |  | Water Meters
a1d91327-30f2-4755-b969-3928e0c71add | checkpoint-no-value | Water Meters
86e7736a-4cf2-5cf8-acf7-072676dc9897 | textbox | Date
4f3f7066-6848-517f-9fd4-3d318a06dff4 | textbox | Item
97ba2cd7-3838-51b8-85a6-56b02e392b2e | textbox | Location
a305bbb5-6307-4295-a171-46ba2c83fe55 | checkpoint | Confirm operation with BMS
fda271af-ff55-4901-8579-68e5dcf6a4e7 | checkpoint | QA complete
3ec4db7d-382b-4e86-a5ca-fbfc821e4cbd | checkpoint | Final Sign Off
38a7e22b-ea53-4b0f-b277-01f4914d4e94 | checklist | Checklist - Water Quality Testing |  | Water Quality Testing
c4940505-dc3c-4c09-bad5-2644b32561af | checkpoint-no-value | Water Quality Testing
c5845c41-f137-5c3a-9e14-65298549b113 | textbox | Date
731a42ab-8ec0-5f6a-8d0d-c4007eb8fa00 | textbox | Test point Location
2a267f67-eb64-41a9-a0ec-74686dd0211e | checkpoint | Lab results confirmed and attached
4246fcf9-383e-4e13-a50c-399169e88659 | checkpoint | QA Complete
eba20e85-ebfe-44c1-8041-c77415c3ac4e | checkpoint | Final Sign Off
9b8ad645-bcfa-4fbf-ad62-90bf4cab3ae6 | checklist | Checklist - Water Strainers |  | Water Strainers
a0d869ec-0746-41ad-b9ef-c3727dce819f | checkpoint-no-value | Water Strainers
4d03f969-a89d-5803-8428-470252698111 | textbox | Date
09ff102e-87fe-53ac-a238-a2e1ef16731d | textbox | Item
8c163c51-e2b9-5695-9a39-c929b4c8ca97 | textbox | Location
eeae5b5c-e93f-46be-ab0a-4fc70f18b3dc | checkpoint | Size (Micron's)
d3500488-4e53-4498-8051-bb78f818a037 | checkpoint | Strainer mesh replaced
755ac647-846d-4644-a765-cc1e2b4a6f98 | checkpoint | QA Complete
c16e1be2-fd3f-46a3-bb97-4dba13d3b63e | checkpoint | Final Sign Off
7a42b55d-3d74-4e82-9512-ed7fa087f647 | checklist | Civil Drainage - Stormwater & Foul |  | Civil Drainage - Stormwater & Foul
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
3f99e978-90f7-4d66-bf71-a102efdfb119 | checkpoint | Plans checked against what has been supplied for pipe types & size
c6283265-d283-47f5-be48-8f6e5504cdab | checkpoint | Trench shoring in place or benched if required.
db73ae75-eeb1-4f90-b37a-392787c3f02e | checkpoint | Trench bedding material (AP20 or dust) compacted
930bada3-eb91-4528-838f-cf88317d2cd8 | checkpoint | Sumps & manholes checked and confirmed for correct position
6fcd219f-38b4-46b5-bc71-a714e22e8a7a | checkpoint | Manholes have corbels in place and manhole benched
a5ba2519-5a9d-4ecc-89b3-82086c13f25d | checkpoint | Drop structures complete
d3d4288e-a97a-4d04-86b7-e4dd63eeddfc | checkpoint | Pipe laid to correct grade
9da55ece-5e6a-4a83-b14e-664d02d37990 | checkpoint | Pressure test complete
d1bfd343-7475-4130-8193-503f43faa98c | checkpoint | DCC inspection complete
9469e307-c202-4e47-8581-20cfb39dab30 | checkpoint | Trench backfilled and compacted
c2e4a543-51e8-463b-a372-eb44d2fafbb7 | checkpoint | Commissioning signoff
fc6fa1f7-53b9-413d-8567-45bef57b2ef8 | signoff
e161b0a4-b40c-4bb1-ba80-5460d88323bf | checklist | Gas Pipe Line Checklist |  | Gas Pipe Line Test Sheet
6753d118-c420-40e0-8a17-613ff597bff2 | section | Job Details
425f340e-db52-4f86-98e3-3dfac872f2ec | checkpoint | Job details complete
6adfbfc9-27a7-5730-b7ca-13658d93c34c | textbox | Job:
8d840f53-7bb4-5fac-bd8d-bd9782fd1dd7 | textbox | Gasfitter:
9f6d2782-ef98-537f-8d0e-39851073d045 | textbox | Date:
c746a487-d94d-5112-be21-bcb417833f8a | textbox | Site Address:
cb9002bd-2ff1-58c4-bb00-20bacc36a43d | dropdown | Gas Installation "Safe To Use" | No,Yes
e7787134-d4a9-5a61-9556-d347f5a7220b | textbox | Risk Classification
6b5a725b-2679-5be2-bbce-f090c642b12d | textbox | Part/Whole Installation
e69540ff-b204-5253-8f14-0d456294af7f | textbox | Gas Type
32f2cf79-d547-5178-bde5-ae9e7cd0ae4a | textbox | Certifying Gasfitter
48b74626-bcdd-545a-8372-ae495e0a0dbc | dropdown | Work done in accordance with means of compliance (AS/NZS 5601.1:2010 part 1) | No,Yes
ef8c4fee-0077-462a-a65c-47774040dbf2 | section | Test Details
dd37317b-2385-4885-a9d6-173400936b4f | checkpoint-no-value | Test Details
81afa944-4cd3-5abc-8337-9b52f44ade38 | textbox | Work undertaken:
72e973fa-3296-591e-8ece-25b49748d870 | textbox | Test location:
85ceccdb-b6af-460e-9297-16cb8f17f3f3 | checkpoint | Test procedure AS/NZS 5601.1:2010 Appendix E
53cca389-2794-530d-bf22-871ebb0b5f4e | textbox | Date:
0482fbb3-7d25-40bf-9613-0ac7de61d31b | checkpoint | Leakage test of Existing installation E6
2939c52c-0876-5e41-9703-da4fd281736c | textbox | Test Pressure: |  |  | kPa
7145107a-683e-5a2d-9abd-e37e7a61de1a | textbox | Duration:
395f1071-c6e9-5211-9643-baafe1f3cfa2 | textbox | Drop/raise
11f738bd-db72-41a8-8305-98a28a10331e | checkpoint | Final Connection Test E7
1e9724af-8de0-567a-af71-6586c27de737 | textbox | Test Pressure: |  |  | kPa
1dd012bc-5177-574a-83fb-b93a09779298 | textbox | Duration:
2f5b37e0-570f-55c1-a375-70bda91cd19f | textbox | Drop/raise
bb775e8a-7ba3-5f82-b001-79c4a49f0a46 | textbox | Working Pressure |  |  | kPa
ecf3574d-ad4e-4ca5-a341-5213cb92403e | checklist | Programmed Maintenance Checklist |  | Programmed Maintenance Checklist
08780e0c-4419-4483-940d-6816cfb5ab15 | checkpoint | Details
1d56504b-865f-5df3-b1ab-c58b41324254 | textbox | Maintenance Number:
474bb84d-d7c5-563b-893d-5c91060a941c | button |  | Area -
5f225e8d-6243-42d2-9c55-e06efa626cce | checkpoint | Having recieved approval to carry out the maintenance, ask the department heads if there have been any problems with the plumbing systems
b9ea543b-c7ec-4c50-8bdb-426970c288bd | checkpoint | coordinate with the electrical trade to carry out the maintenance at the same time
f0af80c4-e8d8-4ae4-be8a-55740a191fe1 | checkpoint | Inspect the integrity of the portaboe hot and cold pipework
bc98e873-ae43-4197-9866-077f9a54730f | checkpoint | Inspect the integrity of the waste water pipe work
072523cc-a8a8-430c-92c3-fa8c65071414 | checkpoint | Inspect the integrity of the HWC for leaks
56398257-c1ac-4f76-bf9a-62f0eed36d05 | checkpoint | Inspect the integrity of the HWC valves
af51f177-ce29-41c4-a6d0-6f489e6052eb | checkpoint | Inspect the integrity of the TMV temperatures
3d4ca3b5-1657-49a4-85d1-ead917db6279 | checkpoint | Inspect the integrity of the toilet flush
c0e001f1-0f07-42bc-8fdb-af6ccfea6cd6 | checkpoint | Inspect the integrity of the pumps
e3834230-2c48-4785-aba2-3d707267a109 | checkpoint | Inspect the integrity of the trap primers
f9225ffc-dfec-40db-a7f0-c3ab2bd93f29 | checkpoint | Inspect the integrity of the suction pipework
804b4218-d8e8-42b2-bfd1-22d4f797da99 | checkpoint | Inspect the integrity of the LPG pipework and valving
328f1f9b-a0d2-4855-b6c2-fd905abdaa6a | checkpoint | Inspect the integrity of the basins and sinks
32ba44b5-5bc9-4873-8de1-c2832c880584 | checkpoint | Inspect the integrity of the suction pipe work
7704301a-20f7-4096-8eb8-3df5e573bf40 | checkpoint | Inspect the integrity of the plaster traps
68851661-1710-4892-885c-38842439164e | checkpoint | Inspect the integrity of the foul sewer and water systems
993fc830-f17c-4c32-ba8a-0866664fb5ed | checklist | Pump Station |  | Pump Station
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
764cc0c7-6564-41c2-8ae0-01284b8238d7 | checkpoint | Check ground conditions for correct installation
1d90abef-f667-40be-9b35-3cd56760b378 | checkpoint | Backfilled with appropriate fill
8fdd694a-1e0c-46f7-9cca-375880ff293e | checkpoint | Check floats and controls clear of any obstructions in pump chamber
ab2788fc-64ab-44d5-a30f-03595d5326d4 | checkpoint | Check correct electrical connection has been made
26aef6ea-df72-4ef7-9db1-9577501e1277 | checkpoint | Fill tank with water to float level and check operation of pump
a7412f82-caf5-4c55-af4a-e6ad9d4b1d51 | checkpoint | Check high level float alarm
4ab8d3f2-76f7-482c-a95d-d9efa45aaddb | checkpoint | Commissioning signoff
e209793d-ab4e-4976-9141-2176c2323a04 | signoff
5fdd7000-1e17-4790-a8c0-0db073a79932 | checklist | QA Commenced/Finished |  | QA Commenced/Finished
6a638a51-dbd7-4573-a79c-688542c403e7 | checkpoint | Pass when work has begun
4039e020-568b-5f2b-915d-dbe7e2d86d49 | tickbox | Additional QA checklists specific to the room added and completed
e14fca03-5520-4ab8-8d0f-eac14518e0f3 | checkpoint | Pass when all work is done and it can be handed back to Southbase
71bfd78f-4c96-4666-9053-9439cc181758 | checklist | QA Sheet - 1st Fix - LPG |  | 1st Fix - LPG
e68427d7-ccc0-480d-a58a-d85da4890ecf | checkpoint | Check pipework is installed as per listed drawings
1bb350d0-3a19-48e7-861c-06908c72639e | checkpoint | Check that the correct pipe sizing is complete to each fixture
0edaed5e-d994-4fa1-91ef-6808be818057 | checkpoint | Check that the wingbatts are installed at the correct height
a20e7fdc-da94-4ebd-b75b-a457d7cb9d3b | checkpoint | Check that seismic restraints are installed
3bf8bc43-37d1-484b-bb36-25f17e2d801f | checkpoint | Check that the fixing's are installed at correct height
2bb33161-b171-4cc2-bbec-00c20c2e4984 | checkpoint | Check that the pressure test is complete
29c16a49-578b-4b7d-be1d-45f01aeda12d | checkpoint | Check that the test sheet is filled out
0fe84030-2c2b-4dcb-b202-a6c3a45d9de9 | checkpoint | Check the pipe labels are on
608e023d-24d8-492e-a74a-77689a49092f | checklist | QA Sheet - 1st Fix - RO Water pipe work |  | 1st Fix - RO Water pipe work
6ff88650-5450-4e50-9abc-c1de239d0ff6 | checkpoint | Check pipework is installed as per listed drawings
3f249074-aee2-47a8-bcba-582c7ce845f7 | checkpoint | Check that the correct water and pipe sizing is complete to each fixture
b779a830-2863-4c71-859b-a02b962d6b63 | checkpoint | Check that the wingbatts are installed at the correct height
268e0301-1552-498f-8494-8a003e6d8379 | checkpoint | Check that seismic restraints are installed
39031aed-d896-4ccf-b3fe-4502cb6afe5b | checkpoint | Check that the waste pipe is the correct location
9d7d0c95-b578-45d5-8f5c-ff99b22f1010 | checkpoint | Check that the fixing's are installed at correct height
1e385014-b7bf-4123-b66f-5d0954749904 | checkpoint | Check that the pipe insulation is installed
d5a49803-1467-4f9b-9d78-216824fbc836 | checkpoint | Check that the acoustic insulation is installed
1b01bc0d-d845-48e1-ba19-4e93cc879e45 | checkpoint | Check that the pressure test is complete
8cfd4e44-795b-44a0-94fa-3c09b15be756 | checkpoint | Check that the test sheet is filled out
afd379c4-a07c-4e6f-ae99-76ea559383b5 | checkpoint | Council inspection complete
ce8426c1-644c-40e2-91bf-5a314e0d04d7 | checkpoint | Check the pipe labels are on
077e8d23-b977-41b7-bc55-0696ff85fc7c | checklist | QA Sheet - 1st Fix - water pipe work |  | 1st Fix - Water pipe work
cca03704-f375-4e03-8591-2a370a68542a | checkpoint | Check pipework is installed as per listed drawings
f5de1dc6-45b7-42fd-968d-cd3fdc1a215d | checkpoint | Check that the correct water and pipe sizing is complete to each fixture
02b30e85-51b6-4a16-989c-5ccd5efa17b3 | checkpoint | Check that the wingbatts are installed at the correct height
494406df-66a1-421d-9ef3-c1628487128b | checkpoint | Check that seismic restraints are installed
ced83cd3-f390-4c19-b4a5-9a94b044ebda | checkpoint | Check that the waste pipe is the correct location
d6f73549-26ef-463a-85c6-e883e951a8ef | checkpoint | Check that the fixing's are installed at correct height
0157cdc6-104c-450e-9605-193ef8b6f0e9 | checkpoint | Check that the pipe insulation is installed
d75a297a-f5c4-41e0-964d-fc67f0bcdbd4 | checkpoint | Check that the acoustic insulation is installed
5951fb7d-83cf-4ed4-9286-1368dc3ac41c | checkpoint | Check that the pressure test is complete
b247e177-678e-4b35-865d-7524c6a5c512 | checkpoint | Check that the test sheet is filled out
fd539508-7297-41f4-8d7f-569be09068fc | checkpoint | Council inspection complete
067ccb6b-86ac-4292-bf47-6e922656e452 | checkpoint | Check the pipe labels are on
2b9e5d96-07db-400a-8e15-e90ab376565d | checklist | QA Sheet - Sanitary drainage - waste pipe work |  | Sanitary drainage - waste pipe work
a9cc0895-c76a-4db8-8ebc-b81110902502 | checkpoint | Check pipework is installed as per listed drawings
68fdc05b-a871-48d6-a936-270ec9a8a76b | checkpoint | Check pipe brackets conform to PS1 design
7224b59e-0d7a-4024-a5da-acbc9359de86 | checkpoint | Check maximum spacing of brackets not exceded.
38b6b7ca-90f8-46c1-84b7-905bed8698ad | checkpoint | Drains installed at correct grades/fall ratios
4a52ad30-64b0-4ca8-9b04-f7823b2f29b4 | checkpoint | Check that risers are in the correct location and secure
4fffade7-4f38-4d86-babe-6081ec427fac | checkpoint | Check that the pressure test is complete
e5f5b485-d5db-4462-b9ca-4bb2dd73cc70 | checkpoint | Check that the test sheet is filled out
934cc7ca-26ee-4c33-a88f-d81b070fc5d4 | checkpoint | Council inspection complete
2e89933a-61dc-4e17-b510-e4d56f4bae2b | checkpoint | DCC inspection complete
16cb163c-f7fc-4e70-9605-228142e17a19 | checklist | QA Sheet - Sanitary drainage below slab - water and waste pipe work |  | Sanitary drainage below slab - water and waste pipe work
b15e30e1-fc26-4b43-b49c-f19fa6a21f15 | checkpoint | Check pipework is installed as per listed drawings
d3e00f12-b8a8-408f-9791-a47163b91d9a | checkpoint | Check pipe brackets conform to PS1 design
6052ae5a-1be2-4cdd-abdb-ffa4ec7fe697 | checkpoint | Check maximum spacing of brackets not exceded.
59673db4-e4b8-4aab-a0ae-cfcf46b235a3 | checkpoint | Drains installed at correct grades/fall ratios
c157b7ae-c29c-49e4-9f29-e1e887de3468 | checkpoint | Check that risers are in the correct location and secure
5594e644-2108-4134-8067-4d17e2c48c90 | checkpoint | Check that the pressure test is complete
eb400940-3b7a-4616-babf-01f6f06a1923 | checkpoint | Check that the test sheet is filled out
61a17137-4563-4567-9124-2a9191a1ee9a | checkpoint | Council inspection complete
c232a972-d434-4979-9ff0-75ef32ae3e85 | checkpoint | DCC inspection complete
df404b3a-a363-47c3-ba94-941bed0878ce | checklist | Safety Shower Operation & Flow test |  | Safety Shower Operation & Flow test
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
6faadf3c-03af-4057-948a-15152c8177e2 | checkpoint | Water supply delivers required flow when shower and eye wash are operated
2e7b3302-7969-4c66-8160-352c89c5086c | checkpoint | Hands free valve operating correctly
d5254328-23af-45ee-9e60-24edf3680f89 | checkpoint | Shower delivers required 75.7 litres per minute
83177ac9-0862-4956-8b0a-6571ae39c8ed | checkpoint | Eye wash delivers 11.4 litres per minute
c540db73-1539-4ca1-9253-1caaa84b813b | checkpoint | Tempering valve set to correct temperature
d1c48963-e1e6-42f1-8734-508e328a64a1 | checkpoint | Commissioning signoff
c116e58a-82d5-425d-aa80-d01abe51ffae | signoff
fb0cf2e7-3a2f-4455-9ddb-ecef266f0e4c | checklist | Sanitary drainage - waste pipe work QA Sheet |  | Sanitary drainage - waste pipe work
dab2ceb2-6a00-475b-90d6-2223f885d138 | checkpoint | Check pipework is installed as per listed drawings
c841e192-660f-40d7-82cb-049bd3d8587d | checkpoint | Check pipe brackets conform to PS1 design
07e97209-e662-459d-ad09-fde38aa64ce1 | checkpoint | Check maximum spacing of brackets not exceded.
b9a16720-0b26-4627-8922-49648816ee25 | checkpoint | Drains installed at correct grades/fall ratios
dea8c39b-6169-41a3-ab5e-683290a3c408 | checkpoint | Check that risers are in the correct location and secure
12f42fe5-7e82-41d0-a0be-7c7e3f9cf9e9 | checkpoint | Check that the pressure test is complete
54172464-9a97-436e-b460-b3f0dbfbe42e | checkpoint | Check that the test sheet is filled out
0f13ed59-a23e-4b40-a106-ae23be6a773d | checkpoint | Council inspection complete
e5a93f43-055b-4a62-9f78-3f61df2abddd | checkpoint | DCC inspection complete
85761d80-1fcd-4da6-8c21-88f9f528738d | checklist | Sanitary drainage below slab - water and waste pipe work QA Sheet |  | Sanitary drainage below slab - water and waste pipe work
c552488e-69b7-485f-b9f9-a66ddb0fd030 | checkpoint | Check pipework is installed as per listed drawings
40e9acc8-26f0-4750-90e0-b8245e1f1c4e | checkpoint | Check pipe brackets conform to PS1 design
64046501-2027-4b09-bc87-28cd62a89c8f | checkpoint | Check maximum spacing of brackets not exceded.
ddc50108-e0ba-4f57-a371-aa4b07b7e90e | checkpoint | Drains installed at correct grades/fall ratios
4751c0a2-f53c-48d6-8183-950c46822fe9 | checkpoint | Check that risers are in the correct location and secure
c166d24c-950d-4653-8f32-8521ca73b543 | checkpoint | Check that the pressure test is complete
60d4662a-ed85-4635-9f88-3a350cc0a8e1 | checkpoint | Check that the test sheet is filled out
1d7717a6-0740-4637-addf-6bf7cc9fa462 | checkpoint | Council inspection complete
acb95793-30eb-4608-b6de-cf4a852f6134 | checkpoint | DCC inspection complete
710460f7-a11c-4909-83ee-0223d46035b4 | checklist | Seismic Bracketing |  | Seismic Bracketing
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
a3aeb2a8-c84b-4439-b674-c01ae676c210 | checkpoint | Location of Bracket checked on shop drawings
9ebe58c3-1e64-4948-9ab9-a6b81c6de651 | checkpoint | Correct bracket type selected
bd60fac5-e216-4ea0-a7bd-d85274e4d7ad | checkpoint | Correct Anchor selected and checked
550506c1-df5f-4b2a-896f-f3e9dd734353 | checkpoint | Anchor Hole Size and Depth checked
c11e7d7f-c2cc-4067-a390-5ff5f130a84d | checkpoint | Correct torque set for anchor
7b2f6d94-cd4a-4cc1-90f8-06166dc1c1bc | checkpoint | Final Photo of bracket
d691291e-8b8f-4637-bf75-a52614452754 | checklist | Test Sheet - Pipework Pressure - Water |  | Pipework Pressure Test Sheet - Water:
d3103d95-64df-4783-bc6d-214ec26ff6d3 | checkpoint | Details Complete
31fecb59-9fd8-5424-a9e3-84d6e5a1394e | textbox | Consent Number: ABA
c76edb6b-f630-503e-ab35-7b1b891c2d8d | textbox | Location:
0a9cb41c-cc79-5ddd-a725-b7f4300b8e7a | textbox | Drawing:
3ca28c87-22ae-5410-b0d6-abe145507367 | textbox | Plumber:
be603d54-ca19-54dc-bd6a-81fbb3c5c0b1 | textbox | Date:
f4b62b10-9a9c-4dd0-b44d-b7b370430066 | checkpoint | Testing
5a9d7f48-2543-58b3-bd93-9b2c489e10cd | note | Required Test Pressure: Static Water Test
1541dfb2-9f32-5798-b031-0bcf55b300cf | note | Required Test Time: 1/2 hour (as per NZBC and ASNZ 3500)
56014687-7cf8-50b4-81dc-9556046970b4 | textbox | Date:
4faa21fc-7925-539c-9a4c-2396bc74d782 | textbox | Start Pressure: |  |  | (kPa)
0b8f1647-98d8-59b3-b593-7d3b81c3479a | textbox | Finish Pressure: |  |  | (kPa)
9e760dc7-316f-4359-bec7-8a0e1f512cb8 | checkpoint | Signoff
6a15bfd9-9d81-43c5-b594-a5e5a2537b08 | checklist | Test Sheet - Pipework Pressure - Water/LPG |  | Pipework Pressure Test Sheet -
b203be6c-86e7-48cb-9a23-0d4c10edaf50 | checkpoint | Details Complete
057d672a-b37c-5a96-8103-ac430ff6022d | textbox | Consent Number: ABA 2016-513
4813f4ea-93c4-59ec-91e3-7df93338afe6 | textbox | Location:
efbbd926-30e5-5c23-956a-498e5ec122e1 | textbox | Drawing:
e091daa5-23a4-5f51-995c-15d171a450a4 | textbox | Plumber:
eb4f5655-da04-52ab-b089-7da51cbe36ae | textbox | Date:
383a9cd7-2af6-4982-9ae4-d40434b58cb9 | checkpoint | Testing
7f1df8aa-ea47-5301-97f2-3f14f7006542 | note | Required Test Pressure: 1500kpa (min)
b41d55d7-b832-5e3e-ba54-6ca27e4f5d2f | note | Required Test Time: 15 min (min) (as per NZBC G12 and ASNZ 3500)
6f6a9488-dd7d-5d63-9059-f779429d1e76 | textbox | Date:
17ccc683-aace-598f-b382-bd6c16d20e42 | textbox | Start Pressure: |  |  | (kPa)
bae25366-5cf5-5e8f-a818-eb1798734fc3 | textbox | Finish Pressure: |  |  | (kPa)
360226bc-8890-4c8b-8f32-a37c6bca7f71 | checkpoint | Signoff
c4738c42-b439-473d-ad7f-ae65ca9838f8 | checklist | Test Sheet - Sanitary drainage/Suction |  | Sanitary drainage/SuctionTest Sheet -
7e3d8ba4-f42d-4d02-8a71-acef4fe33749 | checkpoint | Details Complete
3ee0fb05-10ce-536a-ae25-81c6fd72c8e5 | textbox | Consent Number:
eef37951-54bf-5400-a1b7-e8dece7702b8 | textbox | Location:
6c856cce-d9a1-570b-a549-76b911dbafa2 | textbox | Drawing:
795ae24c-37ac-504a-8a59-9825f78fe4ce | textbox | Plumber:
df05d6bd-9a01-550f-84b3-b281af9633c9 | textbox | Date:
55db597e-1479-4571-9f18-084667bc62d3 | checkpoint | Testing
bb5e4ac5-3c6b-5782-9a26-d21bec651d7a | note | Required Test Pressure: Static Head
38b7fcca-d57f-52f2-b483-befdf2a8233c | note | Required Test Time: 10 min (min) (as per NZBC G12 and ASNZ 3500)
7815ea5a-a17f-55ad-9397-701c3b4bfa2d | textbox | Date:
ca434c42-bf17-5f23-b26f-d59be239b538 | textbox | Water Level Check 1
3a3c7600-93ae-5fd3-8109-2c22642e5178 | textbox | Water Level Check 2 |  |  | (kPa)
459aedc5-fc60-413c-b812-8dc8cc4f0c38 | checkpoint | Signoff