## ITP 04 - Pavement Layers
INSPECTION & TEST PLAN
Contract Name: 7020 Meridian BESS
ITP 04 - Pavement Layers
No. | TASK | SPECIFICATION REFERENCE | ACTIVITY/TASK | INSPECTION BY | TASK TIMING OR TASK FREQUENCY | ACCEPTANCE CRITERIA | UCCL | CLIENT
1 | Subgrade (Existing Brown Rock Surface) | Civil Works Specification Section 2, Clause 14.1 | Proof Roll Witnessed by Principal's Representative. | UCCL/MEL | Prior to commencing with the AP65 subbase layer. | Acceptance of subgrade by Principal's Representative. | H | H
2 | Subbase Course Material Testing | Civil Works Specification Section 2, Clause 14.4.2 | Material Test Certificates | UCCL/MEL | Prior to placing AP65 subbase layer on site. | Material meets specification. Material acceptance by Principal's Representative. | S | A
3 | Subbase Compaction (Under Containers) | MELNZ-CI-000133 | Clegg Testing - Minimum Clegg Impact Value (CIV) of 25. | UCCL | Prior to placing Fibre Concrete under containers. Minimum 2 tests under each container. | Minimum CIV 25 achieved. Acceptance by Principal's Representative. | W | W
4 | Subbase Compaction (Inner Zone Between Containers) | MELNZ-CI-000133 | Clegg Testing - Minimum Clegg Impact Value (CIV) of 25. | UCCL | Prior to placing Basecourse layer. | Minimum CIV 25 achieved. Acceptance by Principal's Representative. | W | W
5 | Subbase Compaction (Site Roads Outside of PCS's and Containers) | Civil Works Specification Section 2 Clause 14.4. TNZ B/02 Clause 7.6 | NDM Testing | UCCL/MEL | Minimum 5 No. NDM Tests per area. Compaction to achieve average > 95% MDD with minimum value > 92%. | Compaction achieves average > 95% MDD achieved with minimum value > 92%. | H | H
6 | Subbase Tolerances | Civil Works Specification Section 2 Clause 14.4. TNZ B/02 Clause 5.1 | Strings. Survey setout/as-builts | UCCL | On completion of Subbase layer prior to placing Basecourse layer. | Line and level within tolerances. | S | A
7 | Kerb and Channel |  | Kerb and channel installation | UCCL | On completion of kerb and channel installation. | Kerb and channel meets specification. | W | W
8 | Basecourse Material Testing | Civil Works Specification Section 2 Clause 14.5. | Material Test Certificates | UCCL/MEL | Prior to placing AP40 Basecourse layer on site. | Material meets specification. Material acceptance by Principal's Representative. | S | A
9 | Basecourse Compaction Compaction (Inner Container Zones) |  | NDM Testing | UCCL | NDM Testnig each area. Compaction to achieve average > 95% MDD with minimum value > 92%. | Compaction achieves average > 95% MDD achieved with minimum value > 92%. | W | W
10 | Basecourse Compaction (Site Roads Outside of PCS's and Containers) | Civil Works Specification Section 2 Clause 14.5. TNZ B/02 Clause 7.6. | NDM Testing | UCCL/MEL | Minimum 5 No. NDM Tests per area. Compaction to achieve average > 98% MDD with minimum value > 95%. | Compaction achieves average > 98% MDD achieved with minimum value > 95%. | H | H
11 | Basecourse Tolerances | Civil Works Specification Section 2 Clause 14.4. TNZ B/02 Clause 5.1. | Strings. Survey setout/as-builts. | UCCL | On completion of Basecourse layer prior to placing Basecourse layer. | Line and level within tolerances. | W | W
12 | AC Material Specification |  | Specification as agreed between Principal and Contractor. | UCCL/MEL | Prior to using the material on site | Specification as agreed between Principal and Contractor prior to works commencing. | H | H
13 | AC Pavement Testing |  | Testing as agreed between Principal and Contractor. | UCCL/MEL | On completion of AC pavement layer. | Testing as agreed between Principal and Contractor prior to works commencing. | H | H