## Table 1
INSPECTION & TEST PLAN
|  | Contract Name: |  |  |  | KEY |  | Date | Approved | Date
Perform (P)
ITP 4 - SP204 TO SP528 (MANHOLES AND PIPELINE - TRENCHED) |  | 7050 - DONALD ROAD CATCHMENT - WASTEWATER PIPELINE |  |  |  | Review (R)
Witness (W)
Hold (H)
TASK | SPECIFICATION REFERENCE | ACTIVITY/TASK | INSPECTION BY | TASK TIMING OR TASK FREQUENCY | ACCEPTANCE CRITERIA | UCCL | FNDC | COMMENTS
MANHOLE/PIPELINE INSTALLATION (TRENCHED)
Manhole Excavation and Bedding | FNDC Engineering Standards 2023, Sheet 39 | Visual check of excavation. Subgrade meets specification. Hardfill layer constructed as per project drawings. | UCCL | Prior to installing each manhole. | Subgrade meets minimum CBR of 5 (1.5 blows/50mm). Miniumum 150mm layer of GAP65, minimum CIV of 25. | H | H
Materials Quality | FNDC Approved Material List | Visual check for approved materials, quality and condition. | UCCL | On arrival to site, prior to using materials. | Delivery dockets, photos. | W | R
Manhole Installation | FNDC Engineering Standards 2023, Sheet 39 | Manhole installed in correct position and to correct level as per Project Drawings and FNDC EES. | UCCL | On completion of installation of each manhole. | Completed manhole installation checklist, photos. | P | R
Pipeline Excavation and Bedding | Donald Road Catchment - Wastewater Pipeline Specification, page 19. FNDC Engineering Standards 2023, Sheets 31-37 | Visual check of excavation. Lower bedding layer constructed as per project drawings. | FNDC | Prior to laying pipe. | Acceptance by Engineer's Representative. Photos. | H | H
Pipeline Installation | Donald Road Catchment - Wastewater Pipeline Specification, page 19. | Pipeline installed to correct invert levels and grade. | UCCL | On completion of each pipeline (manhole-to-mahole) prior to backfilling. | Acceptance by Engineer's Representative. As-builts drawings. Completed pipeline installation checklist, photos. | H | H
Testing of Manholes and Pipelines | Donald Road Catchment - Wastewater Pipeline Specification, page 19. | Engineer's Representative to witness testing of manholes and pipelines. | FNDC | During testing of manholes and pipelines. | Acceptance by Engineer's Representative. Testing checklists. | H | H
Sewer Connections (Household) | FNDC Engineering Standards 2023, Sheet 37 | Visual check of connection. | UCCL | On completion of each connection. | As-built drawings. Photos. | P | R
Sewer Connection (to Existing Wastewater System) | Donald Road Catchment - Wastewater Pipeline Specification, page 19. | Inspection prior to connection into exisitng wastewater system. | FNDC | On completion of installation, prior to connecting to existing wastewater system. | Acceptance by Engineer's Representative. | H | H