## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
60941a89-af19-49e6-8d08-983a2fcb252f | checklist | Ceiling ITP |  | Ceiling ITP
df21acb4-7ac5-4f1f-8858-d4db775ccaeb | section | Set out
ec8df6fb-c03c-461d-a492-719cfbac4602 | checkpoint | Reflected ceiling plans current revisions checked and ceiling set out completed as per the current plans
31c3a236-605e-4cc3-9e6d-4d725fb1980f | section | Construction Generally
9e057e2a-c0b6-4516-a675-5ebad6a02b92 | checkpoint | Install & fix to prevent looseness or rattling of ceiling components
827de70f-711c-448d-91f6-33e3d6b6a94b | checkpoint | Install the ceiling to allow for differential movement at abutting surfaces
af220dc3-de12-40c4-8326-d2f53041c0fe | section | Suspension system
acd97354-4cfb-4f96-a247-b622c8d82549 | checkpoint | Provide suspension system and workmanship as per supplier installation guides.
768509fb-78d0-4972-9420-d6a419064b18 | checkpoint | Provide additional back support or suspension members to prevent distortion, overloading or excessive vertical deflection.
4e7ba411-d00a-4b97-8af4-ea8b35110ae5 | checkpoint | Ensure that the failure of any one suspension point does not cause a progressive failure of the ceiling.
8a223bbc-a527-4a5d-a551-4eb47eaf77c1 | checkpoint | Where applicable, provide height adjustment with a length adjustment device at each suspension point.
fe5ff95f-8bfb-4cbb-bc5e-d3ecf89ff170 | checkpoint | Services: Do not fix to the installed services. Where services obstruct the ceiling supports, provide bridging and suspension on each side of the services.
f62b6504-b592-4b84-ac0d-6b80ea4c89b5 | checkpoint | Uplift: Suspension system and framing to resist uplift.
abfa066a-8d7b-426b-b2b4-dfbe660a8628 | checkpoint | Tolerances: Flatness, twist, winding and bow: 1.5mm deviation from a 1.5m straightedge places in any position
e678b142-ee42-4314-ad52-137645fe8963 | section | Hold Point
cf5e8cde-4b70-4f7f-97b4-75a150d112f1 | checkpoint | Suspension system completed – Ready for installation of ceiling tiles, lining and panels.
5bf9d431-1723-4d16-8dc9-2c724edc6fcc | checkpoint | Confirm all service trades are complete & ready for closing in of ceilings.
19022f8c-c8aa-4401-8040-6293e27cd329 | section | Ceiling Lining
963a2d89-16ad-413f-a235-d8d94e9fc2aa | checkpoint | Provide board lining to a finish and workmanship as per supplier installation guides.
f8bab96a-40ba-4673-ab6a-772ebd543a7c | checkpoint | Fit accurately and neatly, without distortion and free from air leakage and staining.
927ce9be-f4d9-421f-aeaa-a9a61b162958 | checkpoint | Set out patterned or heavily textured materials with a consistent direction of pattern or texture.
6f870619-6eff-4e76-bdc8-4ca8f0f68d5e | checkpoint | Cut ceiling unit edges: conceal, or finish to match prefinished edges.
6653c94a-ba99-477e-bb81-135683f26973 | checkpoint | Multiple sheet layers to fire rated and acoustic rated elements: Fill & flush up all joints on each layer and caulk up perimeters and penetrations before commencing succeeding layers. Stagger all sheet joints by minimum 200mm.
96ad51c0-661e-4dc0-9f9b-25c553bedd2d | checkpoint | Board joints support: Provide framing parallel to the joint on each side. Do not fix the lining to abutting building surfaces
f1a5c31f-ed9f-4f79-9dab-08dc398f772b | checkpoint | Flush joints: Provide recessed edge sheets and finish flush using perforated paper reinforcing tape. Locate & position joints to intersect light fixtures, vents or air diffusers.
e6e953ea-3ae7-4e52-85a3-77e2a16e4326 | checkpoint | Tolerances: Suspension system bearing surface for flush lined ceiling to AS/NZS 2589
385a687a-58ec-4953-9f4a-ff54cfaa4e70 | checkpoint | Levelness: Max tolerance of ±5mm relative to the documented height datum for the ceiling in each room or space.
f43f3b23-413a-4e94-b0a4-7480f5518c83 | checkpoint | Trims & accessories: Provide trims at junctions with other building elements and surfaces, including walls, beams and penetrations.
fc60b50f-9047-4062-94ee-15d4b85f3921 | section | Control joints
7d3c4f46-58c8-4762-8419-a128541f1a72 | checkpoint | Align ceiling control joints with the structural control joints. Do not bridge structural control joints.
6de76021-c98d-414a-a0cb-c25f67109790 | checkpoint | Provide purpose made PVC control joint beads where documented.
f0c27c05-52b8-517a-9c73-709e1e317e71 | note | Provide framing parallel to the joint on each side.
e222f189-5973-5f18-b52b-88d5711f115e | note | Plasterboard lining: 12m centres
4368e638-4bf3-536b-aa77-94d5b545b559 | note | Fibre cement lining: 7.2m centres
ef0adfc2-c028-4fe7-822a-5a169d64906d | section | Bulkheads
a6f5e34c-d3d4-478f-9d94-9a9037e75b83 | checkpoint | Integrate bulkheads with the ceiling structure and brace to prevent lateral movement. Where ceiling is terminated at the bulkhead, provide for seismic requirements
da0256f3-cbe4-4d13-9295-3cd32b35cf7a | section | Tolerances
1d622821-75bf-48db-8099-b921f31e63e3 | checkpoint | Flatness, twist, winding and bow: Maximum 1.5mm deviation from a 1.5m straightedge
39515853-1ef6-456c-9453-59453db9229b | section | Acoustic installation
dde6be54-4b18-4264-8352-6524debaa001 | checkpoint | Where documented, place acoustic batts on top of ceilings system and butt to each other and to partitions.
9f05ccaa-4eb5-4334-ba5d-7c7654634d19 | checkpoint | Tightly butt and trim neatly around services items and other items.
2ae6b4da-8aa2-408d-bddb-b1631ac6f68e | section | Smoke baffles and acoustic baffles
2bca070a-7f39-4228-bc4c-f757e5a675c7 | checkpoint | Provide approved smoke and acoustic baffles where required
8cb5cbed-c345-4a0d-9cd0-f2953aafcfa0 | section | Additional checks for fire-protective board lining
2ebd199c-6674-47c1-994f-201cb45fe579 | checkpoint | Check the fire resistance levels on RCP
55a4ce48-a2b9-4e3b-b4ef-01a0dbc280be | checkpoint | Fixings: Direct to concrete elements and to purpose made steel framing
f6a3ab9f-0a6b-4147-b72f-62c2d7593769 | checkpoint | Penetrations: Seal penetrations in the board lining to maintain the integrity of the required fire resistance level including suspended ceiling hangers and suspension systems for services.
30f159b1-6ad7-436e-aff8-c15282b883c2 | checkpoint | Board perimeter: Provide fire sealant and trims at junctions with other building elements and surfaces, including walls, beams and penetrations to maintain the required fire resistance levels.
39155ce0-8d4a-4812-8403-f500f7b23321 | section | Access panels
481dedf6-70a8-4ad3-ac49-a784a4e9f7a6 | checkpoint | Match the access panels to the ceiling in appearance and performance
eb441c87-2bb1-427e-ac29-52210f5099fa | checkpoint | Provide access panels supported and anchored to permit ready removal and refixing
9b713267-0424-4f1f-a465-ce993f0aae1c | checkpoint | Provide fire rated and acoustic rated panels where documented or where required to maintain the designated rating of the ceiling element
cd880fd6-569c-44f2-b743-d3e6657a1871 | checklist | Corner Guards ITP |  | Corner Guards ITP
67e31b25-9d49-4ec2-9b8e-6c20fad52890 | section | Set out
89bc5e08-4c56-4f24-88a2-9e24471ad755 | checkpoint | Wall setout plans checked for AMW-104 & AMW-105 locations
8075ff05-c272-45bf-bea7-9d5ecb8b40e5 | checkpoint | Setout heights confirmed via site survey
9128abfb-4331-4609-9a43-0c62edcb14ca | section | Materials
0ba67937-fc44-4c5d-8404-aed1ff359383 | checkpoint | Confirmed AMW-104 & AMW-105 supplied as per spec
62ee4a89-7564-4cc4-8aa5-02598424587d | section | Installation
58e5a7bb-1627-4baf-89ff-66fbe8a85d5f | checkpoint | Fixings installed with tension
e0878995-13d9-4bec-8517-e45748bbd9bd | checklist | Doors & Frames ITP |  | Doors & Frames ITP
da0be092-fef9-46e1-b31f-eb4cc0c93a6e | section | Take delivery
69b3c3b7-2f03-4b29-a56d-0b9785e49c55 | checkpoint | Frames as per design documents
a0fd5c80-0885-4e9e-8f17-ebcc6f3b226d | section | Setout
2a1a343e-8588-4523-bfcc-7c35e87499de | checkpoint | Ensure Frames are set out as per Partition plans.
2bf8ebed-5b4d-41bf-b6a8-803b70ae317f | checkpoint | Set out is to be read in conjunction with Door Schedule.
787b4c44-c8e8-43e0-a93d-546bd2850832 | section | Frame installation
975fd97a-d78d-4084-9b79-b2a705b788e9 | checkpoint | Frames are plumbed, levelled, straight and within acceptable tolerances
de63c075-4515-4eb0-9d82-12c5b6a3f380 | checkpoint | Frames are adequately fixed or anchored to the building structure
b2292320-8f61-4f08-ac4d-702dc6c0406b | checkpoint | Frames are installed so that they do not carry any building loads
44281fc1-02d9-4dcf-b1dc-ec885e6edd60 | section | Door Leaf installation
e64d59e5-2393-4a4b-bc20-c6bb9fc5c8ea | checkpoint | Hardware preparations neat and correct
385efef8-3206-4fd8-9aa8-aa865e00eb95 | checkpoint | Moving parts operate freely and smoothly, without binding or striking, at correct tensions or operating forces and are lubricated.
ca8e9423-fb53-4453-ba19-d618db4faf12 | checkpoint | Fixings, rebates, grooves and clearances as necessary for installation and operation of the seals are provided.
28de060c-91d9-446b-a561-761a88e6e1a2 | section | Hardware Installation
4a39985b-a889-4d23-97a9-447060f79f3c | checkpoint | Hardware schedule checked
3f0720ab-4cf6-4588-89d0-e5635271dd34 | checkpoint | Hardware installed and operating as required
2a6c2a8f-c62e-49d0-993f-5cfb89d77095 | checklist | Paint ITP |  | Paint ITP
88943f59-4889-41fb-861e-d0035c03956f | section | Spray out internal
efa86a45-d5b9-45f5-b295-0fb4fa974cf0 | checkpoint | All plastering sanded and internal junctions free from dust prior to sealer undercoat
209920a8-ba82-4a23-a2e7-dfc22c09c79d | checkpoint | Full protection to joinery, window frames etc prior to painting. Any overspray is cleaned off prior to completion of spray out.
a74242c1-9064-4da1-8431-a4877b6f4e95 | checkpoint | All nail holes, joints and gaps are filled prior to painting.
6c34d677-7bc0-4325-90d5-b7a3883d2a50 | checkpoint | All edges to internal / external doors are sealed and painted as per manufacturers specification.
de4d89d2-3053-4376-ba0b-44771d327f44 | checkpoint | All hinges, door furniture, latches and striker plates if removed are to be retained and re-installed prior to completion.
f3caa5cc-6124-4ede-904b-43ddd2d87017 | checkpoint | All ceilings are lightly sanded in between all coats and are back rolled and layed off in reasonable fine stipple finish.
b8300d28-6117-4ee1-b21f-59d9238c7438 | checkpoint | All wall coasts are back rolled and layed off in a reasonable fine stipple finish.
a82abec7-ade5-4958-ad85-94b968fb325d | checkpoint | All paint is NOT site tinted or any other liquid added or altered without written approval.
06595880-ea5a-4d50-ad8e-7f5d1aac74e2 | checkpoint | Clean up is completed ONLY in the supplied wash out area.
a2dbc1d5-b112-4cf7-9a52-1938473a2e3d | checkpoint | All rubbish is to be placed in the bins provided and the area is to be left clean and tidy and void of rubbish and excess materials.
f5b9b4d1-f6a5-49b4-9c63-e5131be206e0 | checkpoint | Ensure no damage is done to other trades work (if so, you Must Report to the Supervisor and Wadsworth Project Manager immediately).
bb7c6657-bd93-471d-ba7b-bd564f55d6f2 | checkpoint | All completed works are consistent with the scope of works supplied by CBGU JV, the supplied paint specification, and approved samples.
72f69e43-a01e-4204-be78-9a0c6c073a63 | section | First Coat & Final Coat
665d6390-232f-4118-a3c4-5af5d479fe25 | checkpoint | Full protection to joinery, window frames etc prior to painting. Any overspray is cleaned off prior to completion.
1fbe6384-cd29-424b-ae73-fd321781ac4d | checkpoint | All nail holes, joints and gaps are filled prior to painting.
14fb0010-ba39-4f7f-976e-5484523542f4 | checkpoint | All edges to internal / external doors are sealed and painted as per manufacturers specification.
deaf4d8b-8d5b-443d-b18d-dec0569d0673 | checkpoint | All hinges, door furniture, latches and striker plates if removed are to be retained and re-installed prior to completion.
06345fa7-1ddd-44c5-9727-c5c52de86792 | checkpoint | All walls are lightly sanded between coats.
cd1795d4-0f85-4785-bb99-5538f091ae9a | checkpoint | All wall coasts are back rolled and layed off in a reasonable fine stipple finish.
0c7d8060-1715-43b3-9288-1d2e5a1fd78e | checkpoint | All paint is NOT site tinted or any other liquid added or altered without written approval.
ce5efa3d-41eb-458c-873b-1343c139323d | checkpoint | All cutting work is consistent is consistent and complete in a tradesman like manor.
c439dff3-9ec1-4cc4-89a7-9c5ae6d06e66 | checkpoint | Clean up is completed ONLY in the supplied wash out bay.
ec188ff6-06c9-4be3-bbfc-854c6b01df44 | checkpoint | All rubbish to be placed in bins provided and the area is to be left clean and tidy and void of rubbish and excess material.
8a4e00b6-115b-4367-b07a-d68219ef5243 | checkpoint | Ensure no damage is done to other trades work (if so, you Must Report to the Supervisor and Wadsworth Project Manager immediately).
192f82fa-d621-46df-bf91-e25e028b96f4 | checkpoint | All completed works are consistent with the scope of works supplied by CBGU JV, the supplied paint specification, and approved samples.
dd109a6e-fa31-435e-8a6b-465a1e29bee4 | checklist | Partitions ITP |  | Partitions ITP
36aac969-f31e-433b-a69c-3a5988236bc1 | section | Set out
6d93512c-9528-45b1-b237-6519aa17711b | checkpoint | Partitions set out plans current revisions checked and wall set out completed as per the current plans
1aa901e3-9f2c-464f-b036-6df7a7add872 | checkpoint | Minimum/critical dimensions (face to face) on drawings checked
3c187d51-3817-4e00-8226-58a5f3131b8e | section | Stud Framing
79b92609-84b6-43fc-8d26-aa402713cfb2 | checkpoint | Base & Head tracks fixed in accordance with steel stud partition design. Typically ≤600mm centres and 100mm from ends
18614645-469a-413f-a01a-96dacd367188 | checkpoint | Fixing to post tensioned concrete: Maximum embedment for fixings = 50mm
f7448dab-2cfc-4e09-ac69-cc0fee34cd7b | checkpoint | Stud spacings correct as per steel stud partition design. Noting max 450 centres for wet area sheeting.
c4598d48-3183-4a2f-9306-b0a446630af8 | checkpoint | Fixing to post tensioned concrete: Maximum embedment for fixings = 50mm
90bb6b18-6a5b-4ae4-abf6-ef618f2a49e1 | checkpoint | Door frame openings as per Rondo design
c8af8519-a52c-4b41-8e2f-1c74ccd11bd8 | checkpoint | Full height partitions: Fix deflection head tracks to the floor slab soffit to allow a minimum deflection capacity of 20mm.
bd5638e1-2d56-4b31-815c-2bdaf43f21dc | checkpoint | Rotate intermediate studs into tracks for friction fixing
60881634-ded1-4ace-beae-655ffa42894b | checkpoint | Structural floor control joints: Disconnect partitions over joints with detached double studs and ensure bottom tracks, bracing and top tracks are not fastened across joints
5ecb68a6-2fa8-4d9c-89f1-9eed7698249d | checkpoint | Stud service holes: Splice additional stiffening to studs if site cut service holes exceed 1/3 the width of the member
35b939cf-071c-4de1-b0b1-d1a83fc89f12 | checkpoint | Provide fire, smoke and acoustic sealing where indicated on the drawings/details
e1ee475e-7302-4649-9549-c0977c4187de | checkpoint | Noggings: Fix noggings as per steel stud design.
07491fd7-4319-4243-b233-f6b051901844 | checkpoint | Door frames: Installed
234d558f-9ac7-49fb-aa0b-a5dd7012af3b | section | Bulk Insulation
d5cffe78-324f-4ac6-8144-3ce0d3952dd7 | checkpoint | Install acoustic and thermal insulation.
d5e1bc9b-7f54-4a3f-a0e4-667c0418a6f1 | section | Hold Point
785f630d-8d6d-4087-9729-6b8d0ca85e21 | checkpoint | Framing system completed – Ready for installation of sheets.
4a1cae7a-77f2-4b3d-b2b9-d32aa4571ac1 | section | Board Lining
ba4a2532-9324-4b22-bc32-4ec72fbcf36d | checkpoint | Stagger end joints in a brick pattern and locate them on framing members away from the corners of large openings
5a352650-73b4-427a-9043-5d75c1acf6cf | checkpoint | Multiple sheet layers: Fill & flush up all joints and fixings in each layer and caulk up perimeters and penetrations before commencing succeeding layers.
b1ac6869-f04c-4b58-b4ee-57788777cd2d | checkpoint | Butt joints staggered on adjoining sheets and opposite sides of wall.
391eec6c-903b-47ce-b314-415adc70e81c | checkpoint | Fire rated recess joints staggered on opposite sides of the wall, or backed by steel nogging
29348e6d-2765-4fbf-bd4d-3812ea2defd0 | checkpoint | Tape & Bead all joints and corners as required
eb00a0ba-acda-4dfa-bc99-efd3dc156a6a | checkpoint | Provide sealants at junctions between partition systems and with other building elements
6413688a-4617-4c07-a4b1-8c795705a2ab | checkpoint | Provide trim such as beads, moulding and stops to make neat junctions between lining components, finishes and adjacent surfaces
9588b7d6-0637-4d45-a417-db85730ae20d | section | Control Joints
d6f57add-0ae2-4f74-b7da-853f3d27b288 | checkpoint | Control joints to coincide with structural control joints
894bc04a-44c0-49c4-8a3b-0d38e2d4f3c7 | checkpoint | Provide control joints as follows:
1edec3df-527b-5bbf-baa0-81c3122bbbce | tickbox | Plasterboard lined partitions: 12m centres
ef2f7607-bea7-560a-813c-b3b9f8c4fb92 | tickbox | Fibre-cement board lined partitions: 7.2m centres
09c0bf82-e740-560f-8649-0eb7deffe783 | tickbox | Board lined partitions in wet areas: To suit joints required in tiling and at max 4.2m centres
b21d5a8c-1bda-4219-9f0a-c935d67bcfa8 | section | Tolerances
8938849a-801e-48c0-b50d-632574b52d87 | checkpoint | Flatness, twist, winding and bow: Maximum 1.5mm deviation from a 1.5m straightedge
92d380a7-47b1-415a-afea-6384f0089414 | section | Additional checks for Fire Walls
33e244f4-e602-4fca-8685-f700ba3a1556 | checkpoint | Installed as per board suppliers design & install specification
7b21a3b7-acc5-475c-9fa7-b28b61906b10 | checkpoint | Correct FRL achieved
54552967-6320-43bf-875b-9d7dd25ca272 | checkpoint | Perimeter fire rated sealant completed.
5d6cc4ce-7887-4286-9e11-22f3fa6c251f | checkpoint | All penetrations through fire walls below and above ceiling protected/sealed – Service penetrations sealing by others
7c6eed79-60bc-4580-a3e2-f8cf3b778394 | checkpoint | Fire door frames installed
80548095-28f2-40ed-9f51-b24750a9e239 | section | Additional Checks for Smoke Walls
87d5373c-edb1-40d5-be57-38cfec248d2a | checkpoint | Deflection heads and all joints sealed, taped and set (Sealant is approved prior)
918c89c1-813f-4780-8e1f-a2368305424a | checkpoint | All penetrations through smoke walls below and above ceiling protected/sealed
00bccb1e-1caf-49c9-a64f-c117b556e23d | section | Additional Checks for Acoustic Walls
96b2a994-badd-4def-bb9f-822c0c3b68b0 | checkpoint | Deflection heads and all joints sealed, taped and set (Sealant is approved prior)
78a82446-dfb0-4cd5-8b40-e7c014f2c103 | checkpoint | All penetrations through smoke walls below and above ceiling protected/sealed
3c9680f5-6b1c-4729-8151-a1b2abbf9b13 | section | Access panels
d56f982c-091a-44ab-9228-a372d6b26354 | checkpoint | Installed with consideration for required acoustic, smoke & fire rating.
f34a734e-9c7d-4042-9766-4df1ba13023a | checklist | Speed Panel ITP |  | Speed Panel ITP
e43cca28-eaf8-44c4-aa85-1d8ca68271e1 | section | Prior to Commencement – The following documentation are completed and approved
0abc53a9-5bde-4b13-b1ee-f8cc27b109c4 | checkpoint | Samples and prototypes submitted and approved (Fire sealants approved)
acd075d7-2d23-4c4b-8727-35f013577bcd | section | Set out
0eaa03b3-8617-4edc-afbc-57babeb60129 | checkpoint | Speedpanel walls set out plans current revisions checked and wall set out completed as per the current plans
75732784-3316-45e3-bb57-b7655259d8b2 | section | Framing & Speed Panel
565af6c2-b7f9-491d-9bf3-ae1d63687721 | checkpoint | Powder coated speedpanel used where required
cec877ec-ecb0-4f63-a04a-1d9cc7cc1d30 | checkpoint | Fix tracks to floor & soffit per manual
e7fd97c8-09cd-42f5-ba78-84b224538eb1 | checkpoint | Provide fire, smoke and acoustic sealing where indicated on the drawings/details.
0239bc34-eabb-4dc4-8116-f819860dd415 | checkpoint | Ensure that the configuration is as per the Speedpanel site specific detailing.
dae7090d-f643-4d62-8a75-e18940f5a012 | checkpoint | Ensure that all caulking is as per the Speedpanel site specific detail.
40cd4a5b-ee47-4c34-8b41-2ae7efd17f88 | checkpoint | Ensure openings are as per the specified jamb & door sizing.
3fb8d2bf-4883-4aba-8b80-6ae4d6d54ce7 | checkpoint | Door frames: Installed
88344d9e-3dce-46ec-a6a5-bac899cd67f5 | section | Tolerances
05fa2806-8406-4da1-93c1-21b1ee7f4797 | checkpoint | Flatness, twist, winding and bow: Maximum 1.5mm deviation from a 1.5m straightedge.
5cd69a85-6c29-4b59-8e4a-947240feaaee | section | Penetrations/Access panels
02329a5d-530c-4c81-b310-5d7ac7904856 | checkpoint | Installed as per Speedpanel design & install specification.
eeebfb90-4ccd-4111-90eb-4f5f05f9c448 | checkpoint | Correct FRL achieved.
62b2cb19-6ba7-4d01-bcde-11769109993b | checklist | Underslab Insulation ITP |  | Underslab Insulation ITP
d9c7f729-fe02-4e0a-94e2-6a742418c4e0 | section | Take delivery
4ce07b67-b2db-422a-968d-97e6b8471ec2 | checkpoint | Insulation panels arrive as per Design Documents and defect free.
7c6e30c1-bc28-4fdc-96cf-59543fa7e96e | section | Setout
9d78fa72-c9f7-4156-b6ca-a8c3d1c88c69 | checkpoint | Ensure most up to date drawings are being utilised
4df3161b-691b-491b-b519-5138d21aed7a | section | Execution
18b5f090-b927-413a-ab59-dfa4eb87995d | checkpoint | Mechanically fix panels to Manufacturers Specifications
9ad3eadc-7059-4e4d-8049-3bcafd323853 | checkpoint | Tape all joints and exposed edges with a minimum of 75mm wide silver tape
112e66e9-a3e1-454c-9819-ef2944a5c6d3 | checklist | Wall Protection ITP |  | Wall Protection ITP
c91b8d1f-77ad-463e-8f33-8364c4a50f85 | section | Set out
46f7f84c-6409-4e87-a094-21e5453207a7 | checkpoint | Wall setout plans checked for TRM-606 & TRM-607 locations
56535435-2099-45f6-819a-76258b48cbd2 | checkpoint | Setout heights confirmed via site survey
7ca2cbbf-242c-4ef2-b450-bafb0120603a | section | Materials
bcd87b54-b6d6-4d2b-b98a-c9fdf36c378a | checkpoint | Confirmed TRM-606 / TRM-607 supplied as per spec
6acf5ebe-fed3-4e7e-854b-1f6d5e15e984 | section | Installation
f740fe9e-1888-4684-922a-c9fd6759bd50 | checkpoint | Installed with fixings @ max 600 centres
51ec5775-7ad5-48d4-868d-e13c00c090f9 | checkpoint | Joints at intersecting boards finished neat
4bace4a3-f2aa-4219-9341-f023afb8a144 | checkpoint | Fixing holes filled
848e56ee-ada8-47fc-91a8-0617df358e66 | checklist | zSYS - Doors & Frames ITP (old version) |  | Doors & Frames ITP
86bed9cf-9f51-4de8-8312-5a8703516545 | section | Take delivery
865d4e21-8804-45c7-afe5-7b1831e50f63 | checkpoint | Frames as per design documents
ecf6d02a-86e4-4722-86ec-214d2541d222 | section | Setout
e55f14eb-0bea-4691-88ee-ac90d3c61699 | checkpoint | Ensure Frames are set out as per Setout Plans.
e78e87b4-603a-4d66-8758-f13de2569eed | checkpoint | Set out is to be read in conjunction with Door Schedule.
61fe1cba-f20b-4962-b4fe-8f4b3b4cf31b | section | Execution
59b4f18d-9f45-4079-8deb-17e834f41004 | checkpoint | Frames are filled in accordance with acoustic or fire requirements where applicable
5b170df2-0a5d-4a79-94c0-732b38b4a58a | checkpoint | Frames are plumbed, levelled, straight and within acceptable tolerances
3c4e0140-b001-4882-b13c-a8f3941a88a7 | checkpoint | Frames are adequately fixed or anchored to the building structure.
ce43b928-af78-47e4-8527-4cf41a10d78e | checkpoint | Frames are installed so that they do not carry any building loads
0565947d-833b-41ab-b8c9-bd890fa9edd3 | checkpoint | Fire door frame note: Fixings to substrate to be in accordance with manufacturers instruction. Steel stud frame typically, 10 gauge steel screws at max 300mm centres and no more than 100mm from each end.