## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
004b6c55-2e59-484c-bd8d-e404e1e17c72 | checklist | Ceiling ITP |  | Ceiling ITP
a86e2d27-0022-461f-b1da-b889abf09e1b | section | Set out
ceccbbe9-6eaa-4aa1-88fb-d625f43f973e | checkpoint | Reflected ceiling plans current revisions checked and ceiling set out completed as per the current plans
23ca8d82-e592-4559-8cf6-a62c5d574907 | section | Construction Generally
6ccc4978-b749-475e-b2b8-676970c258a6 | checkpoint | Install & fix to prevent looseness or rattling of ceiling components
f2805ab9-aa77-4006-9b4a-8155d6004959 | checkpoint | Install the ceiling to allow for differential movement at abutting surfaces
0670cb19-eebe-45bb-ab46-841a0e82dbc6 | section | Suspension system
5bc71ee4-bd20-47c1-b4f1-1f67a8ec8d96 | checkpoint | Provide suspension system and workmanship as per supplier installation guides.
65761349-f469-48f4-9855-bcc05a50d916 | checkpoint | Provide additional back support or suspension members to prevent distortion, overloading or excessive vertical deflection.
21271c21-182b-430c-8604-89c6aec27f85 | checkpoint | Ensure that the failure of any one suspension point does not cause a progressive failure of the ceiling.
71d0a97c-a6b0-4422-97cb-8f68f04cbdd4 | checkpoint | Where applicable, provide height adjustment with a length adjustment device at each suspension point.
b0d98b15-9ea3-45c8-9079-360738b15a3b | checkpoint | Services: Do not fix to the installed services. Where services obstruct the ceiling supports, provide bridging and suspension on each side of the services.
c1b1e862-e673-46f7-a295-b4db9e933346 | checkpoint | Uplift: Suspension system and framing to resist uplift.
0c379730-8e62-41cf-b20c-038b3f10960e | checkpoint | Tolerances: Flatness, twist, winding and bow: 1.5mm deviation from a 1.5m straightedge places in any position
8655df17-9eb7-4eb3-8ed9-d864133b4a35 | section | Hold Point
2b53e4b0-dbff-4881-aed8-7e52102c3694 | checkpoint | Suspension system completed – Ready for installation of ceiling tiles, lining and panels.
00b86880-40e7-4134-8bff-58182a3a8055 | checkpoint | Confirm all service trades are complete & ready for closing in of ceilings.
ca9624e1-0ee1-4a40-bcb7-ce277093c5f0 | section | Ceiling Lining
fa48ede1-3f1a-43d2-a3c8-eefee9a19ace | checkpoint | Provide board lining to a finish and workmanship as per supplier installation guides.
94ced55d-9037-48d7-95ad-ba97865c9961 | checkpoint | Fit accurately and neatly, without distortion and free from air leakage and staining.
74de319a-672a-4e9b-8f74-b9969fae473f | checkpoint | Set out patterned or heavily textured materials with a consistent direction of pattern or texture.
e0339253-f852-4eb3-bbf0-adf84750d482 | checkpoint | Cut ceiling unit edges: conceal, or finish to match prefinished edges.
f4b2442f-1ce5-4312-a75e-e1e60d912625 | checkpoint | Multiple sheet layers to fire rated and acoustic rated elements: Fill & flush up all joints on each layer and caulk up perimeters and penetrations before commencing succeeding layers. Stagger all sheet joints by minimum 200mm.
1e7937d0-dc2c-4162-9170-b3bf331486d3 | checkpoint | Board joints support: Provide framing parallel to the joint on each side. Do not fix the lining to abutting building surfaces
ce7e9462-eb71-47cb-ae97-a7f3550daacf | checkpoint | Flush joints: Provide recessed edge sheets and finish flush using perforated paper reinforcing tape. Locate & position joints to intersect light fixtures, vents or air diffusers.
06f940f3-a563-46a4-9835-a0ce8ebbe0c6 | checkpoint | Tolerances: Suspension system bearing surface for flush lined ceiling to AS/NZS 2589
174d4c65-5b53-4a4c-9e9c-595a3aee4a24 | checkpoint | Levelness: Max tolerance of ±5mm relative to the documented height datum for the ceiling in each room or space.
cc8bfcaa-2d04-432f-b52e-91cfb0a81d9a | checkpoint | Trims & accessories: Provide trims at junctions with other building elements and surfaces, including walls, beams and penetrations.
7414b68f-d953-412d-9b76-ee7c5f45b99a | section | Control joints
71f4d6d9-d3d1-412d-ab58-0fc7b42650ca | checkpoint | Align ceiling control joints with the structural control joints. Do not bridge structural control joints.
589ddda5-6cf1-4b5a-ba06-e7937e05ca4b | checkpoint | Provide purpose made PVC control joint beads where documented.
968bccaf-246c-5396-b006-5c2233861568 | note | Provide framing parallel to the joint on each side.
0aa46d81-bbef-588f-90d9-a9197024f0eb | note | Plasterboard lining: 12m centres
051daa92-02d6-5041-aa0d-cabe40c6b957 | note | Fibre cement lining: 7.2m centres
b0a52747-14c2-4cfc-ac7a-c1bba48be906 | section | Bulkheads
9180d848-79db-451d-9f4f-aae37912ae37 | checkpoint | Integrate bulkheads with the ceiling structure and brace to prevent lateral movement. Where ceiling is terminated at the bulkhead, provide for seismic requirements
be8a1910-05b1-467e-a0ef-5b58d6c7b130 | section | Tolerances
8b8c2506-0b95-40a9-9c27-8a639d22bc69 | checkpoint | Flatness, twist, winding and bow: Maximum 1.5mm deviation from a 1.5m straightedge
1b3c12a6-cea0-4603-8a39-cc8902e0facb | section | Acoustic installation
4462cfc6-d196-4f1c-86b6-be052e358277 | checkpoint | Where documented, place acoustic batts on top of ceilings system and butt to each other and to partitions.
39be9cab-7181-4bb0-bc20-ee0f81f82ef9 | checkpoint | Tightly butt and trim neatly around services items and other items.
920509af-61a8-4a16-9af0-562a4abbbf57 | section | Smoke baffles and acoustic baffles
8df60c8a-9710-4870-94d4-b4c5670a282f | checkpoint | Provide approved smoke and acoustic baffles where required
358b28fd-357d-4e55-bb1a-000ff4144452 | section | Additional checks for fire-protective board lining
d24253d2-aa34-4d91-a58a-398f7876de18 | checkpoint | Check the fire resistance levels on RCP
844871af-f263-42a2-8e56-a14a520cdbe8 | checkpoint | Fixings: Direct to concrete elements and to purpose made steel framing
0aae1b7d-70ed-4bbd-bc4e-1659bda35d04 | checkpoint | Penetrations: Seal penetrations in the board lining to maintain the integrity of the required fire resistance level including suspended ceiling hangers and suspension systems for services.
5ae394f1-9c2d-4c80-b1b4-180cb0015eb7 | checkpoint | Board perimeter: Provide fire sealant and trims at junctions with other building elements and surfaces, including walls, beams and penetrations to maintain the required fire resistance levels.
9dd0ec92-724f-493d-96c0-cc05b413d513 | section | Access panels
137ba411-079c-45ff-8786-adcff7161175 | checkpoint | Match the access panels to the ceiling in appearance and performance
cb40c285-b6ef-477f-a577-6870537109fe | checkpoint | Provide access panels supported and anchored to permit ready removal and refixing
08840828-4398-4ca3-a16c-f2ed634f8724 | checkpoint | Provide fire rated and acoustic rated panels where documented or where required to maintain the designated rating of the ceiling element
2c73535c-8a08-43e9-adae-999bef904a29 | checklist | Doors & Frames ITP |  | Doors & Frames ITP
7bcc49fa-0c27-4266-b6fb-c6465693dede | section | Take delivery
4235a939-634a-46f8-8b8a-6f02693ae7be | checkpoint | Frames as per design documents
39b8dc3d-601b-40c8-84f2-b05e1c6573dc | section | Setout
7df51dd3-8c6a-4d2f-843a-e9ebcceaa665 | checkpoint | Ensure Frames are set out as per Setout Plans.
68e0c348-83e0-4b10-bc69-949efbcde0b7 | checkpoint | Set out is to be read in conjunction with Door Schedule.
26063017-6dd9-4280-aa2f-d72e60791114 | section | Execution
f6ff7154-9897-4f7f-b340-99666ead58be | checkpoint | Frames are filled in accordance with acoustic or fire requirements where applicable
38eb72a2-6666-410b-af4d-ea8396ff1ca0 | checkpoint | Frames are plumbed, levelled, straight and within acceptable tolerances
a5116170-4f35-4e80-b88f-c4349c522b45 | checkpoint | Frames are adequately fixed or anchored to the building structure.
729e4aa7-c298-4c70-8547-11e7a38d7599 | checkpoint | Frames are installed so that they do not carry any building loads
a0222c60-757e-4c4d-b4b6-529242086f38 | checkpoint | Fire door frame note: Fixings to substrate to be in accordance with manufacturers instruction. Steel stud frame typically, 10 gauge steel screws at max 300mm centres and no more than 100mm from each end.
3decc5eb-fb84-4a18-ab52-132c7a94ed55 | checklist | Paint ITP |  | Paint ITP
917a4b04-70d5-40ff-a735-e11284d1b4af | section | Spray out internal
72f1ed55-dad6-4d81-b4e0-58ee735cefd4 | checkpoint | All plastering sanded and internal junctions free from dust prior to sealer undercoat
7c8efb13-a29e-4737-af2b-4858c0a26fb5 | checkpoint | Full protection to joinery, window frames etc prior to painting. Any overspray is cleaned off prior to completion of spray out.
597782b5-6760-4a9d-b156-b8da52d97064 | checkpoint | All nail holes, joints and gaps are filled prior to painting.
2576565a-e013-4b40-a415-d4f5f3d10d7d | checkpoint | All edges to internal / external doors are sealed and painted as per manufacturers specification.
d133449c-6c5c-470f-b488-999d08801559 | checkpoint | All hinges, door furniture, latches and striker plates if removed are to be retained and re-installed prior to completion.
3553a857-4a78-47a2-940f-fd2737a177ba | checkpoint | All ceilings are lightly sanded in between all coats and are back rolled and layed off in reasonable fine stipple finish.
1f8d187f-aa1a-4242-bc2e-629dc1ec1c7e | checkpoint | All wall coasts are back rolled and layed off in a reasonable fine stipple finish.
89fe7687-d287-4c16-a5c8-39a08e09afed | checkpoint | All paint is NOT site tinted or any other liquid added or altered without written approval.
68ea6b7f-eeec-4f7c-8a3e-d0f9a3d008c3 | checkpoint | Clean up is completed ONLY in the supplied wash out area.
8b830488-b1c8-4df7-98c0-44b1a088057a | checkpoint | All rubbish is to be placed in the bins provided and the area is to be left clean and tidy and void of rubbish and excess materials.
7b6a292e-5067-4ef3-8387-70eac4135213 | checkpoint | Ensure no damage is done to other trades work (if so, you Must Report to the Supervisor and Wadsworth Project Manager immediately).
564627cc-bf6b-4ba5-88f2-5577cb11956e | checkpoint | All completed works are consistent with the scope of works supplied by CBGU JV, the supplied paint specification, and approved samples.
d2dc13ec-a82a-4346-b571-7897dc53f115 | section | First Coat & Final Coat
54bcd81a-8716-4e86-9b10-6b9f0840fe47 | checkpoint | Full protection to joinery, window frames etc prior to painting. Any overspray is cleaned off prior to completion.
41e1e26f-5ff0-4eba-a121-617ab2af4cea | checkpoint | All nail holes, joints and gaps are filled prior to painting.
5d50adab-29e4-4615-be9d-a9f4d19b06eb | checkpoint | All edges to internal / external doors are sealed and painted as per manufacturers specification.
18483edd-2b48-49d0-b1ee-a6ac8a1c1645 | checkpoint | All hinges, door furniture, latches and striker plates if removed are to be retained and re-installed prior to completion.
1f1d2a58-71b2-47a0-84c2-dd71334e9adc | checkpoint | All walls are lightly sanded between coats.
e4e9aa6f-abe7-4194-a70a-2dcbaed22519 | checkpoint | All wall coasts are back rolled and layed off in a reasonable fine stipple finish.
7afcca1a-aa09-4a9f-99e2-14068d6e5aef | checkpoint | All paint is NOT site tinted or any other liquid added or altered without written approval.
2ee45139-736f-4101-ba15-3cf072043bc6 | checkpoint | All cutting work is consistent is consistent and complete in a tradesman like manor.
1f138199-d1fe-4a46-925a-05ff9e347141 | checkpoint | Clean up is completed ONLY in the supplied wash out bay.
323fcffa-96f6-43e1-9714-890dbcace52c | checkpoint | All rubbish to be placed in bins provided and the area is to be left clean and tidy and void of rubbish and excess material.
95ae864b-21f1-4899-8480-5319ac6bdaf9 | checkpoint | Ensure no damage is done to other trades work (if so, you Must Report to the Supervisor and Wadsworth Project Manager immediately).
88a0dce9-b11c-4047-a89b-5d00ebcffbdb | checkpoint | All completed works are consistent with the scope of works supplied by CBGU JV, the supplied paint specification, and approved samples.
ca501a05-da67-4232-b789-beb505aa9bf7 | checklist | Partitions ITP |  | Partitions ITP
0c65b5f3-5b2b-404a-b927-a2d719cb83e0 | section | Set out
cfc9283c-2523-4e81-82d3-2a7068a3686b | checkpoint | Partitions set out plans current revisions checked and wall set out completed as per the current plans
275166e5-8fd2-4ddf-9633-24baf58e18fb | checkpoint | Minimum/critical dimensions (face to face) on drawings checked
4b04b8e8-8913-4423-bf50-125c928824b8 | section | Stud Framing
718b17d4-1c7b-4ec5-b835-c841146b751c | checkpoint | Base & Head tracks fixed in accordance with steel stud partition design. Typically ≤600mm centres and 100mm from ends
159fe86c-f8d4-474c-8a14-84ad24b8d088 | checkpoint | Fixing to post tensioned concrete: Maximum embedment for fixings = 50mm
c02ba4bc-8b4e-47c7-b511-bba97beb1e5f | checkpoint | Stud spacings correct as per steel stud partition design. Noting max 450 centres for wet area sheeting.
412d864f-0930-4a8d-afae-1e97ee73ed3b | checkpoint | Fixing to post tensioned concrete: Maximum embedment for fixings = 50mm
a1cec6fd-02b5-40f8-bc6b-b33b15c08a99 | checkpoint | Door frame openings as per Rondo design
45c7a740-b11f-44ce-88cf-f04362e4e1a7 | checkpoint | Full height partitions: Fix deflection head tracks to the floor slab soffit to allow a minimum deflection capacity of 20mm.
dc578f3c-b5d9-490f-9468-66ad3cd767ec | checkpoint | Rotate intermediate studs into tracks for friction fixing
0457816f-5da7-4266-b06e-7a9751fda391 | checkpoint | Structural floor control joints: Disconnect partitions over joints with detached double studs and ensure bottom tracks, bracing and top tracks are not fastened across joints
4b3c561e-0fa0-40c2-8b79-66e940dcb684 | checkpoint | Stud service holes: Splice additional stiffening to studs if site cut service holes exceed 1/3 the width of the member
8c3e7ace-e93e-487e-b434-106733a4851f | checkpoint | Provide fire, smoke and acoustic sealing where indicated on the drawings/details
2186f1dc-1e88-4424-bc32-95af63a33d1a | checkpoint | Noggings: Fix noggings as per steel stud design.
410c2982-5dda-47ef-925e-c2ddfb2b4210 | checkpoint | Door frames: Installed
92146e67-908f-49fe-ae52-e302c882de4e | section | Bulk Insulation
30eba899-274b-4434-9bad-8113b7d495df | checkpoint | Install acoustic and thermal insulation.
e10b0278-aaff-4733-835a-80fc9860a419 | section | Hold Point
b00c5f43-9542-4d43-bc24-42a364acd9d9 | checkpoint | Framing system completed – Ready for installation of sheets.
df979535-5d40-49b7-9a63-d63d1dcc14f0 | checklist | Speed Panel ITP |  | Speed Panel ITP
75f8481c-8b66-4ad1-85e2-0e8e1365a860 | section | Prior to Commencement – The following documentation are completed and approved
d56af8bb-085d-4798-99a7-3615f6120767 | checkpoint | Samples and prototypes submitted and approved (Fire sealants approved)
d61b5187-9d2e-4a29-9b2a-c20e8ec7e1b2 | section | Set out
e63c4997-c07f-42f6-b0b3-4dc9321fef86 | checkpoint | Speedpanel walls set out plans current revisions checked and wall set out completed as per the current plans
108465a0-7e7b-4d76-8fb6-e9c45cb0275b | section | Framing & Speed Panel
726112c4-ecc0-4022-b40b-4a1d378f6395 | checkpoint | Powder coated speedpanel used where required
292d408a-c18d-4b26-bef3-4159987289f1 | checkpoint | Fix tracks to floor & soffit per manual
8b54bf9f-f716-43d3-9314-cafa07a50095 | checkpoint | Provide fire, smoke and acoustic sealing where indicated on the drawings/details.
56656d0a-6b1e-4dd2-9505-055df0967369 | checkpoint | Ensure that the configuration is as per the Speedpanel site specific detailing.
80335c30-fca7-4b4f-802d-4919673e5b86 | checkpoint | Ensure that all caulking is as per the Speedpanel site specific detail.
c803512c-c1bb-44f3-bad5-6973b028e787 | checkpoint | Ensure openings are as per the specified jamb & door sizing.
fbd29b6e-eb79-42e5-b1e4-9a5ab9c59d52 | checkpoint | Door frames: Installed
3825dcb7-b5a6-4472-9979-1bcb295f0863 | section | Tolerances
18d05465-b2f7-4d4e-9c35-d433c73e2308 | checkpoint | Flatness, twist, winding and bow: Maximum 1.5mm deviation from a 1.5m straightedge.
ff704fd2-ff73-4116-9ddb-d455c2ff5c4e | section | Penetrations/Access panels
14bcf07e-d49b-4f6a-aa67-c55997070ae0 | checkpoint | Installed as per Speedpanel design & install specification.
2154aa2c-8c22-4b9a-91f0-f200a5aed8fe | checkpoint | Correct FRL achieved.
62678b58-4c4b-437e-8289-a858188474cb | checklist | Underslab Insulation ITP |  | Underslab Insulation ITP
aa8c541d-e483-422b-8c24-4b7eaeaa520f | section | Take delivery
a27a8402-32c6-4005-8a44-b8b7b3a739d7 | checkpoint | Insulation panels arrive as per Design Documents and defect free.
0e1a46d7-5940-4c55-85cb-eb5dc4d804ee | section | Setout
b55ba63c-c93f-4939-a0be-3e0d36b09515 | checkpoint | Ensure most up to date drawings are being utilised
8169a9d9-9d21-4658-8bea-b49c65d2db90 | section | Execution
0af3b050-da4c-46c4-993f-bc3a3ad05bac | checkpoint | Mechanically fix panels to Manufacturers Specifications
ed05e7c7-c99d-4ffd-9c2b-f98597ac912f | checkpoint | Tape all joints and exposed edges with a minimum of 75mm wide silver tape