## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | Partitions ITP |  | Partitions ITP
0c65b5f3-5b2b-404a-b927-a2d719cb83e0 | section | Set out
cfc9283c-2523-4e81-82d3-2a7068a3686b | checkpoint | Partitions set out plans current revisions checked and wall set out completed as per the current plans
275166e5-8fd2-4ddf-9633-24baf58e18fb | checkpoint | Minimum/critical dimensions (face to face) on drawings checked
4b04b8e8-8913-4423-bf50-125c928824b8 | section | Stud Framing
718b17d4-1c7b-4ec5-b835-c841146b751c | checkpoint | Base & Head tracks fixed in accordance with steel stud partition design. Typically ≤600mm centres and 100mm from ends
159fe86c-f8d4-474c-8a14-84ad24b8d088 | checkpoint | Fixing to post tensioned concrete: Maximum embedment for fixings = 50mm
c02ba4bc-8b4e-47c7-b511-bba97beb1e5f | checkpoint | Stud spacings correct as per steel stud partition design. Noting max 450 centres for wet area sheeting.
412d864f-0930-4a8d-afae-1e97ee73ed3b | checkpoint | Fixing to post tensioned concrete: Maximum embedment for fixings = 50mm
a1cec6fd-02b5-40f8-bc6b-b33b15c08a99 | checkpoint | Door frame openings as per Rondo design
45c7a740-b11f-44ce-88cf-f04362e4e1a7 | checkpoint | Full height partitions: Fix deflection head tracks to the floor slab soffit to allow a minimum deflection capacity of 20mm.
dc578f3c-b5d9-490f-9468-66ad3cd767ec | checkpoint | Rotate intermediate studs into tracks for friction fixing
0457816f-5da7-4266-b06e-7a9751fda391 | checkpoint | Structural floor control joints: Disconnect partitions over joints with detached double studs and ensure bottom tracks, bracing and top tracks are not fastened across joints
4b3c561e-0fa0-40c2-8b79-66e940dcb684 | checkpoint | Stud service holes: Splice additional stiffening to studs if site cut service holes exceed 1/3 the width of the member
8c3e7ace-e93e-487e-b434-106733a4851f | checkpoint | Provide fire, smoke and acoustic sealing where indicated on the drawings/details
2186f1dc-1e88-4424-bc32-95af63a33d1a | checkpoint | Noggings: Fix noggings as per steel stud design.
410c2982-5dda-47ef-925e-c2ddfb2b4210 | checkpoint | Door frames: Installed
92146e67-908f-49fe-ae52-e302c882de4e | section | Bulk Insulation
30eba899-274b-4434-9bad-8113b7d495df | checkpoint | Install acoustic and thermal insulation.
e10b0278-aaff-4733-835a-80fc9860a419 | section | Hold Point
b00c5f43-9542-4d43-bc24-42a364acd9d9 | checkpoint | Framing system completed – Ready for installation of sheets.
| section | Board Lining
| checkpoint | Stagger end joints in a brick pattern and locate them on framing members away from the corners of large openings
| checkpoint | Multiple sheet layers: Fill & flush up all joints and fixings in each layer and caulk up perimeters and penetrations before commencing succeeding layers.
| checkpoint | Butt joints staggered on adjoining sheets and opposite sides of wall.
| checkpoint | Fire rated recess joints staggered on opposite sides of the wall, or backed by steel nogging
| checkpoint | Tape & Bead all joints and corners as required
| checkpoint | Provide sealants at junctions between partition systems and with other building elements
| checkpoint | Provide trim such as beads, moulding and stops to make neat junctions between lining components, finishes and adjacent surfaces
| section | Control Joints
| checkpoint | Control joints to coincide with structural control joints
| checkpoint | Provide control joints as follows:
| checkpoint | Plasterboard lined partitions: 12m centres
| checkpoint | Fibre-cement board lined partitions: 7.2m centres
| checkpoint | Board lined partitions in wet areas: To suit joints required in tiling and at max 4.2m centres
| section | Tolerances
| checkpoint | Flatness, twist, winding and bow: Maximum 1.5mm deviation from a 1.5m straightedge
| section | Additional checks for Fire Walls
| checkpoint | Installed as per board suppliers design & install specification
| checkpoint | Correct FRL achieved
| checkpoint | Perimeter fire rated sealant completed.
| checkpoint | All penetrations through fire walls below and above ceiling protected/sealed – Service penetrations sealing by others
| checkpoint | Fire door frames installed
| section | Additional Checks for Smoke Walls
| checkpoint | Deflection heads and all joints sealed, taped and set (Sealant is approved prior)
| checkpoint | All penetrations through smoke walls below and above ceiling protected/sealed
| section | Additional Checks for Acoustic Walls
| checkpoint | Deflection heads and all joints sealed, taped and set (Sealant is approved prior)
| checkpoint | All penetrations through acoustic walls below and above ceiling protected/sealed
| section | Access panels
| checkpoint | Installed with consideration for required acoustic, smoke & fire rating.