## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat | af82b5c6-809b-4529-910d-8326096ee13e |  | checklist | In Slab Pipe Work |  |  |  |  | Yes | In Slab Pipe Work | 1851bada-7f27-403f-b3a4-1e6f7f945426
checkpoint-status | e847c20c-f6af-419e-83de-4307ea1984dc |  | checkpoint | Drains laid to correct falls
checkpoint-status | 293ddbf4-aac4-4f05-8e40-caabb477d036 |  | checkpoint | Pipes wrapped/ lagged though floor correctly
checkpoint-status | b85ad143-c7cf-4d11-889d-5bd9fd04635d |  | checkpoint | Check Set out of all risers and inline with drawings
checkpoint-status | c8b423e8-9fa3-4e89-b27e-b7e51729fa57 |  | checkpoint | Pipe work clipped correctly to reo and fixed
checklist-sectioned | e71613fd-a79f-44f8-9ccd-e63df40b3a10 |  | checklist | Second Fix QA |  |  |  |  | Yes | Second Fix QA | 1cc04bc1-f003-4e33-918e-f62d34da446b
checkpoint-group | d2a4ac37-3c5a-4ad9-8800-7ecba4e58da3 |  | section | Preinstall QA
checkpoint-status | 7fbf52bc-b488-425c-9f3b-9193e03137fe |  | checkpoint | Substrate acceptable
checkpoint-status | 63c9714a-c569-413e-9dcd-0b29d37b67fa |  | checkpoint | Area accessible and ok to begin work
checkpoint-group | f7985e76-be07-4aef-9607-719618ece927 |  | section | Second Fix Checks
checkpoint-status | d4b61a5e-2f15-4494-bf82-b44a2d79d77e |  | checkpoint | Fixtures and fittings checked for damage
checkpoint-status | bd0cb38c-5a50-411a-a540-87ce9385beb0 |  | checkpoint | Flanges installed on all penetrations
checkpoint-status | 35176bfb-4ab2-43ff-9369-c0971a4fd59d |  | checkpoint | All fixtures sealed with silicone as required
checkpoint-status | 143c3509-74e4-4709-a946-83c86163fabf |  | checkpoint | All fittings checked for leaks
checkpoint-status | ea2dc047-87e5-43e8-9a65-6b505c8ced56 |  | checkpoint | Hot Water system commissioned
checkpoint-status | 910d71fe-e2e3-4796-a072-fb48ede3053c |  | checkpoint | Pumps Install and Commission correctly
checkpoint-status | 52f2d292-1e16-4ad5-998e-e88fff2637fe |  | checkpoint | System commissioned
checkpoint-status | 2f9b07e5-2271-4f15-a343-f1243858b5dd |  | checkpoint | Handover checks
checkpoint-status | 0ac2a4c2-ca8b-4598-a82a-a88e1d838f5e |  | checkpoint | Photos Taken & attached
checkpoint-status | ba1c41fe-32fa-40bf-aced-21751e05f6db |  | checkpoint | Work completed as per spec and tidied up
checklist-sectioned | 82c74330-fca0-4bfb-ac4a-46c1fecfa71c |  | checklist | Underfloor Check |  |  |  |  | Yes | Underfloor Check | 451cb3e3-1a85-4c94-b93a-f214d1089043
checkpoint-group | e394470d-a0c4-403d-aec1-f14c1640aa87 |  | section | Preinstall QA
checkpoint-status | 48e4775f-6487-4843-a4e3-f2e9ead77f13 |  | checkpoint | Substrate acceptable
checkpoint-status | fab9aed7-d0e2-4839-ae4b-a622ad0ec996 |  | checkpoint | Area accessible and ok to begin work
checkpoint-status | 4315cf2a-4465-4f19-a403-b7743a4795fd |  | checkpoint | Plans correct issue and construction set
checkpoint-status | f0c603b1-050b-4d54-9877-f35b96676d32 |  | checkpoint | Check set out from builders
checkpoint-group | 93a084fc-b56d-481c-8b55-357e0285c666 |  | section | Install QA
checkpoint-status | 2b5d025e-4d97-4c12-bd71-3bb7f023991d |  | checkpoint | Sleeves installed though Structural Foundations Beams correct
checkpoint-status | d7550634-f8bc-4c1b-8d79-12d175a6c8a7 |  | checkpoint | Hot Water System (relief drain)
checkpoint-status | 056727eb-3761-4702-a9fd-3079b7ffebd0 |  | checkpoint | Correct Floor wastes set up for Grates and Grills in different areas
checkpoint-status | cef4aefe-55dc-4474-b53d-105bd2f9c56d |  | checkpoint | Drains laid to correct falls
checkpoint-status | 7256e0c5-ce05-46ff-ab01-1dee1f8b90b7 |  | checkpoint | Pipes wrapped through floor
checkpoint-status | 4793e457-d689-4cf4-a530-383caa946f87 |  | checkpoint | Pipes tested for inspection
checkpoint-status | 757bbd7b-d29d-47a1-9246-ce9bbd2951d8 |  | checkpoint | Handover checks
checkpoint-status | 73641ed5-b9ab-4266-b386-d358382bfe1c |  | checkpoint | Photos Taken & attached
checkpoint-status | 5b89f655-d2a0-4cc9-aea9-9c5aa31a3583 |  | checkpoint | Inspection passed
checkpoint-status | 60c4731f-04fe-4718-959a-3c96b359d06b |  | checkpoint | Water needed in floor for 1st fix
checkpoint-status | ef60cac4-409d-4b95-a936-7f621229c8d0 |  | checkpoint | Work completed as per spec and tidied up
checklist-sectioned | a6349b4a-61f1-4082-8eb0-f5fc520b0c1b |  | checklist | Drainage |  |  |  |  | Yes | Drainage | aa8ce1ff-5c57-4e02-81a3-f84aa3303dcf
checkpoint-group | ee8ee14a-a12f-497d-8920-20b1b7fe837b |  | section | Storm Water
checkpoint-status | c13fb141-9061-4abb-9d6d-2738f6eb5225 |  | checkpoint | Plans correct issue and construction set
checkpoint-status | 8b956c91-0d75-4958-a01b-3309bccc819a |  | checkpoint | Check set out from builders
checkpoint-status | d4837ae8-8be2-42c2-b6e8-4ca0a551234d |  | checkpoint | Check Plans for correct sizing and pipe material
checkpoint-status | c8fb1153-38da-422a-8847-2956e89f26d8 |  | checkpoint | All Falls achieved as per plans
checkpoint-status | 53bb5cda-129d-43d0-a48c-d660e504a331 |  | checkpoint | All Manholes haunched as per code
checkpoint-status | 0cd1f82c-17d6-4410-ae74-ec74dfbfa10f |  | checkpoint | All Cesspits, Manholes installed to correct heights
checkpoint-status | b5e838a9-c7bd-41c7-996d-38ad45862f16 |  | checkpoint | All Trenches compacted with compactor
checkpoint-status | 355e5f40-9ae9-4a3d-ba07-f1ea4320fd2a |  | checkpoint | Subgrade Scala test ever 10m - 3 Blows per 100mm
checkpoint-status | fc89df9b-141b-40ec-a093-8cd8f9e013f1 |  | checkpoint | Backfill in layers of 300mm and test every 10m - 3 Blows per 100mm
checkpoint-status | b33c1b3a-7c7d-4280-8ce5-5f888cb5cb06 |  | checkpoint | Pipes tested for inspection
checkpoint-status | 721b292e-e914-4d9f-ab7a-27f81f83ebce |  | checkpoint | Rainwater Tank installed as per engineers report
checkpoint-status | 98785fd4-21d6-45a7-993f-81676b78ae1e |  | checkpoint | Photos Taken
checkpoint-status | 3f23add7-7e97-447f-b09f-5a0c63daa333 |  | checkpoint | Inspection passed
checkpoint-status | 4af69b83-884c-47e8-87e3-05a8ff3ce287 |  | checkpoint | Engineer Inspected
checkpoint-status | 39ce3027-062c-4f5e-9ef6-138fd35dc1bb |  | checkpoint | Mark up drawings Done
checkpoint-group | 01cd4c6d-ba76-45a8-bbde-492a0afefe2a |  | section | Sewer
checkpoint-status | 5d39c004-335f-4460-83a4-acaebefc935d |  | checkpoint | Plans correct issue and construction set
checkpoint-status | 278980e7-9486-4c93-ab8b-1c8e474b398c |  | checkpoint | Check Plans for correct sizing and pipe material
checkpoint-status | c4243bc4-9987-42e7-a449-bb00cf7546fd |  | checkpoint | All Falls achieved as per plans
checkpoint-status | fa572e4e-eddb-4424-a1ba-27267efd1a9c |  | checkpoint | All Manholes haunched as per code
checkpoint-status | 1af8402c-094f-4e52-b32e-d0aaf8801937 |  | checkpoint | All Manholes installed to correct heights
checkpoint-status | 61869215-8e0f-4641-b356-9099dde802ac |  | checkpoint | All Trenches compacted with compactor
checkpoint-status | 8819f0a2-e467-4fc4-8bf3-dff5996643ca |  | checkpoint | Subgrade Scala test ever 10m - 3 Blows per 100mm
checkpoint-status | 1a67fc19-0180-4487-9daf-6bfbe8e2eaf7 |  | checkpoint | Backfill in layers of 300mm and test every 10m - 3 Blows per 100mm
checkpoint-status | 2cba0966-b75e-4786-8889-8240cb2f0846 |  | checkpoint | All ORG and RE installed as per plan
checkpoint-status | 176065dc-9a72-4574-94a8-1dab379c0270 |  | checkpoint | Pipes tested for inspection
checkpoint-status | 564087c3-fbf2-47c3-ae41-001f467fc52e |  | checkpoint | Inspection passed
checkpoint-status | 8dc66657-adb6-4cc2-95df-4289675e14fd |  | checkpoint | Mark up drawings Done
checkpoint-status | 336cf6b0-fd87-4e8b-b933-fe3c7b89e643 |  | checkpoint | Photos Taken
checkpoint-group | 31141297-f82d-405a-878b-b0e6ea0ed1fd |  | section | Water Mains and Infrastructure
checkpoint-status | e393c0b6-fa5f-463b-a9e8-ffee01beb405 |  | checkpoint | Plans correct issue and construction set
checkpoint-status | fdca831f-e529-476d-a26a-666e790ee30d |  | checkpoint | Check Plans for correct sizing and pipe material
checkpoint-status | de30bb7e-361c-4137-ab86-8225968e6eab |  | checkpoint | EF welding completed by a certified welder
checkpoint-status | 47c527e0-f2eb-4a6a-84ed-2513f2e3970b |  | checkpoint | Subgrade Scala test ever 10m - 3 Blows per 100mm
checkpoint-status | 1c91c194-ad11-40ea-8d52-ba78bb6fc200 |  | checkpoint | Backfill in layers of 300mm and test every 10m - 3 Blows per 100mm
checkpoint-status | 409430bf-7ae4-42d0-9daf-9e77443af319 |  | checkpoint | Water Main flushed ready for connection - Fire Main 1600L/Min at 250KPA
checkpoint-status | d37ea673-2149-480f-baa7-471e6a7a98fc |  | checkpoint | Pipes tested for inspection
checkpoint-status | bc7d1642-d8f0-4e5f-b8dc-5cb9b496f1ab |  | checkpoint | Chlorination of Pipe work completed as per TCC IDC Code
checkpoint-status | e70ba676-cf2d-4f27-9ca0-72b4323387a2 |  | checkpoint | E Coli Test done and Passed
checkpoint-status | eaf338da-ba10-4465-aa92-ab1527ba6e33 |  | checkpoint | Warning tape installed
checkpoint-status | 7727b712-2fbe-40a2-a3e3-35f8e0d36b14 |  | checkpoint | All Trenches compacted with compactor
checkpoint-status | 53fcc86e-a3db-439c-b3c0-71ff01d53077 |  | checkpoint | Inspection passed
checkpoint-status | 37442c55-dc4c-4308-a0d5-bfac1250223a |  | checkpoint | Mark up drawings Done
checkpoint-status | 15a980e6-b307-487a-a8fb-464c2080eb02 |  | checkpoint | Photos Taken
checklist-sectioned | c3cc7286-851e-4b24-b7f6-0e759690fce3 |  | checklist | First Fix QA |  |  |  |  | Yes | First Fix QA | d6f6921a-f13a-41bd-9798-61f17ba13ea9
checkpoint-group | 79aa3b03-ffe9-44d6-9144-62dc5e6a4c58 |  | section | Preinstall QA
checkpoint-status | 61c06ff9-dd78-446c-858f-d337ad9819b0 |  | checkpoint | Substrate acceptable
checkpoint-status | 04174994-625a-480a-9392-fe80d88546fc |  | checkpoint | Area accessible and ok to begin work
checkpoint-status | 84b6b6bf-3caa-4d5c-becc-6dd07e015903 |  | checkpoint | Plans correct issue and construction set
checkpoint-status | 8f866726-25b4-428e-a09d-944da664427b |  | checkpoint | Check Plans for correct sizing and pipe material
checkpoint-group | e8333929-0d24-4032-9616-a73a07f54e74 |  | section | First fix checks
checkpoint-status | 2a6c37ca-1d8c-40ac-9b65-8029f9744666 |  | checkpoint | Sanitary fixtures and fittings specifications received for set out
checkpoint-status | b2ae17ae-1c8b-4abe-8bd0-bdfd1f7e7587 |  | checkpoint | Acoustic Wrap installed
checkpoint-status | b737e1c1-08cb-4a01-b324-5ff645e5c9db |  | checkpoint | All Pipes silicone though noggs
checkpoint-status | 6a88013b-4757-4a3c-9c6b-333d49832748 |  | checkpoint | Vents install through roof
checkpoint-status | cdd0d150-f103-4471-a174-ff29a8657e2d |  | checkpoint | Floor Flanges and Grates installed and Capped
checkpoint-status | e77662db-28cf-4d03-9960-b6adf4932ec1 |  | checkpoint | All stud stiffeners installed
checkpoint-status | 5dc74701-6f74-46b0-a037-44ed7c29daf4 |  | checkpoint | Marshall flashings installed
checkpoint-status | 1f554434-862d-48d7-b8dc-a1bc218d7fb6 |  | checkpoint | All pipes pressure tested to 1500KPA (Fusiotherm refer to test procedures)
checkpoint-status | 491b7203-baa4-42b5-af65-c1134aa41620 |  | checkpoint | Seismic restraints installed
checkpoint-status | c2c177f5-c1b6-440a-a804-6e0a4552a1c1 |  | checkpoint | Water Meters installed and BMS Ready
checkpoint-status | 24d0b5f3-928e-47a8-b1bc-3036a03ceb27 |  | checkpoint | Hot Water Cylinder Set Up
checkpoint-status | 42232f7b-e511-465b-af0f-cf730303a14c |  | checkpoint | Noggs installed for fixing of sanitary fixtures and fittings
checkpoint-status | 0144e7db-bf66-45ae-bd37-467c464c6adb |  | checkpoint | Handover checks
checkpoint-status | 32600f2d-786e-4191-877f-97d548118df6 |  | checkpoint | Photos Taken & attached
checkpoint-status | 59dc1d35-60a7-48f8-955e-faeae8b627fc |  | checkpoint | Inspection passed
checkpoint-status | 6ed000d5-c59d-493f-a055-fcc7082e60b6 |  | checkpoint | Work completed as per spec and tidied up
checkpoint-status | 437f55b1-da1a-4047-a958-98699175498e |  | checkpoint | Council Inspection Passed