## General
Modify template as required prior to use, e.g. to accommodate project or customer specific requirements, then delete this instructional text when complete.
SECTION 1 – GENERAL DETAILS
Project Name: | SH58-M2TG | [5 empty] | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | DS2681 | [5 empty] | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Waka Kotahi NZ Transport Agency | [5 empty] | B | Report by Breach | PM | Project Manager | Gordon Lemon | GL
Contract Number: | 106877 | [5 empty] | C | Check | CM | Construction Manager | Jamie Nisbet | JN
Area/ Sub-System: | M2F |  |  | Lot ID Number: |  |  | D | Dimension Inspection | ER | Stantec Representative | Sam Parkinson | SP
[7 empty] | E | Examine | QE | Quality Engineer | Diliban Sengottian | DS
ITP Number: | DS2681-SH58-ITP-C-019 Ducting |  |  | Version: | 1 |  | H | Hold Point | QM | QA Manager | Diliban Sengottian | DS
ITP Description: | Sitewide ducting | [5 empty] | I | Inspection | SV | Surveyor | Jim Robbins | JR
Discipline: | Civil | [5 empty] | M | Monitor on Random Basis | PS | Project Supervisor | John Masters | JM
Specification: | MCIP SH58 East of Moonshine Road to Transmission Gully- Project Specification | [5 empty] | O | Operation | ST | Superintendent | Craig Maloney | CM
[7 empty] | R | Review | PE | Project Engineer | Dehan Erasmus | DE
Drawings: | Ducting Markup-M2F | [5 empty] | S | Subcontractor | SE | Site Engineer | Tyrese Dickson | TD
[7 empty] | V | Visual Verification | EM | Environmental Manager | Ross Glubb | RG
Prepared By: (Name) | Tyrese Dickson |  |  | Date: | 18/08/2025 |  | W | Witness Point
Quality Specified:
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: | Jamie Nisbet |  |  | Signature: |  | #VALUE! |  |  | Date: | 2025-08-27
Downer Approval |  | Name: |  |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: |  |  |  | Signature: |  |  |  |  | Date:

## Materials
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
3.1 | Ducts (PVC) | Prior to construction | Ducts shall comply with AS/NZS 61386:2015 or AS/NZS 2053.2:2001 | Manufacturer's specification | Prior to works | Witness Point | W | SE/PE
3.2 | Bedding sand | Prior to construction | The bedding material shall contain no organic material that will affect embedment material performance.The bedding material shall be free of materials that would be physically or chemically harmful to any pipeline component, including any protective coating | Quarry Testing | Prior to works | Witness Point | W | SE/PE

## Construction
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
4.1 | Bedding | Minimum bedding | A fine layer of fine sand to be laid at the bottom of the trench and top of duct. Minimum bedding layer to be 100mm . Ensure the bottom of trench is free from sharp stones | Photos DN-QUA-QC-26 Ducting Installation Checksheet | During duct installation | Witness Point | W | SE
4.2 | Duct laying | Duct spacing | Duct to be installed with with 50mm minimum gap between ducts and 50mm between duct and trench wall. Check vs Trench detail. Chorus gapping to be maintained where required. | Photos DN-QUA-QC-26 Ducting Installation Checksheet | During duct installation | Witness Point | W | SE
4.3 | Survey of duct alignment | Duct location | Surveyor / Site Engineer to as-built duct location | As Builts | During duct installation | Witness Point | W | SE
4.4 | Warning tape | Underground service warning | Ensure warning tape is installed 300mm above top of duct | Photos DN-QUA-QC-26 Ducting Installation Checksheet | During duct installation | Witness Point | W | SE
4.5 | Duct cover | Minimum cover | 900mm minimum cover for ducts on road verge | Photos As Builts DN-QUA-QC-26 Ducting Installation Checksheet | During duct installation | Witness Point | W | SE
4.6 | Compaction of AP65 in Carriageway | Compaction of granular fill | 200-250mm Lifts Beneath Pavement Layers: 95% MDD and+/- 2% of OMC as determined from the plateau test/or lab testing. None less than 92% Inside Pavement Layers: 98% MDD and+/- 2% of OMC as determined from the plateau test/or lab testing. None less than 95% | DN-QUA-QC-09 NDM Worksheet | 1 set of NDM tests per lift (comprising 5 No. NDM tests per set) | Witness Point | W | SE
4.7 | Compaction in verge | Compaction of as won material | Ensure compaction in 200-250mm lifts of suitable as-won material. | Photos DN-QUA-QC-26 Ducting Installation Checksheet | During backfill operation | Witness Point | W | SE

## Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
5.1 | As-built Survey | Upon completion of works | Comply with the project specification and drawings | As built survey record completed | Handover | Witness Point | W | SE/SV
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: