## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | DS2681-SH58-ITP-C-019 Ducting | itp |  |  |  |  | DS2681-SH58-ITP-C-019 Ducting
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Ducts (PVC)
label | Inspection Point: Quality Control Activity - Prior to construction
label | Acceptance Criteria - Ducts shall comply with AS/NZS 61386:2015 or AS/NZS 2053.2:2001
label | Verifying Document - Manufacturer's specification
label | Frequency - Prior to works
label | Inspection Type (Visual, other) - Witness Point
label | Inspection: Key - W
label | Inspection: By (Role Key) - SE/PE
checkpoint | 3.2 - Bedding sand
label | Inspection Point: Quality Control Activity - Prior to construction
label | Acceptance Criteria - The bedding material shall contain no organic material that will affect embedment material performance.The bedding material shall be free of materials that would be physically or chemically harmful to any pipeline component, including any protective coating
label | Verifying Document - Quarry Testing
label | Frequency - Prior to works
label | Inspection Type (Visual, other) - Witness Point
label | Inspection: Key - W
label | Inspection: By (Role Key) - SE/PE
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Bedding
label | Inspection Point: Quality Control Activity - Minimum bedding
label | Acceptance Criteria - A fine layer of fine sand to be laid at the bottom of the trench and top of duct. Minimum bedding layer to be 100mm . Ensure the bottom of trench is free from sharp stones
label | Verifying Document - Photos, DN-QUA-QC-26 Ducting Installation Checksheet
label | Frequency - During duct installation
label | Inspection Type (Visual, other) - Witness Point
label | Inspection: Key - W
label | Inspection: By (Role Key) - SE
checkpoint | 4.2 - Duct laying
label | Inspection Point: Quality Control Activity - Duct spacing
label | Acceptance Criteria - Duct to be installed with with 50mm minimum gap between ducts and 50mm between duct and trench wall.
label | ○ Check vs Trench detail. Chorus gapping to be maintained where required.
label | Verifying Document - Photos, DN-QUA-QC-26 Ducting Installation Checksheet
label | Frequency - During duct installation
label | Inspection Type (Visual, other) - Witness Point
label | Inspection: Key - W
label | Inspection: By (Role Key) - SE
checkpoint | 4.3 - Survey of duct alignment
label | Inspection Point: Quality Control Activity - Duct location
label | Acceptance Criteria - Surveyor / Site Engineer to as-built duct location
label | Verifying Document - As Builts
label | Frequency - During duct installation
label | Inspection Type (Visual, other) - Witness Point
label | Inspection: Key - W
label | Inspection: By (Role Key) - SE
checkpoint | 4.4 - Warning tape
label | Inspection Point: Quality Control Activity - Underground service warning
label | Acceptance Criteria - Ensure warning tape is installed 300mm above top of duct
label | Verifying Document - Photos, DN-QUA-QC-26 Ducting Installation Checksheet
label | Frequency - During duct installation
label | Inspection Type (Visual, other) - Witness Point
label | Inspection: Key - W
label | Inspection: By (Role Key) - SE
checkpoint | 4.5 - Duct cover
label | Inspection Point: Quality Control Activity - Minimum cover
label | Acceptance Criteria - 900mm minimum cover for ducts on road verge
label | Verifying Document - Photos, As Builts, DN-QUA-QC-26 Ducting Installation Checksheet
label | Frequency - During duct installation
label | Inspection Type (Visual, other) - Witness Point
label | Inspection: Key - W
label | Inspection: By (Role Key) - SE
checkpoint | 4.6 - Compaction of AP65 in Carriageway
label | Inspection Point: Quality Control Activity - Compaction of granular fill
label | Acceptance Criteria - 200-250mm Lifts
label | ○ Beneath Pavement Layers: 95% MDD and+/- 2% of OMC as determined from the plateau test/or lab testing. None less than 92%
label | ○ Inside Pavement Layers: 98% MDD and+/- 2% of OMC as determined from the plateau test/or lab testing. None less than 95%
label | Verifying Document - DN-QUA-QC-09 NDM Worksheet
label | Frequency - 1 set of NDM tests per lift (comprising 5 No. NDM tests per set)
label | Inspection Type (Visual, other) - Witness Point
label | Inspection: Key - W
label | Inspection: By (Role Key) - SE
checkpoint | 4.7 - Compaction in verge
label | Inspection Point: Quality Control Activity - Compaction of as won material
label | Acceptance Criteria - Ensure compaction in 200-250mm lifts of suitable as-won material.
label | Verifying Document - Photos, DN-QUA-QC-26 Ducting Installation Checksheet
label | Frequency - During backfill operation
label | Inspection Type (Visual, other) - Witness Point
label | Inspection: Key - W
label | Inspection: By (Role Key) - SE
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - As-built Survey
label | Inspection Point: Quality Control Activity - Upon completion of works
label | Acceptance Criteria - Comply with the project specification and drawings
label | Verifying Document - As built survey record completed
label | Frequency - Handover
label | Inspection Type (Visual, other) - Witness Point
label | Inspection: Key - W
label | Inspection: By (Role Key) - SE/SV